## Audit overview
Britain Electricity Model ¦ calculation audit v2.2
20 October2026. Original nine high-throughput presets retained as historical controls. Delivery study and Delivery annual add26conditional retention/procurement/coal cases (546annual cases,4914connected replays). Main explorer supply-first plans use selective five-year retention and constrained delivery. Sources and methods distinguish estimates, published references and saved hourly outputs. Changing workbook cells does not rerun dispatch.
ID | Status | Impact | Topic | Finding | Remaining
F01 | Corrected | Material | Renewable residual ages | Previously, 29.672 GW of solar, 6.337 GW of onshore wind and 5.769 GW of offshore wind residual capacity were all dated 2030. Existing unlisted stock is now separated from future completions. | Vintage allocation remains an estimate based on aggregate deployment history.
F02 | Corrected | Material | Sizewell B retirement | The former 2035 closure boundary is replaced by the conditional 2055 extension in both programmes. | Final contract and regulatory approvals remain conditions. The inherited cost allowance is still a generic proxy.
F03 | Corrected | Material | Import cost comparison | The gas variable operating cost of £5/MWh was read from the wrong configuration section and omitted from the import comparison. | The corrected threshold includes fuel and variable O&M. Foreign prices and availability remain scenario assumptions.
F04 | Corrected | Small | Gas startup wear | Starts of a fractional gas block were charged as starts of a whole 0.5 GW block. Wear now follows the actual MW started. | The default positive startup-fuel coefficient permits exact recovery of started MW; a zero-coefficient custom setting still uses a block proxy.
F05 | Corrected | Small | Trade checks and weather proxy | Trade uses the same unmet-energy threshold as the core screen. The neighbouring wind proxy is retained when domestic offshore capacity is zero. | Imports are not credited as contracted reserve.
F06 | Checked | Important | Pipeline additions | Preset additions top up surviving capacity to targets. Full targets are not added twice, and CfD contract capacity is not added to physical REPD capacity. | Anonymous future tranches have not been reconciled to every signed contract.
F07 | Retained assumption | Material | Opening fleet in 2030 | The opening fleet assumes delivery of the outlook forecast and retention of listed old assets through 2030. | It is a conditional forecast baseline, not a contracted-only floor.
F08 | Retained assumption | Material | Nuclear delivery and cost | The agreed £1.8 billion repeat-SMR cost and commissioning ramp of 2, 4, 6, then 8 units per year remain policy assumptions. | Advance rollout orders overlap pilot construction and precede operating evidence. The 2021 manufacturer target is assigned to 2024 prices by convention. Neither this cost nor the eight-unit annual ramp is demonstrated delivery.
F09 | Clarified | Material | Weather and security | Seven chronological weather/demand shapes are normalised to annual output. Dispatch has perfect information within its look-ahead horizon. | The screens do not establish probabilistic reliability, real-time forecast performance or frequency stability.
F10 | Clarified | Material | Cost boundary | The headline subtotal covers generation and storage. Network and fuel-infrastructure allowances are separate partial overlays. | Connections, offshore transmission, distribution, location and retail are incomplete. This is not a full system cost or household bill.
F11 | Retained assumption | Material | Inherited capital valuation | Inherited assets retain a generic replacement-cost annuity while operating. | This is not their actual outstanding debt or new Treasury spending. Common 4.5% financing applies to new projects.
F12 | Retained assumption | Material | Solar capacity and yield | Inherited solar uses a 12% yield calibrated to 2030, then declines. New solar uses 10.5% against DC panel capacity and a 1.25 DC/AC ratio. | Inherited capacity measurement is not fully harmonised. The combined GW figure is not a pure AC export-capacity measure.
F13 | Clarified | Material | Government comparison | The alternative preset combines 2030 ambitions with an analyst-defined continuation and includes named nuclear projects. | The government renewables continuation now includes costed gas adequacy top-ups. New gas starts in 2029; earlier supply gaps remain explicitly unresolved. Domestic-alone failures remain separately visible. Hydrogen, CCS, long-duration storage and demand flexibility are incompletely represented; the separate 5% gas diagnostic can fail.
F14 | Checked | Important | Funding ledger | RO, FIT, CfD settlements and carbon tax are separated from physical resource costs. | Legacy eligible output does not automatically change with physical retirements or trade. Nuclear support contracts are outside this renewable ledger.
F15 | Clarified | Documentation | Active and historical results | This audit covers the six current plans and their active calculation path. Earlier experimental outputs retain their original assumptions. | Use the v1.28 editor and audit tables for current comparisons.
F16 | Corrected | Small | Repowered wind sites | Five obsolete REPD entries at four sites totalled 30.7 MW. They are excluded; replacements remain. Hagshaw Hill replacement capacity is updated from 84 MW to the operator's rounded 80 MW. | The national 2030 total is preserved by reconciling the residual to official stock. Other project dates remain source records or labelled estimates.
F17 | Checked | Small | Repeated battery site names | The two 15 MW Buxton records and two 50 MW initial Minety records are retained as separate physical units, supported by developer/network evidence. | A repeated site name is not sufficient evidence of a duplicate. Project-specific storage duration remains a common model proxy.
F18 | Corrected | Material | Offshore construction | New offshore construction uses DESNZ 2025 Annex A 2030 construction £2,500/kW in real 2024 prices. The separate £170/kW pre-development line is excluded. | Offshore electrical/transmission scope remains to be reconciled with the separate wider-network overlay.
F19 | Corrected | Material | Gas additions for matched supply | Both families use the same nine import-inclusive screens. New gas orders start in 2029 with four-year lead and at most eight stations/year. Total gas-unit counts are preserved. | Unverified pre-2029 gas orders are deferred. Earlier gaps are not claimed closed. Gas fuel deliverability remains separate; the 5% diagnostic can fail.
F20 | Corrected | Verification | Current regression fixtures | The three reported failures are repaired. Lifecycle and construction tests use the nine-case protocol. Integration and inherited-capacity fixtures are generated from current inputs. | Calculation and DOM tests pass. A graphical Chromium run was unavailable because the browser download failed; no screenshot inspection is claimed.
F21 | Corrected | Material | 2029 start constraint | The rejected pre-2029 bridge is removed. Three other unverified earlier gas orders are also deferred to the earliest spare slots from 2029. All six plans contain zero gas orders before 2029. | First new gas commissions in 2033. Transition shortages remain unresolved under the chosen lead times, fleet and import assumptions.
F22 | Implemented | Material | Connected stress imports | The 28-day stress limits foreign availability to 30% of the entered interconnector capacity, about 3GW delivered at defaults. Scarcity purchases preserve domestic operating headroom. | Imports provide no inertia or reserve credit. Actual foreign supply and cable availability are uncertain; passing these cases is conditional, not a reliability probability.
F23 | Corrected | Material | Coal operating commitment | Economic dispatch left the proposed 2 GW coal station idle in 2050 in low and central demand cases. The proposed presets now explicitly keep it running when available from 2035, with physical fuel, imports, gas displacement, emissions and costs recalculated. | 85% availability is a smooth allowance; mine delivery and fuel stocks remain assumptions. Coal operation may increase curtailment of other sources. This is a policy choice rather than an optimised dispatch result.
F24 | Recorded | Material | Binding clean-generation share and gas-firmed comparison | The target case now enforces at most five-percent gas in each annual replay and records resulting shortages. The same gas fleet remains installed. The gas-firmed alternative retains unrestricted gas dispatch and additional capacity. | Unserved electricity is unpriced; adequate and shortage cases are not equal-service cost comparisons. Official flexibility and interconnection expansions remain incomplete. Allocation is controller-dependent, not an impossibility proof.
F25 | Amended | Material | Pilot gate replaces advance SMR rollout | Separate Wylfa pilot units are retained. Repeat orders begin conditionally in 2034; first repeat output is 2039. Four coal stations (M49) and one large-reactor sensitivity bridge part of the delay. No additional gas is silently inserted. | A 2034 evidence gate precedes first pilot operation; it cannot establish proven operating performance. Delivery, fuel security and any remaining supply gaps remain conditions.
F26 | Estimate | Material | Large-reactor cost and readiness | French programme-budget proxy, not a UK single-reactor tender or a clean EPC quote. General UK CPI and a provisional currency conversion are estimation conventions. Programme engineering and shared-site scope cannot be cleanly stripped out; no separate development deduction has been invented. Borrowing costs are calculated separately. | User-selected seven-year construction case plus one-year reformed planning. EDF's 70-month ambition is a repeat-build improvement target, not demonstrated first UK EPR2 delivery. Assumes design acceptance, site and supply-chain readiness; no UK EPR2 consent asserted. Uses the existing new-nuclear INL moderate SMR fixed, variable and fuel allowances as an explicit temporary proxy. This is not an EPR2 operating-cost quote. Availability and the two-GW synthetic outage screen retain the existing model conventions.
F27 | Implemented with explicit assumptions | Dispatch, gas use, shortages and OPEX | Electrolysis flexibility | All nine plans now shift electrolysis within finite daily energy and capacity limits; annual energy and all generation orders are preserved. Buffer chronology is cyclic. Fixed-load reference results are retained for comparison. | Capacity and buffer are assumptions, not a delivery commitment. Hydrogen infrastructure and cycling costs are excluded unless an allowance is entered. No seasonal flexibility, hydrogen-to-power or joint gas-quota optimisation is claimed. Shortages are not produced hydrogen.
F28 | Historical stage retained | Gas construction, finance, fixed costs and dispatch | Gas fleet resized after flexible electrolysis | Historical CCGT-only resizing after flexible electrolysis remains archived. Current plans use M48 mixed gas and M49 additional coal. | Read current mixed-gas comparison; old station counts are not current procurement totals.
F29 | Implemented and tested | Construction, fuel, OPEX, reliability and equipment diversity | Mixed gas and four-coal programme | OCGT and modular engine options have separate dispatch and cost inputs. Six supply-first schedules resize; our programme adds coal stations in 2037/38. Two-coal mixed-gas controls isolate the coal change. Existing target plans stay unchanged. | Supplier allocations and fuel-delivery contracts are unconfirmed. Balanced CCGT share is a tested procurement scenario, not a global optimum. Coal central capex has high transfer uncertainty; higher-cost sensitivity retained. Early shortages remain separately visible.

## Assumptions
Assumptions and evidence status
Values are resolved active defaults or labelled sensitivities. Source IDs refer to the Sources sheet; model files provide exact provenance. Policy assumptions and estimates are not quotations or forecasts.
Area | Assumption | Value | Unit | Status | Basis | Method | Source | Location
Scope | Model horizon | 2030–2050 | calendar years | Convention | Construction cash also includes pre 2029 and post 2050 commitments. | M01 | Policy choice | planner/data.json
Scope | Price base | 2024 | GBP real base year | Convention | Nominal carbon tax deflated separately. No actual household tariff. | M26 | Model convention | assumptions.json
Finance | New project financing | 0.045 | real fraction/year | Policy assumption | Editable; common to all new technologies. Not a lender quote. | M22 | User choice | planner/data.json:finance_rate
Finance | Planning duration | 1 | year | Policy assumption | Conditional on reforms; planning costs still require an allowance. | M21 | User choice | planner/finance.py
nuclear | Reference unit | 0.47 | GW | Policy/analyst assumption | Retains the agreed £1.8 bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections. | M01 | S032 | planner/data.json:technologies.nuclear.unit_gw
nuclear | Total lead | 5 | years | Policy/analyst assumption | Includes 1 planningyear | M21 | S032 | planner/data.json:technologies.nuclear.lead
nuclear | Operating life | 60 | years | Policy/analyst assumption | Operating and financing life are separate editable fields. | M01 | S032 | planner/data.json:technologies.nuclear.life
nuclear | Capital recovery | 60 | years | Policy/analyst assumption | Operating and financing life are separate editable fields. | M22 | S032 | planner/data.json:technologies.nuclear.recovery
nuclear | UI delivery warning threshold | 4 | GW/year | Policy/analyst assumption | Preset commissioning limits may be tighter; exceeding a UI threshold warns, does not block. | M30 | S032 | planner/data.json:technologies.nuclear.annual_limit_gw
nuclear | low overnight capital | 3.8298 | £bn/GW | Policy assumption | Policy assumption; construction scope unverified Low/high are reference alternatives, not confidence limits. | M20 | S032 | planner/data.json:technologies.nuclear.capex_bn_per_gw.low
nuclear | central overnight capital | 3.8298 | £bn/GW | Policy assumption | Policy assumption; construction scope unverified Low/high are reference alternatives, not confidence limits. | M20 | S032 | planner/data.json:technologies.nuclear.capex_bn_per_gw.central
nuclear | high overnight capital | 4.5951 | £bn/GW | Policy assumption | Policy assumption; construction scope unverified Low/high are reference alternatives, not confidence limits. | M20 | S032 | planner/data.json:technologies.nuclear.capex_bn_per_gw.high
nuclear | Potential utilisation | 0.9 | fraction | Yield/availability assumption | Explanatory potential, not dependable capacity or guaranteed dispatch. | M08 | DESNZ2025 AnnexA2030 column; data/raw/desnz_costs_2025.xlsx | planner/data.json
nuclear | Fixed operations | 120.9551 | £/kW-year | Source-derived proxy | INL moderate SMR estimates; notRRquote | M24 | S034 | planner/data.json
gas | Reference unit | 0.92 | GW | Policy/analyst assumption | PLN 6,378 m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption. | M01 | S027 | planner/data.json:technologies.gas.unit_gw
gas | Total lead | 4 | years | Policy/analyst assumption | Includes 1 planningyear | M21 | S027 | planner/data.json:technologies.gas.lead
gas | Operating life | 35 | years | Policy/analyst assumption | Operating and financing life are separate editable fields. | M01 | S027 | planner/data.json:technologies.gas.life
gas | Capital recovery | 35 | years | Policy/analyst assumption | Operating and financing life are separate editable fields. | M22 | S027 | planner/data.json:technologies.gas.recovery
gas | UI delivery warning threshold | 8 | GW/year | Policy/analyst assumption | Preset commissioning limits may be tighter; exceeding a UI threshold warns, does not block. | M30 | S027 | planner/data.json:technologies.gas.annual_limit_gw
gas | low overnight capital | 0.68062 | £bn/GW | Source-derived proxy | Recent EPC proxy; associated infrastructure not fully separated Low/high are reference alternatives, not confidence limits. | M20 | S027 | planner/data.json:technologies.gas.capex_bn_per_gw.low
gas | central overnight capital | 0.95344 | £bn/GW | Source-derived proxy | Recent EPC proxy; associated infrastructure not fully separated Low/high are reference alternatives, not confidence limits. | M20 | S027 | planner/data.json:technologies.gas.capex_bn_per_gw.central
gas | high overnight capital | 0.95344 | £bn/GW | Source-derived proxy | Recent EPC proxy; associated infrastructure not fully separated Low/high are reference alternatives, not confidence limits. | M20 | S027 | planner/data.json:technologies.gas.capex_bn_per_gw.high
gas | Potential utilisation | 0.9 | fraction | Yield/availability assumption | Explanatory potential, not dependable capacity or guaranteed dispatch. | M08 | DESNZ2025 AnnexA2030 column; data/raw/desnz_costs_2025.xlsx | planner/data.json
gas | Fixed operations | 18.5 | £/kW-year | Source-derived proxy | DESNZ allowance excluding network use charges | M24 | DESNZ2025 AnnexA2030 column; data/raw/desnz_costs_2025.xlsx | planner/data.json
coal | Reference unit | 2 | GW | Policy/analyst assumption | PLN 5,100 m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine. | M01 | S028 | planner/data.json:technologies.coal.unit_gw
coal | Total lead | 6 | years | Policy/analyst assumption | Includes 1 planningyear | M21 | S028 | planner/data.json:technologies.coal.lead
coal | Operating life | 50 | years | Policy/analyst assumption | Operating and financing life are separate editable fields. | M01 | S028 | planner/data.json:technologies.coal.life
coal | Capital recovery | 50 | years | Policy/analyst assumption | Operating and financing life are separate editable fields. | M22 | S028 | planner/data.json:technologies.coal.recovery
coal | UI delivery warning threshold | 2 | GW/year | Policy/analyst assumption | Preset commissioning limits may be tighter; exceeding a UI threshold warns, does not block. | M30 | S028 | planner/data.json:technologies.coal.annual_limit_gw
coal | low overnight capital | 1.3754 | £bn/GW | Source-derived proxy | Older European contract proxy; high UK transfer uncertainty Low/high are reference alternatives, not confidence limits. | M20 | S028 | planner/data.json:technologies.coal.capex_bn_per_gw.low
coal | central overnight capital | 1.3754 | £bn/GW | Source-derived proxy | Older European contract proxy; high UK transfer uncertainty Low/high are reference alternatives, not confidence limits. | M20 | S028 | planner/data.json:technologies.coal.capex_bn_per_gw.central
coal | high overnight capital | 3.1188 | £bn/GW | Source-derived proxy | Older European contract proxy; high UK transfer uncertainty Low/high are reference alternatives, not confidence limits. | M20 | S028 | planner/data.json:technologies.coal.capex_bn_per_gw.high
coal | Potential utilisation | 0.85 | fraction | Yield/availability assumption | Explanatory potential, not dependable capacity or guaranteed dispatch. | M08 | DESNZ2025 AnnexA2030 column; data/raw/desnz_costs_2025.xlsx | planner/data.json
coal | Fixed operations | 50.8405 | £/kW-year | Source-derived proxy | EIA UScoalproxy | M24 | S029 | planner/data.json
offshore | Reference unit | 1 | GW | Policy/analyst assumption | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total. | M01 | S031 | planner/data.json:technologies.offshore.unit_gw
offshore | Total lead | 4 | years | Policy/analyst assumption | Includes 1 planningyear | M21 | S031 | planner/data.json:technologies.offshore.lead
offshore | Operating life | 30 | years | Policy/analyst assumption | Operating and financing life are separate editable fields. | M01 | S031 | planner/data.json:technologies.offshore.life
offshore | Capital recovery | 30 | years | Policy/analyst assumption | Operating and financing life are separate editable fields. | M22 | S031 | planner/data.json:technologies.offshore.recovery
offshore | UI delivery warning threshold | 4 | GW/year | Policy/analyst assumption | Preset commissioning limits may be tighter; exceeding a UI threshold warns, does not block. | M30 | S031 | planner/data.json:technologies.offshore.annual_limit_gw
offshore | low overnight capital | 2.1 | £bn/GW | Source-derived proxy | DESNZ construction category; 2024 real GBP; pre-development excluded Low/high are reference alternatives, not confidence limits. | M20 | S031 | planner/data.json:technologies.offshore.capex_bn_per_gw.low
offshore | central overnight capital | 2.5 | £bn/GW | Source-derived proxy | DESNZ construction category; 2024 real GBP; pre-development excluded Low/high are reference alternatives, not confidence limits. | M20 | S031 | planner/data.json:technologies.offshore.capex_bn_per_gw.central
offshore | high overnight capital | 3.1 | £bn/GW | Source-derived proxy | DESNZ construction category; 2024 real GBP; pre-development excluded Low/high are reference alternatives, not confidence limits. | M20 | S031 | planner/data.json:technologies.offshore.capex_bn_per_gw.high
offshore | Potential utilisation | 0.48 | fraction | Yield/availability assumption | Explanatory potential, not dependable capacity or guaranteed dispatch. | M08 | DESNZ2025 AnnexA2030 column; data/raw/desnz_costs_2025.xlsx | planner/data.json
offshore | Fixed operations | 54.9 | £/kW-year | Source-derived proxy | DESNZ allowance excluding network use charges | M24 | DESNZ2025 AnnexA2030 column; data/raw/desnz_costs_2025.xlsx | planner/data.json
onshore | Reference unit | 0.1 | GW | Policy/analyst assumption | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate. | M01 | S030 | planner/data.json:technologies.onshore.unit_gw
onshore | Total lead | 2 | years | Policy/analyst assumption | Includes 1 planningyear | M21 | S030 | planner/data.json:technologies.onshore.lead
onshore | Operating life | 25 | years | Policy/analyst assumption | Operating and financing life are separate editable fields. | M01 | S030 | planner/data.json:technologies.onshore.life
onshore | Capital recovery | 25 | years | Policy/analyst assumption | Operating and financing life are separate editable fields. | M22 | S030 | planner/data.json:technologies.onshore.recovery
onshore | UI delivery warning threshold | 3 | GW/year | Policy/analyst assumption | Preset commissioning limits may be tighter; exceeding a UI threshold warns, does not block. | M30 | S030 | planner/data.json:technologies.onshore.annual_limit_gw
onshore | low overnight capital | 0.98809 | £bn/GW | Source-derived proxy | UK construction category, separated from infrastructure and development Low/high are reference alternatives, not confidence limits. | M20 | S030 | planner/data.json:technologies.onshore.capex_bn_per_gw.low
onshore | central overnight capital | 1.2354 | £bn/GW | Source-derived proxy | UK construction category, separated from infrastructure and development Low/high are reference alternatives, not confidence limits. | M20 | S030 | planner/data.json:technologies.onshore.capex_bn_per_gw.central
onshore | high overnight capital | 1.6448 | £bn/GW | Source-derived proxy | UK construction category, separated from infrastructure and development Low/high are reference alternatives, not confidence limits. | M20 | S030 | planner/data.json:technologies.onshore.capex_bn_per_gw.high
onshore | Potential utilisation | 0.36 | fraction | Yield/availability assumption | Explanatory potential, not dependable capacity or guaranteed dispatch. | M08 | DESNZ2025 AnnexA2030 column; data/raw/desnz_costs_2025.xlsx | planner/data.json
onshore | Fixed operations | 22.2 | £/kW-year | Source-derived proxy | DESNZ allowance excluding network use charges | M24 | DESNZ2025 AnnexA2030 column; data/raw/desnz_costs_2025.xlsx | planner/data.json
solar | Reference unit | 0.1 | GW | Policy/analyst assumption | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a 1.25 DC/AC ratio; inherited measurement basis is separately disclosed. | M01 | S030 | planner/data.json:technologies.solar.unit_gw
solar | Total lead | 2 | years | Policy/analyst assumption | Includes 1 planningyear | M21 | S030 | planner/data.json:technologies.solar.lead
solar | Operating life | 30 | years | Policy/analyst assumption | Operating and financing life are separate editable fields. | M01 | S030 | planner/data.json:technologies.solar.life
solar | Capital recovery | 30 | years | Policy/analyst assumption | Operating and financing life are separate editable fields. | M22 | S030 | planner/data.json:technologies.solar.recovery
solar | UI delivery warning threshold | 5 | GW/year | Policy/analyst assumption | Preset commissioning limits may be tighter; exceeding a UI threshold warns, does not block. | M30 | S030 | planner/data.json:technologies.solar.annual_limit_gw
solar | low overnight capital | 0.43402 | £bn/GW | Source-derived proxy | UK construction category, separated from infrastructure and development Low/high are reference alternatives, not confidence limits. | M20 | S030 | planner/data.json:technologies.solar.capex_bn_per_gw.low
solar | central overnight capital | 0.5356 | £bn/GW | Source-derived proxy | UK construction category, separated from infrastructure and development Low/high are reference alternatives, not confidence limits. | M20 | S030 | planner/data.json:technologies.solar.capex_bn_per_gw.central
solar | high overnight capital | 0.61666 | £bn/GW | Source-derived proxy | UK construction category, separated from infrastructure and development Low/high are reference alternatives, not confidence limits. | M20 | S030 | planner/data.json:technologies.solar.capex_bn_per_gw.high
solar | Potential utilisation | 0.105 | fraction | Yield/availability assumption | Explanatory potential, not dependable capacity or guaranteed dispatch. | M08 | DESNZ2025 AnnexA2030 column; data/raw/desnz_costs_2025.xlsx | planner/data.json
solar | Fixed operations | 7.5 | £/kW-year | Source-derived proxy | DESNZ allowance excluding network use charges | M24 | DESNZ2025 AnnexA2030 column; data/raw/desnz_costs_2025.xlsx | planner/data.json
battery | Reference unit | 1 | GW | Policy/analyst assumption | Existing storage assumptions: battery power and energy priced separately; no distinct low/high cost evidence supplied. | M01 | Analyst estimate | planner/data.json:technologies.battery.unit_gw
battery | Total lead | 2 | years | Policy/analyst assumption | Includes 1 planningyear | M21 | Analyst estimate | planner/data.json:technologies.battery.lead
battery | Operating life | 15 | years | Policy/analyst assumption | Operating and financing life are separate editable fields. | M01 | Analyst estimate | planner/data.json:technologies.battery.life
battery | Capital recovery | 15 | years | Policy/analyst assumption | Operating and financing life are separate editable fields. | M22 | Analyst estimate | planner/data.json:technologies.battery.recovery
battery | UI delivery warning threshold | 5 | GW/year | Policy/analyst assumption | Preset commissioning limits may be tighter; exceeding a UI threshold warns, does not block. | M30 | Analyst estimate | planner/data.json:technologies.battery.annual_limit_gw
battery | low overnight capital | 0.2 | £bn/GW | Analyst estimate | Existing storage assumptions: battery power and energy priced separately; no distinct low/high cost evidence supplied. Low/high are reference alternatives, not confidence limits. | M20 | Analyst estimate | planner/data.json:technologies.battery.capex_bn_per_gw.low
battery | central overnight capital | 0.2 | £bn/GW | Analyst estimate | Existing storage assumptions: battery power and energy priced separately; no distinct low/high cost evidence supplied. Low/high are reference alternatives, not confidence limits. | M20 | Analyst estimate | planner/data.json:technologies.battery.capex_bn_per_gw.central
battery | high overnight capital | 0.2 | £bn/GW | Analyst estimate | Existing storage assumptions: battery power and energy priced separately; no distinct low/high cost evidence supplied. Low/high are reference alternatives, not confidence limits. | M20 | Analyst estimate | planner/data.json:technologies.battery.capex_bn_per_gw.high
battery | Energy capital component | 0.15 | £bn/GWh | Analyst estimate | Add power and energy terms.4 hour reference battery. | M20 | Analyst estimate | planner/data.json
battery | Fixed operations | 10 | £/kW-year | Source-derived proxy | Analyst storage allowance | M24 | DESNZ2025 AnnexA2030 column; data/raw/desnz_costs_2025.xlsx | planner/data.json
gas | availability | 0.9 | See field suffix | Analyst operating assumption | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates. | M11 | Analyst estimate | assumptions.json:gas.availability
gas | unit gw | 0.5 | See field suffix | Analyst operating assumption | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates. | M11 | Analyst estimate | assumptions.json:gas.unit_gw
gas | min load fraction | 0.4 | See field suffix | Analyst operating assumption | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates. | M11 | Analyst estimate | assumptions.json:gas.min_load_fraction
gas | min up hours | 4 | See field suffix | Analyst operating assumption | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates. | M11 | Analyst estimate | assumptions.json:gas.min_up_hours
gas | min down hours | 2 | See field suffix | Analyst operating assumption | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates. | M11 | Analyst estimate | assumptions.json:gas.min_down_hours
gas | start lead hours | 2 | See field suffix | Analyst operating assumption | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates. | M11 | Analyst estimate | assumptions.json:gas.start_lead_hours
gas | ramp fraction per hour | 0.6 | See field suffix | Analyst operating assumption | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates. | M11 | Analyst estimate | assumptions.json:gas.ramp_fraction_per_hour
gas | efficiency full lhv | 0.58 | See field suffix | Analyst operating assumption | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates. | M11 | Analyst estimate | assumptions.json:gas.efficiency_full_lhv
gas | efficiency at min load lhv | 0.47 | See field suffix | Analyst operating assumption | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates. | M11 | Analyst estimate | assumptions.json:gas.efficiency_at_min_load_lhv
gas | start fuel mwh per mw | 1.5 | See field suffix | Analyst operating assumption | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates. | M11 | Analyst estimate | assumptions.json:gas.start_fuel_mwh_per_mw
gas | start wear gbp per mw | 30 | See field suffix | Analyst operating assumption | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates. | M11 | Analyst estimate | assumptions.json:gas.start_wear_gbp_per_mw
gas | fuel gbp mwh lhv | 30 | See field suffix | Analyst operating assumption | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates. | M11 | Analyst estimate | assumptions.json:gas.fuel_gbp_mwh_lhv
gas | co 2 t per mwh fuel lhv | 0.202 | See field suffix | Analyst operating assumption | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates. | M11 | Analyst estimate | assumptions.json:gas.co2_t_per_mwh_fuel_lhv
coal | availability | 0.85 | See field suffix | Analyst operating assumption | Representativeblock assumptions; not calibrated to a UK station. | M12 | Analyst estimate | coal_assumptions.json:coal.availability
coal | unit gw | 0.5 | See field suffix | Analyst operating assumption | Representativeblock assumptions; not calibrated to a UK station. | M12 | Analyst estimate | coal_assumptions.json:coal.unit_gw
coal | min load fraction | 0.4 | See field suffix | Analyst operating assumption | Representativeblock assumptions; not calibrated to a UK station. | M12 | Analyst estimate | coal_assumptions.json:coal.min_load_fraction
coal | min up hours | 12 | See field suffix | Analyst operating assumption | Representativeblock assumptions; not calibrated to a UK station. | M12 | Analyst estimate | coal_assumptions.json:coal.min_up_hours
coal | min down hours | 8 | See field suffix | Analyst operating assumption | Representativeblock assumptions; not calibrated to a UK station. | M12 | Analyst estimate | coal_assumptions.json:coal.min_down_hours
coal | start lead hours | 8 | See field suffix | Analyst operating assumption | Representativeblock assumptions; not calibrated to a UK station. | M12 | Analyst estimate | coal_assumptions.json:coal.start_lead_hours
coal | ramp fraction per hour | 0.25 | See field suffix | Analyst operating assumption | Representativeblock assumptions; not calibrated to a UK station. | M12 | Analyst estimate | coal_assumptions.json:coal.ramp_fraction_per_hour
coal | efficiency full lhv | 0.4 | See field suffix | Analyst operating assumption | Representativeblock assumptions; not calibrated to a UK station. | M12 | Analyst estimate | coal_assumptions.json:coal.efficiency_full_lhv
coal | efficiency min lhv | 0.33 | See field suffix | Analyst operating assumption | Representativeblock assumptions; not calibrated to a UK station. | M12 | Analyst estimate | coal_assumptions.json:coal.efficiency_min_lhv
coal | start fuel mwh per mw | 5 | See field suffix | Analyst operating assumption | Representativeblock assumptions; not calibrated to a UK station. | M12 | Analyst estimate | coal_assumptions.json:coal.start_fuel_mwh_per_mw
coal | inertia seconds | 5 | See field suffix | Analyst operating assumption | Representativeblock assumptions; not calibrated to a UK station. | M12 | Analyst estimate | coal_assumptions.json:coal.inertia_seconds
coal | heat content mwh tonne | 6.7 | See field suffix | Analyst operating assumption | Representativeblock assumptions; not calibrated to a UK station. | M12 | Analyst estimate | coal_assumptions.json:coal.heat_content_mwh_tonne
coal | co 2 t mwh fuel | 0.34 | See field suffix | Analyst operating assumption | Representativeblock assumptions; not calibrated to a UK station. | M12 | Analyst estimate | coal_assumptions.json:coal.co2_t_mwh_fuel
coal | fuel gbp tonne | 100 | See field suffix | Analyst operating assumption | Representativeblock assumptions; not calibrated to a UK station. | M12 | Analyst estimate | coal_assumptions.json:coal.fuel_gbp_tonne
coal | start wear gbp mw | 50 | See field suffix | Analyst operating assumption | Representativeblock assumptions; not calibrated to a UK station. | M12 | Analyst estimate | coal_assumptions.json:coal.start_wear_gbp_mw
coal | stock days full output | 30 | See field suffix | Analyst operating assumption | Representativeblock assumptions; not calibrated to a UK station. | M12 | Analyst estimate | coal_assumptions.json:coal.stock_days_full_output
coal | domestic supply mt year | 0 | See field suffix | Analyst operating assumption | Representativeblock assumptions; not calibrated to a UK station. | M12 | Analyst estimate | coal_assumptions.json:coal.domestic_supply_mt_year
coal | domestic alternative mt year | 5 | See field suffix | Analyst operating assumption | Representativeblock assumptions; not calibrated to a UK station. | M12 | Analyst estimate | coal_assumptions.json:coal.domestic_alternative_mt_year
Operations | reserve gw | 2 | See field suffix | Analyst screen/proxy | No dynamic or regional stability claim. | M15 | Analyst estimate | assumptions.json:operations.reserve_gw
Operations | minimum inertia gws | 120 | See field suffix | Analyst screen/proxy | No dynamic or regional stability claim. | M15 | Analyst estimate | assumptions.json:operations.minimum_inertia_gws
Operations | nuclear inertia seconds | 5 | See field suffix | Analyst screen/proxy | No dynamic or regional stability claim. | M15 | Analyst estimate | assumptions.json:operations.nuclear_inertia_seconds
Operations | gas inertia seconds | 5 | See field suffix | Analyst screen/proxy | No dynamic or regional stability claim. | M15 | Analyst estimate | assumptions.json:operations.gas_inertia_seconds
Operations | external inertia gws | 0 | See field suffix | Analyst screen/proxy | No dynamic or regional stability claim. | M15 | Analyst estimate | assumptions.json:operations.external_inertia_gws
Operations | nuclear availability | 0.9 | See field suffix | Analyst screen/proxy | No dynamic or regional stability claim. | M15 | Analyst estimate | assumptions.json:operations.nuclear_availability
Operations | other cost gbp mwh | 80 | See field suffix | Analyst screen/proxy | No dynamic or regional stability claim. | M15 | Analyst estimate | assumptions.json:operations.other_cost_gbp_mwh
Shared | Pooled round-trip efficiency | 0.8 | fraction | Policy/analyst assumption | Overrides core 85% storage setting. | M13 | See sourcefiles; analyst conventions | programme/config.json
Shared | Storage forecast horizon | 48 | hours | Policy/analyst assumption | Perfect within-horizon information. | M13 | See sourcefiles; analyst conventions | operations/config.json
Shared | Storage discretionary reserve | 0.2 | fraction | Policy/analyst assumption | Mandatory shortage support can use reserve. | M13 | See sourcefiles; analyst conventions | operations/config.json
Shared | Solar degradation | 0.008 | fraction/year | Policy/analyst assumption | 0.5–1% sensitivity; estimate for future panels. | M07 | See sourcefiles; analyst conventions | planner/lifecycle.json
Shared | Solar inverter interval | 15 | years | Policy/analyst assumption | Replacement before retirement. | M25 | See sourcefiles; analyst conventions | planner/lifecycle.json
Shared | Solar inverter cost fraction | 0.1 | fraction of original capital | Policy/analyst assumption | Provision within fixed O&M;not additive. | M25 | See sourcefiles; analyst conventions | planner/lifecycle.json
Shared | New solar DC/AC ratio | 1.25 | ratio | Policy/analyst assumption | Provisional; inherited capacity basis unresolved. | M07 | See sourcefiles; analyst conventions | planner/data.json
Shared | Nominal carbon tax | 10 | £/tCO 2 | Policy/analyst assumption | From 2031, separate transfer account. | M27 | See sourcefiles; analyst conventions | programme/config.json
Shared | Inflation for tax deflation | 0.02 | fraction/year | Policy/analyst assumption | Constant assumed inflation. | M27 | See sourcefiles; analyst conventions | programme/config.json
Trade | enabled | TRUE | fraction/flag | Analyst assumption | Constant real prices; identical defaults for both presets. | M18 | Analyst scenario | trade/dispatch.py:DEFAULTS.enabled
Trade | capacity gw | 10.3 | GW | Installed benchmark | Constant real prices; identical defaults for both presets. | M18 | Clean Flexibility Roadmap | trade/dispatch.py:DEFAULTS.capacity_gw
Trade | availability | 0.8 | fraction/flag | Analyst assumption | Constant real prices; identical defaults for both presets. | M18 | Analyst scenario | trade/dispatch.py:DEFAULTS.availability
Trade | scarcity availability | 0.3 | fraction/flag | Analyst assumption | Constant real prices; identical defaults for both presets. | M18 | Analyst scenario | trade/dispatch.py:DEFAULTS.scarcity_availability
Trade | loss | 0.03 | fraction/flag | Analyst assumption | Constant real prices; identical defaults for both presets. | M18 | Analyst scenario | trade/dispatch.py:DEFAULTS.loss
Trade | import price | 55 | £/MWh | Analyst assumption | Constant real prices; identical defaults for both presets. | M18 | Analyst scenario | trade/dispatch.py:DEFAULTS.import_price
Trade | scarcity price | 120 | £/MWh | Analyst assumption | Constant real prices; identical defaults for both presets. | M18 | Analyst scenario | trade/dispatch.py:DEFAULTS.scarcity_price
Trade | export price | 35 | £/MWh | Analyst assumption | Constant real prices; identical defaults for both presets. | M18 | Analyst scenario | trade/dispatch.py:DEFAULTS.export_price
Trade | surplus export price | 10 | £/MWh | Analyst assumption | Constant real prices; identical defaults for both presets. | M18 | Analyst scenario | trade/dispatch.py:DEFAULTS.surplus_export_price
Trade | export acceptance | 0.8 | fraction/flag | Analyst assumption | Constant real prices; identical defaults for both presets. | M18 | Analyst scenario | trade/dispatch.py:DEFAULTS.export_acceptance
Stress | low wind multiplier | 0.8 | See field suffix | Synthetic scenario | Current suite uses cold-calm plus 2 GW nuclear outage; gas/coal disruption cases are separate older experiments. | M16 | Analyst scenario | programme/config.json:stress.low_wind_multiplier
Stress | cold spell days | 28 | See field suffix | Synthetic scenario | Current suite uses cold-calm plus 2 GW nuclear outage; gas/coal disruption cases are separate older experiments. | M16 | Analyst scenario | programme/config.json:stress.cold_spell_days
Stress | cold demand multiplier | 1.1 | See field suffix | Synthetic scenario | Current suite uses cold-calm plus 2 GW nuclear outage; gas/coal disruption cases are separate older experiments. | M16 | Analyst scenario | programme/config.json:stress.cold_demand_multiplier
Stress | cold wind multiplier | 0.15 | See field suffix | Synthetic scenario | Current suite uses cold-calm plus 2 GW nuclear outage; gas/coal disruption cases are separate older experiments. | M16 | Analyst scenario | programme/config.json:stress.cold_wind_multiplier
Stress | cold solar multiplier | 0.5 | See field suffix | Synthetic scenario | Current suite uses cold-calm plus 2 GW nuclear outage; gas/coal disruption cases are separate older experiments. | M16 | Analyst scenario | programme/config.json:stress.cold_solar_multiplier
Stress | nuclear loss gw | 2 | See field suffix | Synthetic scenario | Current suite uses cold-calm plus 2 GW nuclear outage; gas/coal disruption cases are separate older experiments. | M16 | Analyst scenario | programme/config.json:stress.nuclear_loss_gw
Stress | gas capacity fraction | 0.5 | See field suffix | Synthetic scenario | Current suite uses cold-calm plus 2 GW nuclear outage; gas/coal disruption cases are separate older experiments. | M16 | Analyst scenario | programme/config.json:stress.gas_capacity_fraction
Stress | outage draws | 12 | See field suffix | Synthetic scenario | Current suite uses cold-calm plus 2 GW nuclear outage; gas/coal disruption cases are separate older experiments. | M16 | Analyst scenario | programme/config.json:stress.outage_draws
Stress | outage seed | 271828 | See field suffix | Synthetic scenario | Current suite uses cold-calm plus 2 GW nuclear outage; gas/coal disruption cases are separate older experiments. | M16 | Analyst scenario | programme/config.json:stress.outage_seed
Stress | weather years | [2019,2024] | See field suffix | Synthetic scenario | Current suite uses cold-calm plus 2 GW nuclear outage; gas/coal disruption cases are separate older experiments. | M16 | Analyst scenario | programme/config.json:stress.weather_years
Other | Biomass, including biomass CHP | 7.3807 | TWh/year | NESO outlook input | Flat hourly output, maintained through 2050; all-in£80/MWh proxy. | M24 | data/evidence/tyo2026_es1.csv | fleet/other_display.json
Other | Waste, including waste CHP | 10.5345 | TWh/year | NESO outlook input | Flat hourly output, maintained through 2050; all-in£80/MWh proxy. | M24 | data/evidence/tyo2026_es1.csv | fleet/other_display.json
Other | Conventional hydro | 3.6224 | TWh/year | NESO outlook input | Flat hourly output, maintained through 2050; all-in£80/MWh proxy. | M24 | data/evidence/tyo2026_es1.csv | fleet/other_display.json
Other | Other renewables: marine and geothermal | 0.24749 | TWh/year | NESO outlook input | Flat hourly output, maintained through 2050; all-in£80/MWh proxy. | M24 | data/evidence/tyo2026_es1.csv | fleet/other_display.json
Fleet | Sizewell B retirement | 2055 | year | Conditional announced extension | July 2026 heads of terms; final contract and approvals remain conditions. | M01 | S055 | programme/config.json:opening_cohorts
Fleet | Old listed asset retention floor | 2031 | year | Strong baseline assumption | Current listings assumed retained into 2030 even if generic age limit exceeded. This is not an operator promise. | M01 | Analyst estimate | fleet/build.py
Fleet | Missing operational date | 2018 | year | Estimate | Fallback for missing REPD dates; exact 2018 dates are not necessarily missing. | M02 | REPD +analystfallback | fleet/build.py
Fleet | Unlisted future completion timing | Equal2027–2030 tranches | years | Estimate | Existing residual stock separated before this allocation. No signed contract claimed. | M02 | audit/sources; NESOoutlook | audit/apply.py
Nuclear | Repeat programme ramp | 2,4,6,then8 | SMRs/year 2035 onward | Policy assumption | Five-year repeat lead; factories/design/reform success assumed. Eight/year not a supplier commitment. | M30 | User policy choice | demand_plans/*.plan.json
Comparison | Government continuation | 2035targets scaled by demand thereafter | scenario rule | Analyst proxy | Includes Hinkley, Sizewell B/C and 3 SMRs; excludes unmodelled clean flexibility. | M30 | presets/assumptions.json | demand_plans/build.py
Support | Reference electricity prices | 40,70,100 | £2024/MWh | Analyst sensitivity | Fixed eligible output, signed CfD settlements; no dispatch-price link. | M29 | legacy/inputs.json | planner/accounts.py
Support | Treasury share from April 2030 | 1 | fraction | Policy choice | Funding transfer only; not added to resource costs. | M29 | User choice | planner/accounts.py
Support | RO GB allocation share | 0.94543 | fraction | Source-based proxy | 2024/25 GB share of ROCs held fixed. | M29 | OfgemROannualreport | legacy/inputs.json
Support | FIT tail zero | 2042 | financial year start | Estimate | Linear tail from 2036 published projection; no automatic 2050 zero for a missing CfD account. | M29 | DESNZprojection +analysttail | legacy/inputs.json
Programme timing | Earliest new gas order | 2029 | year | Policy constraint | No gas orders before government takes office. First new commissioning 2033; four-year lead; eight stations/year maximum. Inherited non-gas pipeline unchanged. | M35 | User instruction 18 October 2026 | security_imports/schedules.json
coal | Proposed-programme operating policy | baseload | dispatch choice | User policy instruction | Keep the single coal station on and generating. Existing 85% availability and fuel/stock parameters retained; no change to construction, retirement or new-gas orders. | M37 | Programme decision, 18 October 2026; existing availability in coal_assumptions.json | demand_plans/ours_{low,central,high}.plan.json:coal_dispatch
Target-gap comparison | low demand: added gas removed | 54.28 | GW | Analyst sensitivity | Same renewables, storage, named nuclear, baseline gas and trade as gas-firmed case. No annual output rationing. | M40 | Official ambition: S048/S050; plan derivation in validation/target_preset_changes.json | demand_plans/target_low.plan.json
Target-gap comparison | central demand: added gas removed | 66.24 | GW | Analyst sensitivity | Same renewables, storage, named nuclear, baseline gas and trade as gas-firmed case. No annual output rationing. | M40 | Official ambition: S048/S050; plan derivation in validation/target_preset_changes.json | demand_plans/target_central.plan.json
Target-gap comparison | high demand: added gas removed | 80.04 | GW | Analyst sensitivity | Same renewables, storage, named nuclear, baseline gas and trade as gas-firmed case. No annual output rationing. | M40 | Official ambition: S048/S050; plan derivation in validation/target_preset_changes.json | demand_plans/target_high.plan.json
Pilot-gated nuclear revision | First repeat-SMR order | 2034 | year | Policy/analyst assumption | Conditional pilot design/construction and factory evidence gate, preceding assumed first operation in 2035. | M41–M43 | EPR2-COST; EPR2-TECH; existing Wylfa and CPI references | planner/large_nuclear.json; demand_plans/ours_*.plan.json
Pilot-gated nuclear revision | First repeat-SMR output | 2039 | year | Policy/analyst assumption | One planning year plus four construction years after first repeat order. | M41–M43 | EPR2-COST; EPR2-TECH; existing Wylfa and CPI references | planner/large_nuclear.json; demand_plans/ours_*.plan.json
Pilot-gated nuclear revision | Repeat order ceiling | [2,4,6,8] | units/year | Policy/analyst assumption | First three order years 2034–36; max eight thereafter, reduced with demand. | M41–M43 | EPR2-COST; EPR2-TECH; existing Wylfa and CPI references | planner/large_nuclear.json; demand_plans/ours_*.plan.json
Pilot-gated nuclear revision | Coal station commissioning | [2035,2036,2037,2038] | years | Policy/analyst assumption | Four 2 GW stations, one per year under M49; domestic coal supply unchanged. | M41–M43 | EPR2-COST; EPR2-TECH; existing Wylfa and CPI references | planner/large_nuclear.json; demand_plans/ours_*.plan.json
Pilot-gated nuclear revision | Additional large reactor | 1.7 | GW | Policy/analyst assumption | One reactor ordered 2029; one planning plus seven build years; online 2037. | M41–M43 | EPR2-COST; EPR2-TECH; existing Wylfa and CPI references | planner/large_nuclear.json; demand_plans/ours_*.plan.json
Pilot-gated nuclear revision | Large-reactor capital conversion | {"source_programme_eur_bn_2020":72.8,"reactors":6,"gbp_per_eur_assumption":0.85,"uk_cpi_2020":108.7,"uk_cpi_2024":133.9} | inputs | Policy/analyst assumption | EDF French programme cost converted using a provisional GBP/EUR rate and general UK CPI; development/shared-site boundary unresolved. | M41–M43 | EPR2-COST; EPR2-TECH; existing Wylfa and CPI references | planner/large_nuclear.json; demand_plans/ours_*.plan.json
Gas-output constraint | Annual gas share | 5 | percent of eligible domestic generation | Binding target-case constraint | Gas output ceiling applies to each weather/mode replay from 2030; installed gas fleet retained. | M40; M44 | Clean Power 2030 ambition, existing sources S048/S050; explicit controller assumption | demand_plans/target_*.plan.json; operations/gas_budget.py
Gas-output constraint | Wylfa dates | [2035,2035,2035] | commissioning years | Analyst assumptions | Three 470 MW units assumed available together; first operational units officially targeted from mid-2030s, not confirmed all three in 2035. | M45 | WYLFA-DATES | demand_plans/*.plan.json
Electrolysis flexibility | Enable flexible electrolysis | TRUE | boolean | Explicit analyst assumption | Same setting in all nine presets; fixed-load option retained. | M46 | ELECTRO-FES; ELECTRO-DESNZ support flexibility, not quantitative defaults | electrolysis/config.json; demand_plans/*.plan.json
Electrolysis flexibility | Scheduling window | 24 | hours | Explicit analyst assumption | Energy fixed in each block; 1–168 hours editable; known within-window weather proxy. | M46 | ELECTRO-FES; ELECTRO-DESNZ support flexibility, not quantitative defaults | electrolysis/config.json; demand_plans/*.plan.json
Electrolysis flexibility | Electrical input capacity multiple | 2 | times average electrical load | Explicit analyst assumption | Explicit available-capacity estimate, not an official electrolyser delivery programme. Editable 1–4. | M46 | ELECTRO-FES; ELECTRO-DESNZ support flexibility, not quantitative defaults | electrolysis/config.json; demand_plans/*.plan.json
Electrolysis flexibility | Hydrogen buffer | 48 | hours of average production | Explicit analyst assumption | Twice scheduling window, initially half full, ending unchanged; electricity-equivalent inventory. Infrastructure must be provided. | M46 | ELECTRO-FES; ELECTRO-DESNZ support flexibility, not quantitative defaults | electrolysis/config.json; demand_plans/*.plan.json
Electrolysis flexibility | Additional flexibility allowance | 0 | real 2024 GBP/MWh electrolysis required | Explicit analyst assumption | Excluded by default; editable. Electrolyser, storage, compression and cycling costs are outside power subtotal unless represented by allowance. | M46 | ELECTRO-FES; ELECTRO-DESNZ support flexibility, not quantitative defaults | electrolysis/config.json; demand_plans/*.plan.json
Historical gas sizing | Station size | 0.92 | GW | Historical CCGT-only stage | Superseded for current supply-first schedules by M48. Standard model combined-cycle station, unchanged from the unit reference. | M47 | Existing unit, weather and trade references; model-derived sizing | gas_sizing/METHODS.md; tools/size_gas.py
Historical gas sizing | Order-to-online lead | 4 | years | Historical CCGT-only stage | Superseded for current supply-first schedules by M48. No orders before 2029; first newly commissioned stations in 2033. | M47 | Existing unit, weather and trade references; model-derived sizing | gas_sizing/METHODS.md; tools/size_gas.py
Historical gas sizing | Combined commissioning ceiling | 8 | stations/year | Historical CCGT-only stage | Superseded for current supply-first schedules by M48. Includes baseline replacement stations and additional adequacy stations; explicit delivery assumption. | M47 | Existing unit, weather and trade references; model-derived sizing | gas_sizing/METHODS.md; tools/size_gas.py
Historical gas sizing | New station operating/recovery life | 35 | years | Historical CCGT-only stage | Superseded for current supply-first schedules by M48. No new-station retirements during 2030–2050; existing fleet retirements remain explicit. | M47 | Existing unit, weather and trade references; model-derived sizing | gas_sizing/METHODS.md; tools/size_gas.py
Historical gas sizing | Capacity criterion | 9 | connected replays/year | Historical CCGT-only stage | Superseded for current supply-first schedules by M48. All seven historical weather profiles and both retained synthetic stresses, with existing reserves/inertia screens and bounded imports. | M47 | Existing unit, weather and trade references; model-derived sizing | gas_sizing/METHODS.md; tools/size_gas.py
Historical gas sizing | Clean-target gas replacement plan | Retained | policy assumption | Historical CCGT-only stage | Superseded for current supply-first schedules by M48. The clean-target fleet is not a minimum adequate system; its annual gas output quota and remaining shortages stay explicit. | M47 | Existing unit, weather and trade references; model-derived sizing | gas_sizing/METHODS.md; tools/size_gas.py
Gas peakers | gas_ocgt: unit_gw | 0.3 | GW net | Analyst assumption | 300 MW OCGT reference rounded from 299 MW; engine site groups five 20 MW modules. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_ocgt: equipment_modules | 1 | modules/site | Analyst assumption | Explicit analyst operational/site assumption. Full notes in operations/peaker_assumptions.json. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_ocgt: lead | 3 | years | Analyst assumption | One reformed planning year plus two OCGT construction years or one engine year. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_ocgt: life | 30 | years | Analyst assumption | Selected physical life; refurbishment and normal maintenance in operating allowance. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_ocgt: recovery | 30 | years | Analyst assumption | Selected capital-recovery term, separate from borrowing rate. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_ocgt: capex_bn_per_gw | {"low": 0.45, "central": 0.95, "high": 1.45} | real 2024 £bn/GW | Source-based estimate | Survey range; central is its arithmetic midpoint. Embedded nearby connections retained; borrowing costs separate. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_ocgt: fixed_bn_per_gw_year | 0.01529 | real 2024 £bn/GW/year | Source-based estimate | Source fixed fee plus 0.4% of central capital for insurance. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_ocgt: availability | 0.95 | fraction | Published representative value | DESNZ representative smooth availability, not independent engine-module outages. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_ocgt: efficiency_full_lhv | 0.389 | fraction LHV | Published representative value | DESNZ representative net LHV efficiency; not a manufacturer maximum. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_ocgt: efficiency_at_min_load_lhv | 0.3 | fraction LHV | Analyst assumption | Explicit analyst operational/site assumption. Full notes in operations/peaker_assumptions.json. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_ocgt: min_load_fraction | 0.25 | fraction | Analyst assumption | Explicit analyst operational/site assumption. Full notes in operations/peaker_assumptions.json. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_ocgt: start_lead_hours | 1 | hours | Analyst assumption | Explicit analyst operational/site assumption. Full notes in operations/peaker_assumptions.json. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_ocgt: min_up_hours | 1 | hours | Analyst assumption | Explicit analyst operational/site assumption. Full notes in operations/peaker_assumptions.json. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_ocgt: min_down_hours | 1 | hours | Analyst assumption | Explicit analyst operational/site assumption. Full notes in operations/peaker_assumptions.json. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_ocgt: ramp_fraction_per_hour | 1 | fraction/hour | Analyst assumption | Explicit analyst operational/site assumption. Full notes in operations/peaker_assumptions.json. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_ocgt: inertia_seconds | 5 | seconds | Analyst assumption | Explicit analyst operational/site assumption. Full notes in operations/peaker_assumptions.json. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_ocgt: start_fuel_mwh_per_mw | 0.2 | MWh fuel/MW started | Analyst assumption | Explicit analyst operational/site assumption. Full notes in operations/peaker_assumptions.json. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_ocgt: variable_gbp_mwh | 4.76 | real 2024 £/MWh | Published representative value | Conservative 500-hour operating case; no extra peaker start-wear charge. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_ocgt: annual_limit_gw | 3.6 | GW/year | Analyst assumption | Candidate procurement envelope; no confirmed manufacturer allocation. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_engine: unit_gw | 0.1 | GW net | Analyst assumption | 300 MW OCGT reference rounded from 299 MW; engine site groups five 20 MW modules. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_engine: equipment_modules | 5 | modules/site | Analyst assumption | Explicit analyst operational/site assumption. Full notes in operations/peaker_assumptions.json. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_engine: lead | 2 | years | Analyst assumption | One reformed planning year plus two OCGT construction years or one engine year. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_engine: life | 30 | years | Analyst assumption | Selected physical life; refurbishment and normal maintenance in operating allowance. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_engine: recovery | 30 | years | Analyst assumption | Selected capital-recovery term, separate from borrowing rate. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_engine: capex_bn_per_gw | {"low": 0.55, "central": 0.65, "high": 0.75} | real 2024 £bn/GW | Source-based estimate | Survey range; central is its arithmetic midpoint. Embedded nearby connections retained; borrowing costs separate. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_engine: fixed_bn_per_gw_year | 0.01723 | real 2024 £bn/GW/year | Source-based estimate | Source fixed fee plus 0.4% of central capital for insurance. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_engine: availability | 0.95 | fraction | Published representative value | DESNZ representative smooth availability, not independent engine-module outages. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_engine: efficiency_full_lhv | 0.446 | fraction LHV | Published representative value | DESNZ representative net LHV efficiency; not a manufacturer maximum. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_engine: efficiency_at_min_load_lhv | 0.4 | fraction LHV | Analyst assumption | Explicit analyst operational/site assumption. Full notes in operations/peaker_assumptions.json. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_engine: min_load_fraction | 0.15 | fraction | Analyst assumption | Explicit analyst operational/site assumption. Full notes in operations/peaker_assumptions.json. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_engine: start_lead_hours | 0 | hours | Analyst assumption | Explicit analyst operational/site assumption. Full notes in operations/peaker_assumptions.json. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_engine: min_up_hours | 1 | hours | Analyst assumption | Explicit analyst operational/site assumption. Full notes in operations/peaker_assumptions.json. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_engine: min_down_hours | 1 | hours | Analyst assumption | Explicit analyst operational/site assumption. Full notes in operations/peaker_assumptions.json. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_engine: ramp_fraction_per_hour | 1 | fraction/hour | Analyst assumption | Explicit analyst operational/site assumption. Full notes in operations/peaker_assumptions.json. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_engine: inertia_seconds | 2.5 | seconds | Analyst assumption | Explicit analyst operational/site assumption. Full notes in operations/peaker_assumptions.json. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_engine: start_fuel_mwh_per_mw | 0.03 | MWh fuel/MW started | Analyst assumption | Explicit analyst operational/site assumption. Full notes in operations/peaker_assumptions.json. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_engine: variable_gbp_mwh | 6.73 | real 2024 £/MWh | Published representative value | Conservative 500-hour operating case; no extra peaker start-wear charge. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Gas peakers | gas_engine: annual_limit_gw | 4 | GW/year | Analyst assumption | Candidate procurement envelope; no confirmed manufacturer allocation. | M48 | PEAKER-DESNZ; PEAKER-BRIGG | operations/peaker_assumptions.json
Mixed gas procurement | Balanced CCGT retention | 0.5 | fraction of original adjustable CCGT orders | Analyst candidate | Retain baseline replacement rows, halve adjustable original CCGT orders subject to four total CCGT commissions annually, and independently size engine capacity. Not a globally optimised technology split. | M48 | Explicit study candidate | tools/size_mixed_gas.py; peaker_study/mixed_dispatch_v2/summary.json
Mixed gas procurement | earliest_order | 2029 | See basis | Analyst assumption | Candidate procurement envelope, not confirmed factory allocations. CCGT limited to four 920 MW stations annually; OCGT and engine limits are separate, with a shared 7.36 GW annual commissioning envelope. Compare original schedules separately; no pre-2029 discretionary orders. Equipment lead times and UK allocation require tender evidence. | M48 | No reserved supplier capacity assumed | operations/peaker_assumptions.json; peaker_study/
Mixed gas procurement | ccgt_stations_per_year | 4 | See basis | Analyst assumption | Candidate procurement envelope, not confirmed factory allocations. CCGT limited to four 920 MW stations annually; OCGT and engine limits are separate, with a shared 7.36 GW annual commissioning envelope. Compare original schedules separately; no pre-2029 discretionary orders. Equipment lead times and UK allocation require tender evidence. | M48 | No reserved supplier capacity assumed | operations/peaker_assumptions.json; peaker_study/
Mixed gas procurement | aggregate_gas_gw_per_year | 7.36 | See basis | Analyst assumption | Candidate procurement envelope, not confirmed factory allocations. CCGT limited to four 920 MW stations annually; OCGT and engine limits are separate, with a shared 7.36 GW annual commissioning envelope. Compare original schedules separately; no pre-2029 discretionary orders. Equipment lead times and UK allocation require tender evidence. | M48 | No reserved supplier capacity assumed | operations/peaker_assumptions.json; peaker_study/
Mixed gas procurement | meaning | Candidate procurement envelope, not confirmed factory allocations. CCGT limited to four 920 MW stations annually; OCGT and engine limits are separate, with a shared 7.36 GW annual commissioning envelope. Compare original schedules separately; no pre-2029 discretionary orders. Equipment lead times and UK allocation require tender evidence. | See basis | Analyst assumption | Candidate procurement envelope, not confirmed factory allocations. CCGT limited to four 920 MW stations annually; OCGT and engine limits are separate, with a shared 7.36 GW annual commissioning envelope. Compare original schedules separately; no pre-2029 discretionary orders. Equipment lead times and UK allocation require tender evidence. | M48 | No reserved supplier capacity assumed | operations/peaker_assumptions.json; peaker_study/
Additional coal | Station commissioning years | 2035, 2036, 2037, 2038 | 2 GW net per station | Programme assumption | Retain one station per year delivery envelope and six-year lead. Domestic coal production unchanged; imports supply the balance. | M49 | Existing coal references | demand_plans/ours_*.plan.json
Gas retention | years | 5 | See methodM50 | Analyst conditional estimate | Use identified GAS- cohorts >=350 MW commissioned from1990 with estimated retirement through2050. Exclude unknown forecast residual, small peakers and ambiguous old site dates. Retain75% of eligible capacity as a pooled inspection-success assumption. Refurbish in preceding year, losing25% of retained capacity in that year's annual-average capacity. Charge £150/kW per five-year tranche, borrowing at plan rate and recovering over5years; extra fixed O&M£10/kW/year plus existing fixed O&M; original inherited capital recovery is complete before the40year estimated retirement, so extended capacity incurs refurbishment capital rather than a new replacement-cost annuity. Model extended blocks separately at85% availability and54% full-load efficiency, behind regular CCGT and ahead of engines. 10year sensitivity repeats inspection/overhaul after5years at£250/kW per tranche,80% availability,52% efficiency. All parameters beyond the cited archetype are analyst estimates, not station-level engineering evidence. | M50 | RETENTION-DESNZ; RETENTION-SSE | operations/life_extension_assumptions.json
Gas retention | eligible_fraction | 0.75 | See methodM50 | Analyst conditional estimate | Central five-year retention case; station inspections and supplier offers unconfirmed. | M50 | RETENTION-DESNZ; RETENTION-SSE | operations/life_extension_assumptions.json
Gas retention | availability | 0.85 | See methodM50 | Analyst conditional estimate | Central five-year retention case; station inspections and supplier offers unconfirmed. | M50 | RETENTION-DESNZ; RETENTION-SSE | operations/life_extension_assumptions.json
Gas retention | efficiency_full_lhv | 0.54 | See methodM50 | Analyst conditional estimate | Central five-year retention case; station inspections and supplier offers unconfirmed. | M50 | RETENTION-DESNZ; RETENTION-SSE | operations/life_extension_assumptions.json
Gas retention | efficiency_at_min_load_lhv | 0.42 | See methodM50 | Analyst conditional estimate | Central five-year retention case; station inspections and supplier offers unconfirmed. | M50 | RETENTION-DESNZ; RETENTION-SSE | operations/life_extension_assumptions.json
Gas retention | refurbishment_gbp_kw | 150 | See methodM50 | Analyst conditional estimate | Central five-year retention case; station inspections and supplier offers unconfirmed. | M50 | RETENTION-DESNZ; RETENTION-SSE | operations/life_extension_assumptions.json
Gas retention | additional_fixed_gbp_kw_year | 10 | See methodM50 | Analyst conditional estimate | Central five-year retention case; station inspections and supplier offers unconfirmed. | M50 | RETENTION-DESNZ; RETENTION-SSE | operations/life_extension_assumptions.json
Gas retention | outage_fraction | 0.25 | See methodM50 | Analyst conditional estimate | Central five-year retention case; station inspections and supplier offers unconfirmed. | M50 | RETENTION-DESNZ; RETENTION-SSE | operations/life_extension_assumptions.json
Constrained gas delivery | Annual procurement envelope | 2CCGT;1.5GW engines;0.9GW OCGT;4.24GW combined | Per year | Analyst scenario | Lower-delivery sensitivity, not industry hard limit. | M51 | PROCUREMENT-WARTSILA; PEAKER-GE | tools/study_retention.py
Mixed coal roles | Regular tranche and reserve switch | 4GW through2044; allreserve from2045 | GW/year | Policy sensitivity | Regular/balancing roles may differ by station and year; no extra coal fuel is free. | M52 | Existing coal model; explicit programme choice | retention_study/*/plan.json

## Methods
How the calculations work
M48 records mixed-gas dispatch, gas-engine sizing and the balanced CCGT-retention candidate. M49 records four coal stations and the higher construction-cost sensitivity. M47 is historical CCGT-only sizing. M46 retains the electrolysis constraints and hydrogen-infrastructure cost exclusions. Screens are deterministic, not probability estimates.
ID | Area | Calculation | Implementation | Limits
M01 | Capacity and retirement | Inherited GW = sum(cohort GW × active days / days in target year). New GW = count × unit GW while start + lead ≤ year < retirement. | programme/assets.py; planner/plan.py; planner/costing.py; planner/pipeline.py; planner/engine.js | Most retirement dates are age estimates. No automatic wind repowering or contract-end closure. Nuclear dates reconstructed within each hourly replay.
M02 | Residual vintage allocation | Unlisted existing = June 2026 GB total − selected REPD operational stock. Age weights = positive annual aggregate additions less listed additions; rescale to unlisted total. Future = original 2030 residual − existing; allocate equally 2027–2030. | Historical construction of frozen inputs: separate v1.28 archive / audit/apply.py; audit/sources | Net additions approximate commissioning. Historical corrections/retirements and missing REPD dates make vintages estimates. Total 2030 capacity preserved; future completions uncontracted.
M03 | No duplicate pipeline | New target additions = ceil(max(0, target − surviving opening capacity − earlier project additions)/unit GW). | Historical construction of frozen inputs: separate v1.28 archive / presets/run.py; demand_plans/build.py | Target top-ups avoid adding full targets twice. Repowered turbine exceptions are reconciled separately in audit/physical_corrections.json. Anonymous future tranches are not proven contracted projects.
M04 | Demand pathways | Read annual NESO FES 2025 ED 1 values in GWh; divide by 1000 for TWh. Use three complete pathways, without the old 2035/2040 hybrid join. | planner/build_inputs.py; programme/engine.py | Fiscal annual totals assigned to same-numbered calendar model years. Scenarios have no assigned probabilities.
M05 | Hourly demand | Raise positive historical demand shape to an exponent; normalise non-electrolysis energy and solve to published peak. Add electrolysis once. M46 separately reschedules that component within its capacity and energy limits. | programme/demand_shape.py | Historical timing and future peak are approximations. Seven 8760/8784-hour calendars reused; not sector forecasts. Electrolysis energy is unchanged, with explicit bounded flexibility rather than compulsory flat load.
M06 | Wind and solar profiles | Normalise historical hourly profiles to capacity × reference capacity factor × replay hours; clip nameplate. Use common wind shape for onshore/offshore. | model.py; programme/engine.py | Annual resource totals are normalised: seven weather shapes are not seven independent raw annual-yield observations. Historical generation contains curtailment and fleet changes.
M07 | Solar ageing | New effective GWp = GWp × (1−0.008)^age. New solar profile = old normalised profile ×10.5%/12% × effective GWp, clipped to original GWp/1.25. Inherited output declines from 2030 calibration. | planner/plan.py; planner/costing.py; planner/pipeline.py; planner/security_protocol.py; planner/engine.js | Inherited capacity measurement basis is unresolved. Do not treat combined solar GW as pure AC export. Old panels are not physically rejuvenated; 2030 is the output calibration, not commissioning date.
M08 | Indicative lifetime output | Constant potential TWh = unit GW × 8.76 × utilisation × life. Separate solar ageing sensitivity = first-year TWh × [1−(1−d)^life]/d. Capital-only £/MWh = £million / TWh. | construction/estimates.json; planner/lifecycle.json; audit workbook | Potential, undiscounted output before grid dispatch, curtailment and network losses. Capital-only metric excludes financing, O&M, fuel and system services; not LCOE.
M09 | Nuclear production | Available output = dated nuclear capacity × clip(0.90 +0.04 cos(2πt/N),0,1); synthetic outage deducts 2 GW for 28 days, floored at zero. | programme/engine.py; planner/security_protocol.py | Smooth seasonal availability, not unit outage probabilities. Curtailment allowed. Multiunit outage correlation and delivery probabilities not estimated.
M10 | Gas commitment | Derate fleet 90%; split into 0.5 GW representative blocks and final fraction. Commit with start/ramp lookahead and minimum up/down times; dispatch blocks sequentially. | operations/thermal.py; model.py | Perfect demand/availability foresight within horizon. Constant derating, not explicit forced-outage process. Initial units already committed; no artificial national cold start.
M11 | Gas fuel and starts | Efficiency =47% + (58%−47%) ×clip((load−40%)/(1−40%),0,1). Fuel GWh =Σgeneration/efficiency +started GW ×1.5. Startup wear =actual started GW ×1000 ×£30/MW. | model.py; operations/thermal.py | Fuel and CO 2 use LHV. Zero startup-fuel custom configuration falls back to full-block wear proxy; default positive coefficient gives exact fractional MW.
M12 | Coal and fuel stock | Dispatch 0.5 GW blocks with 85% availability and coal-specific timers. Tonnes =fuel GWh ×1000 /6.667 MWh/t. Opening+domestic+imports−burn=ending stock. | accelerator.py; coal_extension.py; planner/costing.py | Default economic mode compares coal-first and gas-first heuristics, not global optimisation. The proposed programme instead uses the explicit baseload commitment in M37. Fuel availability remains a constraint.
M13 | Storage | ηcharge=ηdischarge=√0.80; SOCnext=SOC+ηcharge×charge−discharge/ηdischarge.48 h forecast need and 20% discretionary reserve; repair infeasible charging monotonically. | operations/storage.py; programme/engine.py | Batteries and pumped hydro pooled; empty at start of each replay year; no carryover or degradation trajectory. Maintenance/replacement assumptions replace detailed cell ageing.
M14 | Hourly balance | Accepted nuclear+renewables+other+coal+gas+imports+battery discharge+unserved = demand+charging+exports. Track curtailed generation separately. | model.py; programme/engine.py; trade/dispatch.py | Copperplate GB. Curtail VRE then nuclear, other, coal, gas. Thermal fuel remains charged for forced output subsequently dumped.
M15 | Reserve and inertia | Reserve =committed thermal deliverable headroom +battery response; require 2 GW. Inertia =connected nuclear×5 s+gas×5 s+coal×6 s+external; require 120 GW·s. | operations/thermal.py; programme/engine.py | Hourly scalar screens, not frequency simulation, transient stability, regional strength or probabilistic LOLE. No imported reserve or independent stability services credited.
M16 | Security suite | Per model year:7 normal historical shapes 2018–24 plus 28-day cold-calm and 2 GW nuclear outage on 2019,2024. Pass if unserved≤1 MWh and zero reserve/inertia shortfall hours. | planner/security_protocol.py | Zero-import autonomy tests. No probability attached. Gas physical deliverability assessed separately; passing electricity screens does not prove fuel security.
M17 | Gas security requirement | For 14/28-day stress windows and 1/2/3 TWh/day supply: cumulative hourly deficits; minimum working stock =max cumulative deficit above previous minimum. Peak withdrawal=max hourly deficit. | planner/security_protocol.py | Power-sector allocation assumption, not national gas availability or pipeline hydraulics. Endogenous household/industry competition not modelled.
M18 | Trade | Imports≤residual and available capacity×(1−loss); schedule if sending-end price/(1−loss)<gas full-load fuel+variable O&M. Rescue actual shortage from unused capacity. Export otherwise-curtailed VRE then nuclear. | trade/dispatch.py | Exogenous foreign prices and availability. No simultaneous importing/exporting. No induced European prices, cable-specific outages or optimal storage arbitrage.
M19 | Trade settlement | Import £bn =GB received GWh/(1−loss)×sending price/1 e 6. Export revenue =GB sent GWh×(1−loss)×receiving price/1 e 6. Net subtotal =resource subtotal including imports−export revenue. | trade/dispatch.py | Existing interconnector capital/tariffs unpriced. Capacity increases do not automatically price new cables. Export receipts do not reprice legacy CfDs.
M20 | Construction estimates | Foreign amount /foreign units perGBP ×CPI 2024/CPIreference ×target net capacity/reference net capacity; construction-only source category where disclosed. | construction/estimates.json | Linear scale, consumer CPI and FX are proxies. Gas/coal auxiliary loads assumed. Offshore and SMR cost scope not fully separated; not uniform turnkey quotes.
M21 | Construction cash | One planning year; construction cash equal over lead−1 subsequent years; planning allowance in first year, connections in final build year. Sum draws =total commitment. | planner/finance.py; planner/engine.js | Blank allowances mean uncosted, not verified zero. Past and post 2050 draws retained. No construction cost added again to annual capital recovery.
M22 | Financing and recovery | Capital at commissioning =Σmid-year draw×(1+r)^(online−drawyear−0.5). Annual charge =capital×r/[1−(1+r)^−n], or capital/n at r=0. | planner/finance.py | Common 4.5% real for new projects. Includes repayment/return, not actual debt contract. Explicit early retirement reports remaining balance; salvage not assumed.
M23 | Inherited capital | Inherited capacity × inherited replacement-cost annuity. Add actual dated new-project annual capital charges while within their recovery term. Calculate these directly; do not reverse a provisional new-build charge. | planner/costing.py; planner/finance.py; operating/estimates.json | Inherited cost proxy persists while operating and is not actual remaining debt, sunk spending or Treasury outlay. Source financing/lives differ from new policy terms.
M24 | Operations and maintenance | Inherited fixed allowances plus direct new-project O&M. Apply actual gas/coal fuel, starts, part-load losses, coal stock finance and proportional new-nuclear fuel/variable O&M. Preserve the documented decommission-timing provision. | planner/costing.py; planner/finance.py; operating/estimates.json | New nuclear output allocated pro rata across nuclear capacity; existing fuel bundled. Maintenance in allowances, not individual overhaul programme. No automatic performance decay for wind/thermal beyond availability.
M25 | Solar inverter provision | At age 15 (and later multiples before retirement), replacement cash =10% original construction capital. Provision funded within fixed O&M; not added again to resource cost. | planner/plan.py; planner/costing.py; planner/pipeline.py; planner/lifecycle.json | Cost fraction is an estimate. No double provision at retirement. Inherited inverter replacement not separately itemised.
M26 | Resource-cost boundary | Annual resource subtotal =capital recovery+nonfuel operations+gas/coal/new-SMR fuel; trade imports included where enabled. Carbon/support transfers excluded. | planner/costing.py; planner/finance.py; operating/estimates.json | Partial generation/storage service cost. Cost per MWh divides byserved demand, not requested demand; unmet energy must be shown alongside costs.
M27 | Carbon account | From 2031, real tax =£10/(1.02)^(year−2024); transfer £bn =fossil Mt×real tax/1000. | programme/engine.py | Nominal fixed £10 policy converted to 2024 pounds; not an assurance of treaty compliance. No upstream/import emissions footprint. Carbon affects dispatch comparison, not physical resource subtotal.
M28 | Networks and ancillary infrastructure | Offshore/solar transmission =new GW×transfer share×EGL 2£/GW×cost fraction; separate 45-yearassets. Other connections and fuel infrastructure use low/central/high allowances. | planner/accounts.py; policy_update/accounting.py | These are separate partial overlays, not complete marginal system costs. Connection overlap, OFTO assets, distribution base, losses and location remain unresolved. Service-price stability overlay gets no physical reliability credit.
M29 | Inherited support settlement | CfD net £bn =eligible TWh×(real strike−reference price)/1000; add GBproxyRO and grossFIT for funding ledger. Negative CfD settlements retained. | Historical construction of frozen inputs: separate v1.28 archive / legacy/run.py; planner/accounts.py | Separate April financial years, ends 2049/50. Excludes nuclear CfDs, post-CfD output and unawarded AR 8+. No automatic repricing for physical retirement or national spill.
M30 | Presets and demand matching | Our low/high nuclear target scales central nuclear by demand ratio, constrained 2/4/6/8 SMRs/year; gas sized by discrete adequacy search and delivery ceilings. Government low/high scales central capacity targets, retaining inherited orders. | Historical construction of frozen inputs: separate v1.28 archive / demand_plans/build.py; demand_plans/METHODS.md | Saved orders frozen for this audit; no reoptimisation. Government continuation beyond 2030 is analyst-defined and omits proposed hydrogen, CCS, LDES/flexibility. Costs do not compare equal reliability.
M33 | Additional gas for matched supply | For each year and family, search integer 0.92 GW top-ups against nine no-import screens; confirm selected candidate passes and its immediate lower neighbour fails. Schedule actual additions with four-year lead, earliest 2029 order, eight total gas stations/year after original orders. | Historical construction of frozen inputs: separate v1.28 archive / release_1_26/firm_gas.py | Original orders preserved. Early constrained gaps remain explicit. Bisection is not a global portfolio minimum; matching these screens does not establish fuel deliverability or the 5% gas target.
M34 | Import-inclusive security | Apply the common seven normal and two cold-calm/nuclear-outage cases. During the full 28-day stress, sending capacity <=cable GW×scarcity fraction; delivered imports multiply by 1−loss. Nominate scarcity imports where residual demand would exhaust domestic thermal capacity minus 2 GW reserve. | security_imports/dispatch.py; planner/pipeline.py | No foreign inertia or reserve credit. Foreign availability and prices are scenario assumptions, not secured contracts. Costs average the seven normal replays; stress costs are not assigned probabilities.
M35 | 2029 start constraint | Restore v 1.26 post-2029 gas orders. Defer its three unverified earlier gas orders to the earliest spare slots from 2029, preserving total gas counts, four-year lead and eight stations/year. Re-evaluate all annual cases with bounded imports. | demand_plans/*.plan.json; planner/plan.py; planner/pipeline.py | First new gas commissions in 2033. Transition shortfalls remain explicitly unresolved; no assumed pre-2029 orders are used to manufacture closure.
M31 | Annual summaries | Annual costs =arithmetic mean of 7 normalshape replays; synthetic stresses separate. Construction cash and capital recovery shown separately. | planner/summaries.py; planner/pipeline.py | Not expected value under known probabilities. No percentile/confidence claims. UI edits invalidate saved hourly results and require reevaluation.
M32 | Input hierarchy | Opening cohorts +current plan override old scenario totals; planner lifecycle/construction/operating estimates override generic new-project costs; pooled storage 80% overrides 85%; programme tax deflation overrides old fiscal illustration. | planner/build_inputs.py; planner/plan.py; planner/costing.py; planner/pipeline.py | Archived explorers and old fixtures retain original vintage. All Inputs flags overridden/historical values so they are not mistaken for current defaults.
M36 | Refactor verification | Freeze v1.28 plan/evaluation and input hashes; recompute all 126 annual cases and 3,150 published replays; compare every existing numeric field with absolute 1e−8 / relative 1e−10 tolerance and all verdicts exactly. | tools/validate.py; validation/reference_v1_28/; tests/ | Preserves existing assumptions and remaining shortfalls. Arithmetic consistency does not establish future delivery or engineering reliability.
M37 | Coal baseload commitment | Proposed programme: one 2 GW station online 2035; target 2 × 85% = 1.7 GW continuously while fuel is available. This smooth availability allowance represents maintenance/outages rather than dated outages. Gross output = available GW × replay hours / 1000, about 14.9 TWh/year. Dispatch records delivered output and any coal spill separately. Fuel, stocks, starts, emissions, operations, gas dispatch and trade are recalculated. | demand_plans/ours_*.plan.json:coal_dispatch; programme/engine.py; planner/pipeline.py; trade/dispatch.py; security_imports/dispatch.py | Policy operating choice, not least-cost optimisation. Fuel interruption can force shutdown. Keeping coal running can displace gas, nuclear or renewables; any unused coal output still incurs fuel cost. Economic mode remains available for custom plans.
M38 | Standalone operating-cost comparison at design efficiency | Annual output retains the capital table's potential utilisation and maintenance allowances. Fuel cost per MWh of electricity equals input fuel price divided by design efficiency (and coal heat content). Fixed, variable and lifecycle O&M retain their existing source estimates. Borrowing costs, including coal inventory carrying interest, are excluded from the reference comparison and remain in the hourly model accounts. Actual operations, site conditions and grid decisions may prevent these design conditions being achieved. Wind/solar retain weather-based potential yields, not constant nameplate output. | planner/reference_units.json; planner/build.py; planner/app.js:renderOperatingUnits; tests/test_operating_units.py | Gas 63% and coal 45.6% are published design benchmarks for this table. Hourly fleet dispatch retains its separate 58% and 40% full-load assumptions, with part-load and start penalties. Construction and O&M use their separately identified proxies. Site conditions and grid use can prevent design-table performance being achieved.
M39 | Programme cost total, 2030–2050 | Sum connected.summary.net_cost_after_exports_bn for each year from 2030 to 2050 inclusive. Each annual figure is the normal-weather mean of capital recovery plus operating costs (including fuel and import purchases), less export receipts. Construction cash is not added again. Sum uses unrounded values in real 2024 GBP, without discounting. | planner/app.js:periodCost; renderDashboard; renderComparison | Shown only for a matching evaluation marked complete with exactly one finite-cost result for each of the 21 years. Missing, duplicate or non-finite years are never treated as zero. Coverage remains partial; separate connections/planning are excluded unless entered, and later repayments after 2050 fall outside the period. Supply adequacy remains a separate screen.
M40 | 95% clean constraint and gas-firmed comparison | Remove the additional adequacy-gas-* orders and enforce a five-percent annual gas-output ceiling. Baseline gas capacity, all non-gas projects, finance and trade are preserved. Record unserved demand rather than exceeding the quota. | tools/make_target_presets.py; demand_plans/target_*.plan.json; validation/target_preset_changes.json | Clean generation includes nuclear. The approximate eligible-generation scope excludes proportionate waste/gas CHP; imports and battery discharge do not dilute the denominator. Continuation after 2030 is an analyst sensitivity. Allocation is not optimised; official flexibility resources remain incomplete.
M41 | Pilot-gated SMR orders and transition bridge | Wylfa pilot: three 470 MW units in 2035. Conditional repeat orders start with 2 in 2034, then 4, 6 and at most 8 per year; five-year lead makes first repeat output 2039. Later orders are limited to the units needed for the 60% nuclear-output aspiration in the selected demand pathway. One additional 1.7 GW large reactor opens 2037; four 2 GW coal stations open in 2035–38 (M49). Gas orders are separately revised under M48, with no backdating or automatic gap filling. | tools/revise_nuclear_rollout.py; demand_plans/ours_*.plan.json; tests/test_nuclear_rollout.py | 2034 is conditional on satisfactory pilot design/construction and factory-readiness evidence; first pilot operation is assumed in 2035. It is not an operating-proof gate. If evidence is late, orders move later. Eight repeat units per year can leave the 60% aspiration unmet by 2050. Four coal stations retain the existing 3 Mt/year domestic-supply assumption; additional imported fuel remains explicitly costed.
M42 | Large-reactor capital and operating proxy | 72.8 / 6 × 0.85 × 133.9 / 108.7, in £bn per reactor at a provisional 2024 price base. Low is 80% of central (analyst sensitivity); high is £19bn, half of the £38bn 2024 Sizewell C construction comparator. Project capex_bn_per_unit overrides the repeat-SMR rate; count × selected unit cost flows through annual draws, construction interest and 60-year recovery. Seven construction years plus one planning year = eight-year lead. | planner/large_nuclear.json; planner/plan.py; planner/engine.js; planner/finance.py | French programme-budget proxy, not a UK single-reactor tender or a clean EPC quote. General UK CPI and a provisional currency conversion are estimation conventions. Programme engineering and shared-site scope cannot be cleanly stripped out; no separate development deduction has been invented. Borrowing costs are calculated separately. User-selected seven-year construction case plus one-year reformed planning. EDF's 70-month ambition is a repeat-build improvement target, not demonstrated first UK EPR2 delivery. Assumes design acceptance, site and supply-chain readiness; no UK EPR2 consent asserted. Uses the existing new-nuclear INL moderate SMR fixed, variable and fuel allowances as an explicit temporary proxy. This is not an EPR2 operating-cost quote. Availability and the two-GW synthetic outage screen retain the existing model conventions. Legacy new_smr_* ledger fields include this new-nuclear proxy; no separate unit-level nuclear dispatch is claimed.
M43 | Build years in the capital reference | Build years = technology order-to-online lead minus the common one-year reformed planning assumption. Both build years and total order-to-online years are shown, including 4+1 for repeat SMRs and 7+1 for the large-reactor sensitivity. | planner/app.js:renderUnits; planner/template.html; tests/test_ui.cjs | Timing assumptions under the proposed reforms, not supplier-guaranteed UK delivery. Repeat-unit leads do not override pilot, design acceptance, site or factory-readiness gates.
M44 | Binding annual gas-output budget controller | For each weather year and trade mode, calculate the unconstrained hourly committed-gas profile. Scale permitted gas operation along that profile and rerun thermal starts, ramping, storage, reserves, trade and fuel. Safeguarded interpolation retains a solution with G/(eligible domestic generation) <= 5%. For a coal-free case, this is G <= clean generation/19. Recheck actual dispatched/curtailed generation after trade. Nameplate gas capacity, construction, capital recovery and fixed costs remain unchanged. | operations/gas_budget.py; planner/pipeline.py; tests/test_gas_budget.py; tests/test_target_presets.py | This is a declared profile-based quota controller, not a global minimum-shortage or optimal unit-commitment solution. The reference profile and annual calibration use full weather-year information. Gas can run at selected outputs within its permitted operating profile; this does not reduce installed gas capacity to 5%. Shortage distribution depends on the controller. Imports stay bounded; their foreign carbon content is not certified. Synthetic stress replays use the same annual constraint as a separate sensitivity.
M45 | Inherited Wylfa commissioning dates | Three inherited 470 MW pilots are assumed online together in 2035, giving 1.41 GW from that year. These dated delivery assumptions are common to all programmes and are excluded from the new-order editor. | demand_plans/*.plan.json; planner/app.js:isPilot; programme explanations | Government targets the first operational SMRs from the mid-2030s. The source does not establish all three operational in 2035 or publish the model's annual unit sequence. All-three commissioning in 2035 is a user-selected assumption, not a published commitment. As elsewhere in this annual fleet model, online-year capacity is available for the full year before availability/outage adjustments; within-year commissioning is not resolved.
M46 | Bounded electrolysis and finite hydrogen buffer | Take networked electrolysis annual GWh from FES 2025 ED1. Default: preserve its energy in each 24-hour block; trough-fill residual load with 0 <= input <= 2 times annual average. Hydrogen buffer = 2 x window x average, tracked in electricity-equivalent GWh; starts half full and every block ends unchanged. Schedule before imports, storage and gas; retain total demand and all build orders. Apply the same settings to all nine presets. Fixed mode restores constant operation. Optional GBP/MWh allowance enters OPEX once. | electrolysis/config.json; dispatch.py; METHODS.md; planner/pipeline.py; tests/test_electrolysis.py | Capacity multiple and 48-hour default buffer are analyst infrastructure assumptions, not existing or committed assets. Known within-window weather is a forecast proxy. Constant conversion efficiency and aggregate hourly controllability; no explicit degradation, minimum load, compressor limits or seasonal shifting. No hydrogen-to-power. Buffer feasibility is conditional on power served: shortages stay unserved and are not reported as produced hydrogen. Electrolyser/storage/compression/distribution costs are excluded unless an allowance is supplied. Default allowance zero means excluded, not free. Isolated trough filling is not a joint dispatch optimum and does not guarantee gas savings.
M47 | Historical CCGT-only sizing after electrolysis flexibility | For each of six programme/demand pairs, find an integer gas capacity threshold in every year 2033–2050 under seven historical weather years and two synthetic stresses, bounded imports and the existing energy/reserve/inertia screens. Independently size fixed and flexible electrolysis. Propagate cumulative requirements forward and commissioning constraints backwards; retain whole 920 MW stations, four-year lead, 35-year life and at most eight combined stations commissioned annually. Keep non-gas orders and government baseline replacements. Re-evaluate complete flexible schedules in all modes; verify complete fixed schedules. Preserve unresolved pre-delivery gaps. | tools/size_gas.py; verify_fixed_gas_sizing.py; gas_sizing/METHODS.md; results.json; annual_v3; tests/test_gas_sizing.py | Integer search under the existing dispatch controller, not a global system-cost or probabilistic reliability optimum. Adjacent lower-count failures and complete schedules are checked. Fixed-load comparator can exceed the old schedule where that schedule failed stresses. The capped clean-target case retains baseline replacements and its output quota; it is not claimed adequate. Earlier maximum-delivery failures remain visible. Hydrogen infrastructure cost exclusions from M46 remain.
M48 | Mixed gas dispatch and bounded procurement study | Keep the opening gas fleet and baseline replacement orders. Explicit candidates retain specified shares of original adjustable CCGT orders, with at most four 920 MW commissions annually. Size 100 MW engine sites against seven historical-weather and two synthetic connected-security replays in every year. Preserve two-year engine leads, no orders before 2029, at most 4 GW engines/year and a shared 7.36 GW/year gas commissioning envelope. Forward cumulative requirements and backward delivery constraints give latest feasible engine commissioning. Replay complete schedules. CCGT, engines and OCGT dispatch in fuel/variable-cost merit order with separate availability, part load, start fuel, min-load/up/down/ramp and synchronous inertia. All gas technologies share the same hourly balance, fuel price and fuel-interruption multiplier. Capital and fixed costs use each dated technology once. | operations/mixed_gas.py; peaker_assumptions.json; tools/size_mixed_gas.py; peaker_study/; tests/test_mixed_gas.py | Procurement envelopes, CCGT retention shares and several technical parameters are analyst scenarios, not reserved manufacturing slots or a global system-cost optimum. The balanced 50% retention candidate is tested across all three demand pathways. OCGT is selectable but the chosen central engine cost/efficiency favours engines for backup. Source cost scopes retain unquantified embedded nearby connections; separately entered planning/grid allowances remain additional. Engine sites group five 20 MW modules; sub-hour starts, individual module outages, locational deliverability and forecast errors are not certified. Earlier gaps remain. All previously passing connected replays must remain passing.
M49 | Four coal stations and coal-price sensitivity | Retain 2 GW stations online in 2035/36; add one in 2037 and one in 2038, with six-year leads and 50-year operating/recovery life. Retain 85% availability, baseload dispatch, part-load/start/fuel inventory, 30-day stocks and existing 3 Mt/year domestic supply ramp. Imports supply and cost the balance. Compare a separately resized two-station mixed-gas candidate to isolate extra coal. Reprice coal construction using the existing higher US EPC comparator as a cost-only sensitivity; dispatch and fuel remain unchanged. Indicative constant gas-price break-even equals £30/MWh fuel plus the cost difference divided by gas-fuel saving, holding dispatch, trade and coal prices unchanged. | tools/size_mixed_gas.py; peaker_study/; tools/compare_peakers.py; construction/estimates.json; policy_update/accounting.py | Additional coal is an explicit candidate, not a secured construction programme. The older overseas central capital proxy has high UK transfer uncertainty. Domestic mining, ports, rail, storage, emissions permits and legal enabling changes are not inferred from power-station capacity. Annual resource subtotal excludes carbon/support transfers and unpriced wider infrastructure. Early differing service levels are disclosed; cumulative costs are not equal-service comparisons where shortages differ.
M50 | Conditional inherited-gas life extension | Use identified GAS- cohorts >=350 MW commissioned from1990 with estimated retirement through2050. Exclude unknown forecast residual, small peakers and ambiguous old site dates. Retain75% of eligible capacity as a pooled inspection-success assumption. Refurbish in preceding year, losing25% of retained capacity in that year's annual-average capacity. Charge £150/kW per five-year tranche, borrowing at plan rate and recovering over5years; extra fixed O&M£10/kW/year plus existing fixed O&M; original inherited capital recovery is complete before the40year estimated retirement, so extended capacity incurs refurbishment capital rather than a new replacement-cost annuity. Model extended blocks separately at85% availability and54% full-load efficiency, behind regular CCGT and ahead of engines. 10year sensitivity repeats inspection/overhaul after5years at£250/kW per tranche,80% availability,52% efficiency. All parameters beyond the cited archetype are analyst estimates, not station-level engineering evidence. | operations/life_extension.py; operations/life_extension_assumptions.json; planner/plan.py; operations/mixed_gas.py; planner/costing.py | Calendar age alone cannot establish remnant life. Success fraction is pooled, not a list of operator-agreed stations. Refurbishment throughput, parts, staff, permits, gas availability and seasonal outage timing are not contracted. No life credit is assigned before2029 or to closed/dismantled units. Five-year costs are conservatively above the modern-archetype reference; ten-year scenario is an upside engineering sensitivity, not cheap repowering proof. Inherited gas capital recovery ends at the original estimated retirement; continued assets incur paid refurbishment, fixed O&M and fuel. This treats already-recovered construction capital as sunk, rather than charging a hypothetical new plant.
M51 | Constrained gas procurement candidates | Hold all nuclear, renewables, demand, storage, trade and electrolysis inputs fixed. Slow candidates commission at most2CCGT stations/year with5year lead,1.5GW engines/year with2year lead and0.9GW OCGT/year with3year lead;4.24GW combined. CCGT order totals are retained/deferred, or reduced to75%/50% in separately labelled central sensitivities. Size a monotone virtual5engine/1OCGT ladder against two synthetic stresses, then schedule componentwise cumulative requirements backwards subject to dated limits and verify all7normal+2stress profiles every year. Fast controls retain earlier procurement throughput. Unmet screens remain failures. | tools/study_retention.py; retention_study/*/search_*.json; result.json | Analyst delivery scenarios, not global production ceilings or secured UK allocations. Bounded heuristic, not global investment optimisation. Gas orders after2050 are unplaced; commissions after2050 are deferred. No pre2029 discretionary orders. Only connected mode is recomputed for alternatives. Costs differ in service when shortages differ.
M52 | Coal with changing transition roles | Up to4GW nameplate is regularly committed through2044 (two2GWstation equivalents); residual coal is scheduled economically. From2045 allcoal is held for reserve: commitment anticipates demand beyond available gas capacity after scheduled imports/storage, subject to existing starts, ramps, fuel and85% availability. Stocks, starts, fuel use and OPEX are charged in every case. Six-station cases add2GW in2039/2040 at one station/year, or2035/2036 in a separately labelled early-coal sensitivity that raises the coal envelope to two stations/year. | operations/life_extension.py:coal_role; planner/pipeline.py; programme/engine.py:thermal_coal | 2045 switch and4GW regular tranche are policy sensitivities, not a forecast optimal dispatch. Reserve plants cannot start instantaneously; existing forecast-informed start/ramp heuristic retained. Coal availability does not secure mining, logistics, finance or fuel stocks. Compare failed and passing years separately.
M53 | Main delivery presets and frozen controls | Planning selects five-year retention with constrained delivery; stronger retention selects ten-year retention with a second paid inspection/overhaul; faster delivery selects five-year retention with higher throughput. Each setting has separate low, central and high demand plans for both supply-first families. Central proposed planning/retention use the lower30CCGT candidate; other counts follow their dated candidate schedules. The95percent clean output-ceiling experiment remains frozen with its original retirement schedule. | planner/delivery_settings.json; planner/build.py; planning_presets/; planner/app.js:scenario; tests/test_delivery_settings.cjs | No automatic gap filling. Selection preserves saved physical results. Full26case evidence remains; original nine controls remain in demand_plans. Connected-mode outputs only for delivery alternatives.

## Unit economics
Reference-unit capital and potential output
Construction-only lifetime metrics for existing reference units plus OCGT and gas-engine sites. New engine sites group five 20 MW modules. Representative efficiency and potential output are distinct from actual dispatch; borrowing, fuel, OPEX and system costs remain separate. New peaker survey scopes retain unquantified nearby connections; no speculative deduction is applied.
Technology | Unit GW | Utilisation | Life years | Capital £m | Annual potential TWh | Lifetime potential TWh | Capital only £/MWh | Degradation | Age adjusted TWh | Age adjusted £/MWh | Source | Build years | Order to online years
nuclear | 0.47 | 90% | 60 | 1800 |  |  |  | 0% |  |  | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections. | 4 | 5
gas | 0.92 | 90% | 35 | 877.1633 |  |  |  | 0% |  |  | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption. | 3 | 4
coal | 2 | 85% | 50 | 2750.8078 |  |  |  | 0% |  |  | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine. | 5 | 6
onshore | 0.1 | 36% | 25 | 123.5369 |  |  |  | 0% |  |  | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate. | 1 | 2
offshore | 1 | 48% | 30 | 2500 |  |  |  | 0% |  |  | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total. | 3 | 4
solar | 0.1 | 10.5% | 30 | 53.56 |  |  |  | 0.8% |  |  | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed. | 1 | 2
large_nuclear | 1.7 | 90% | 60 | 12704.2809 |  |  |  | 0% |  |  | French programme-budget proxy, not a UK single-reactor tender or a clean EPC quote. General UK CPI and a provisional currency conversion are estimation conventions. Programme engineering and shared-site scope cannot be cleanly stripped out; no separate development deduction has been invented. Borrowing costs are calculated separately. https://www.edf.fr/en/the-edf-group/dedicated-sections/journalists/all-press-releases/edf-shares-its-forecasted-cost-estimate-of-the-epr2-programme-for-eu728bn | 7 | 8
gas_ocgt | 0.3 | 95% | 30 | 285 |  |  |  | 0% |  |  | Sections 3.3 and 5.1.3. Survey construction range £450–1,450/kW; central is midpoint. Embedded gas/electric connection content cannot be separated and is retained, not deducted speculatively. Separate new planning and wider-grid allowances remain excluded unless entered. Fixed £11.49/kW/year plus 0.4% of central construction cost for insurance; variable £4.76/MWh includes an assumed cycling regime, so no additional start-wear charge is added. Efficiency/availability are report references. One-year planning plus two-year construction is the reformed lead. Part-load efficiency, hourly start/ramp/minimum-load/inertia/start-fuel parameters and delivery cap are explicit analyst assumptions, not supplier warranties. | 2 | 3
gas_engine | 0.1 | 95% | 30 | 65 |  |  |  | 0% |  |  | Sections 3.5 and 5.1.4. Construction survey £550–750/kW, midpoint £650/kW, excluding contingency; nearby/existing connection scope remains embedded and unquantified. Fixed £14.63/kW/year plus 0.4% of central construction cost insurance; £6.73/MWh variable from the conservative 500-hour case, no extra start-wear charge. 44.6% efficiency and 95% availability are source references, not the best achievable manufacturer design. One-year construction plus one-year reformed planning is an analyst delivery case. Zero whole-hour start delay approximates a few-minute engine start; sub-hour security is not certified. Other operational parameters, 30-year life/recovery, site grouping and annual delivery cap are analyst assumptions. | 1 | 2

## Annual results
Nine programme/demand presets
Real 2024 £billion. Target cases enforce a 5% annual gas share and retain resulting shortages; gas fleet capital and fixed costs remain. Unserved electricity is unpriced. Historical Old columns remain for the original six plans and are blank for target cases. Net_trade_cost_bn is the bounded-import connected result. The added columns show required/shifted electrolysis, current gas generation, the original fixed-load gas reference, and current/fixed-load-sized new stations online. The original fixed-load column is historical and uses the earlier gas build. Fixed-load station counts are blank in this release: earlier paired CCGT-only sizing is retained as historical evidence. New columns split CCGT/engine/OCGT capacity, engine sites, coal generation and gas fuel. Hydrogen infrastructure costs are excluded unless an allowance is entered.
Programme | Demand_case | Year | Demand_TWh | Nuclear_GW | Gas_GW | Coal_GW | Wind_GW | Solar_GW | Old_partial_cost_bn | Partial_cost_bn | Capital_recovery_bn | Operating_cost_bn | Old_net_trade_cost_bn | Net_trade_cost_bn | Imports_TWh | Exports_TWh | No_import_normal_pass | No_import_stress_pass | Connected_normal_pass | Connected_stress_pass | Worst_stress_unserved_TWh | Normal unserved TWh | Gas share (%) | Electrolysis required TWh | Electrolysis shifted TWh | Gas generation TWh | Original fixed-load gas TWh | New CCGT stations online | Fixed-load sized stations online | CCGT_GW | Gas_engine_GW | OCGT_GW | Engine_sites_online | Coal_generation_TWh | Gas_fuel_TWh
Our programme | low | 2030 | 323.698 | 3.3089 | 34.4879 | 0 | 74.6673 | 55.5029 | 40.426 | 40.4231 | 26.2425 | 14.1806 | 40.1423 | 40.1393 | 13.7793 | 38.5677 | FALSE | FALSE | FALSE | FALSE | 1.8917 | 0.023973 | 25.1898 | 0.53 | 0.26353 | 82.6324 | 82.6702 | 0 |  | 34.4879 | 0 | 0 | 0 | 0 | 171.5271
Our programme | low | 2031 | 332.351 | 3.7837 | 37.3079 | 0 | 80.0161 | 55.5029 | 41.7446 | 41.9934 | 27.3866 | 14.6069 | 41.3501 | 41.5825 | 12.2944 | 40.1513 | FALSE | FALSE | FALSE | FALSE | 4.7863 | 0.014232 | 23.9442 | 0.54 | 0.26841 | 81.4119 | 81.2592 | 0 |  | 33.3079 | 4 | 0 | 40 | 0 | 168.925
Our programme | low | 2032 | 341.738 | 4.458 | 40.6889 | 0 | 86.4936 | 55.5029 | 43.4226 | 43.9136 | 28.8545 | 15.0591 | 42.931 | 43.3972 | 10.9718 | 41.5478 | FALSE | FALSE | FALSE | FALSE | 0.37314 | 0.0046218 | 22.4479 | 0.57 | 0.28344 | 79.0271 | 78.7477 | 0 |  | 32.6889 | 8 | 0 | 80 | 0 | 164.2669
Our programme | low | 2033 | 351.742 | 4.458 | 47.0089 | 0 | 85.8818 | 55.5029 | 43.8253 | 44.2198 | 28.9704 | 15.2494 | 43.3911 | 43.7731 | 12.1191 | 40.1746 | FALSE | FALSE | TRUE | FALSE | 0.036539 | 2.4636e-15 | 22.3678 | 0.89 | 0.44124 | 80.4863 | 80.3784 | 4 |  | 35.4089 | 11.6 | 0 | 116 | 0 | 166.7935
Our programme | low | 2034 | 362.296 | 4.458 | 54.2889 | 0 | 85.5065 | 55.5029 | 44.4507 | 44.7596 | 29.2588 | 15.5008 | 44.0738 | 44.3782 | 13.3198 | 38.8502 | TRUE | FALSE | TRUE | FALSE | 0.573 | 3.0371e-15 | 22.2953 | 1.52 | 0.75017 | 82.02 | 82.0568 | 8 |  | 39.0889 | 15.2 | 0 | 152 | 0 | 169.406
Our programme | low | 2035 | 372.906 | 5.868 | 60.0789 | 2 | 84.7651 | 55.5029 | 45.1365 | 45.6236 | 29.7463 | 15.8773 | 44.7989 | 45.1073 | 11.6187 | 40.4225 | TRUE | FALSE | TRUE | FALSE | 0.015601 | 2.058e-15 | 18.6095 | 2.34 | 1.1464 | 71.0352 | 71.2049 | 12 |  | 41.2789 | 18.8 | 0 | 188 | 14.9037 | 146.7541
Our programme | low | 2036 | 384.269 | 5.868 | 62.5469 | 4 | 84.1397 | 55.5029 | 45.6559 | 46.0686 | 29.7768 | 16.2918 | 45.3041 | 45.517 | 11.2858 | 40.3836 | TRUE | FALSE | TRUE | TRUE | 3.0589e-15 | 2.1052e-15 | 16.6893 | 3.1 | 1.5085 | 65.6484 | 65.8952 | 16 |  | 42.8469 | 19.7 | 0 | 197 | 29.8073 | 135.4144
Our programme | low | 2037 | 396.144 | 7.568 | 64.3419 | 6 | 82.7718 | 55.5029 | 46.1954 | 46.9669 | 30.3941 | 16.5728 | 45.7826 | 46.3164 | 9.6937 | 40.8696 | TRUE | FALSE | TRUE | TRUE | 1.8332e-15 | 1.1785e-15 | 13.141 | 4.55 | 2.1919 | 53.5166 | 61.3838 | 20 |  | 44.6419 | 19.7 | 0 | 197 | 44.711 | 110.403
Our programme | low | 2038 | 407.229 | 9.168 | 63.7319 | 8 | 81.1551 | 55.5029 | 47.1501 | 47.6015 | 30.7955 | 16.806 | 46.6124 | 46.8674 | 8.296 | 41.3133 | TRUE | TRUE | TRUE | TRUE | 1.8368e-15 | 1.1206e-15 | 10.0647 | 5.01 | 2.4066 | 42.2829 | 57.2645 | 22 |  | 44.0319 | 19.7 | 0 | 197 | 59.6146 | 87.2208
Our programme | low | 2039 | 419.392 | 11.708 | 62.9299 | 8 | 79.9688 | 55.5029 | 47.821 | 48.0747 | 31.3196 | 16.7551 | 47.186 | 47.3085 | 7.7318 | 40.976 | TRUE | FALSE | TRUE | TRUE | 1.7124e-15 | 1.1622e-15 | 7.974 | 6.03 | 2.8794 | 34.485 | 49.5888 | 23 |  | 43.2299 | 19.7 | 0 | 197 | 59.6146 | 70.9949
Our programme | low | 2040 | 433.613 | 13.588 | 62.1799 | 8 | 78.992 | 55.4256 | 47.866 | 47.8393 | 31.257 | 16.5823 | 47.2066 | 47.0902 | 8.1178 | 39.5157 | TRUE | FALSE | TRUE | TRUE | 1.8758e-15 | 1.3064e-15 | 6.6821 | 6.94 | 3.2956 | 29.9463 | 45.4011 | 25 |  | 42.4799 | 19.7 | 0 | 197 | 59.6146 | 61.3034
Our programme | low | 2041 | 450.011 | 16.408 | 62.6799 | 8 | 77.3384 | 54.5142 | 48.1551 | 48.1229 | 31.4667 | 16.6562 | 47.4733 | 47.3609 | 7.8685 | 38.4818 | TRUE | FALSE | TRUE | TRUE | 2.0108e-15 | 1.4627e-15 | 4.802 | 8.15 | 3.8383 | 22.27 | 37.9815 | 26 |  | 42.9799 | 19.7 | 0 | 197 | 59.6146 | 45.2541
Our programme | low | 2042 | 464.557 | 20.168 | 62.6199 | 8 | 74.3569 | 53.7572 | 48.1225 | 48.2235 | 31.504 | 16.7195 | 47.4355 | 47.4365 | 7.1104 | 37.9304 | TRUE | FALSE | TRUE | TRUE | 2.5153e-15 | 1.7713e-15 | 2.7108 | 8.63 | 4.0557 | 12.9717 | 26.9915 | 26 |  | 42.1199 | 20.5 | 0 | 205 | 59.6146 | 25.9543
Our programme | low | 2043 | 477.519 | 23.928 | 63.5399 | 8 | 72.6581 | 52.6376 | 48.0666 | 48.6344 | 31.3515 | 17.2829 | 47.3135 | 47.7719 | 6.172 | 39.8754 | TRUE | FALSE | TRUE | TRUE | 2.1743e-15 | 1.4779e-15 | 2.4886 | 8.76 | 4.1189 | 12.298 | 17.9561 | 27 |  | 43.0399 | 20.5 | 0 | 205 | 59.6146 | 24.7685
Our programme | low | 2044 | 490.691 | 27.688 | 63.5099 | 8 | 71.6496 | 50.0004 | 48.6795 | 49.3424 | 31.6803 | 17.6621 | 47.9143 | 48.4456 | 5.5588 | 40.9047 | TRUE | FALSE | TRUE | TRUE | 2.6645e-15 | 1.3896e-15 | 2.2474 | 9.59 | 4.4873 | 11.5165 | 16.7849 | 28 |  | 43.0099 | 20.5 | 0 | 205 | 59.6146 | 23.2158
Our programme | low | 2045 | 504.316 | 31.448 | 68.4669 | 8 | 70.4921 | 45.7444 | 49.2805 | 49.9663 | 31.5155 | 18.4509 | 48.3907 | 48.9337 | 4.9407 | 43.3657 | TRUE | FALSE | TRUE | TRUE | 2.2737e-15 | 1.146e-15 | 2.3494 | 10.36 | 4.8198 | 12.4224 | 17.7797 | 31 |  | 45.6669 | 22.8 | 0 | 228 | 59.6146 | 25.7354
Our programme | low | 2046 | 516.137 | 35.208 | 68.4669 | 8 | 70.1154 | 43.6779 | 50.1382 | 51.1411 | 32.0955 | 19.0456 | 49.2231 | 50.0597 | 4.0381 | 45.0482 | TRUE | FALSE | TRUE | TRUE | 1.5561e-15 | 8.1103e-16 | 1.9919 | 11.34 | 5.2464 | 10.8186 | 15.668 | 31 |  | 45.6669 | 22.8 | 0 | 228 | 59.6146 | 22.5059
Our programme | low | 2047 | 526.834 | 38.968 | 68.4669 | 8 | 68.3652 | 42.9291 | 50.7331 | 51.9175 | 32.3395 | 19.5781 | 49.7828 | 50.7945 | 3.2973 | 46.4876 | TRUE | FALSE | TRUE | TRUE | 1.279e-15 | 5.2377e-16 | 1.7067 | 12.32 | 5.6692 | 9.4891 | 13.939 | 31 |  | 45.6669 | 22.8 | 0 | 228 | 59.6146 | 19.8375
Our programme | low | 2048 | 537.853 | 41.318 | 68.4669 | 8 | 66.3206 | 42.6396 | 51.1963 | 52.2359 | 32.2941 | 19.9418 | 50.2257 | 51.1059 | 3.16 | 46.7065 | TRUE | TRUE | TRUE | TRUE | 1.2648e-15 | 4.8418e-16 | 1.6448 | 13.57 | 6.2026 | 9.3319 | 13.8283 | 31 |  | 45.6669 | 22.8 | 0 | 228 | 59.6146 | 19.5123
Our programme | low | 2049 | 548.276 | 41.788 | 67.5689 | 8 | 63.8724 | 42.3292 | 51.5287 | 51.6815 | 31.6398 | 20.0417 | 50.5288 | 50.5919 | 3.801 | 45.2857 | TRUE | FALSE | TRUE | TRUE | 1.5419e-15 | 6.4253e-16 | 1.8657 | 14.55 | 6.6186 | 10.7417 | 15.8334 | 31 |  | 44.7689 | 22.8 | 0 | 228 | 59.6146 | 22.3521
Our programme | low | 2050 | 558.75 | 42.728 | 67.7259 | 8 | 62.9013 | 42.0193 | 52.0505 | 51.5979 | 31.3246 | 20.2733 | 51.0019 | 50.5281 | 4.1586 | 44.5458 | TRUE | FALSE | TRUE | TRUE | 1.9469e-15 | 7.5216e-16 | 1.9785 | 15.21 | 6.8999 | 11.5774 | 17.0323 | 33 |  | 43.0259 | 24.7 | 0 | 247 | 59.6146 | 24.0305
Our programme | central | 2030 | 339.295 | 3.3089 | 34.4879 | 0 | 74.6673 | 55.5029 | 40.5782 | 40.5553 | 26.2425 | 14.3128 | 40.4267 | 40.4038 | 16.1073 | 36.4255 | FALSE | FALSE | FALSE | FALSE | 2.5779 | 0.026022 | 24.7104 | 3.83 | 1.8525 | 83.8047 | 84.1107 | 0 |  | 34.4879 | 0 | 0 | 0 | 0 | 173.3018
Our programme | central | 2031 | 355.884 | 3.7837 | 37.3079 | 0 | 80.0161 | 55.5029 | 41.9722 | 42.1974 | 27.3866 | 14.8108 | 41.7649 | 41.9702 | 15.4569 | 37.0505 | FALSE | FALSE | FALSE | FALSE | 1.5628 | 0.017936 | 23.3334 | 5.46 | 2.6143 | 83.365 | 83.5624 | 0 |  | 33.3079 | 4 | 0 | 40 | 0 | 171.9637
Our programme | central | 2032 | 373.666 | 4.458 | 40.6889 | 0 | 86.4936 | 55.5029 | 43.7302 | 44.2029 | 28.8545 | 15.3485 | 43.4688 | 43.9074 | 14.9012 | 37.6935 | FALSE | FALSE | FALSE | FALSE | 1.1605 | 0.0064282 | 21.769 | 6.29 | 2.9988 | 81.8982 | 81.9505 | 0 |  | 32.6889 | 8 | 0 | 80 | 0 | 168.8409
Our programme | central | 2033 | 392.593 | 4.458 | 47.0089 | 0 | 85.8818 | 55.5029 | 44.31 | 44.6679 | 28.9704 | 15.6975 | 44.1356 | 44.4789 | 17.2111 | 35.2778 | FALSE | FALSE | FALSE | FALSE | 0.36132 | 0.0008005 | 21.7692 | 7.55 | 3.571 | 85.0579 | 85.5138 | 4 |  | 35.4089 | 11.6 | 0 | 116 | 0 | 174.1966
Our programme | central | 2034 | 411.573 | 4.458 | 54.2889 | 0 | 85.5065 | 55.5029 | 45.138 | 45.394 | 29.2588 | 16.1353 | 45.0399 | 45.2975 | 19.517 | 32.9933 | TRUE | FALSE | TRUE | FALSE | 0.026092 | 7.1014e-15 | 21.9007 | 8.28 | 3.9003 | 88.7278 | 89.4465 | 8 |  | 39.0889 | 15.2 | 0 | 152 | 0 | 180.3805
Our programme | central | 2035 | 433.422 | 5.868 | 60.0789 | 2 | 84.7651 | 55.5029 | 46.1547 | 46.4289 | 29.7463 | 16.6826 | 46.0874 | 46.255 | 19.1533 | 33.1332 | TRUE | FALSE | TRUE | TRUE | 7.2333e-15 | 5.7189e-15 | 18.5932 | 11.97 | 5.5189 | 79.4751 | 80.6686 | 12 |  | 41.2789 | 18.8 | 0 | 188 | 14.9037 | 160.8427
Our programme | central | 2036 | 461.449 | 5.868 | 65.2469 | 4 | 84.1397 | 55.5029 | 47.1169 | 47.3786 | 29.887 | 17.4916 | 47.0809 | 47.2218 | 20.7713 | 31.2459 | TRUE | FALSE | TRUE | FALSE | 0.15314 | 7.6312e-15 | 17.2594 | 16.63 | 7.4838 | 78.0036 | 79.8617 | 16 |  | 42.8469 | 22.4 | 0 | 224 | 29.8073 | 156.3811
Our programme | central | 2037 | 488.675 | 7.568 | 70.6419 | 6 | 82.7718 | 55.5029 | 48.1443 | 48.8095 | 30.6511 | 18.1583 | 48.0894 | 48.6019 | 20.8816 | 29.7852 | TRUE | FALSE | TRUE | FALSE | 0.011386 | 5.2773e-15 | 14.5132 | 21.98 | 9.6292 | 69.3097 | 80.6367 | 20 |  | 44.6419 | 26 | 0 | 260 | 44.711 | 137.8133
Our programme | central | 2038 | 513.806 | 9.168 | 73.9719 | 8 | 81.1551 | 55.5029 | 49.6411 | 50.0206 | 31.2455 | 18.775 | 49.4376 | 49.7639 | 20.8723 | 28.3586 | TRUE | FALSE | TRUE | TRUE | 1.1045e-14 | 7.379e-15 | 12.2445 | 27.6 | 11.775 | 61.3736 | 82.3369 | 24 |  | 45.8719 | 28.1 | 0 | 281 | 59.6146 | 121.0379
Our programme | central | 2039 | 536.367 | 11.708 | 76.2299 | 8 | 79.9688 | 55.5029 | 51.2195 | 51.0489 | 31.943 | 19.1059 | 50.885 | 50.7694 | 21.414 | 26.6749 | TRUE | FALSE | TRUE | TRUE | 1.2765e-14 | 8.6397e-15 | 10.9713 | 31.3 | 13.1358 | 57.2214 | 79.2121 | 28 |  | 47.8299 | 28.4 | 0 | 284 | 59.6146 | 111.8984
Our programme | central | 2040 | 563.928 | 13.588 | 80.0199 | 8 | 78.992 | 55.4256 | 52.1282 | 51.6183 | 32.0979 | 19.5205 | 51.7551 | 51.3772 | 23.8198 | 23.5644 | TRUE | FALSE | TRUE | TRUE | 3.2131e-14 | 9.4868e-15 | 10.7719 | 40.34 | 16.2672 | 58.9068 | 82.9339 | 32 |  | 48.9199 | 31.1 | 0 | 311 | 59.6146 | 113.5618
Our programme | central | 2041 | 582.761 | 16.408 | 83.2799 | 8 | 77.3384 | 54.5142 | 53.4387 | 52.3337 | 32.4687 | 19.8649 | 52.9928 | 52.0617 | 23.9668 | 21.9449 | TRUE | FALSE | TRUE | TRUE | 3.8654e-14 | 9.9344e-15 | 9.5268 | 42.98 | 17.1459 | 53.7227 | 78.5567 | 36 |  | 52.1799 | 31.1 | 0 | 311 | 59.6146 | 102.7041
Our programme | central | 2042 | 602.352 | 20.168 | 82.4199 | 8 | 74.3569 | 53.7572 | 54.6447 | 52.6172 | 32.4734 | 20.1437 | 54.197 | 52.3032 | 23.7685 | 20.2619 | TRUE | FALSE | TRUE | TRUE | 3.9897e-14 | 1.0465e-14 | 8.002 | 47.77 | 18.6613 | 46.5729 | 71.1923 | 36 |  | 51.3199 | 31.1 | 0 | 311 | 59.6146 | 88.1812
Our programme | central | 2043 | 621.073 | 23.928 | 83.3399 | 8 | 72.6581 | 52.6376 | 55.2466 | 52.9784 | 32.3209 | 20.6575 | 54.7509 | 52.6394 | 22.9973 | 21.2423 | TRUE | FALSE | TRUE | TRUE | 3.7211e-14 | 1.0117e-14 | 7.4977 | 53.71 | 20.4741 | 45.1558 | 65.0647 | 37 |  | 52.2399 | 31.1 | 0 | 311 | 59.6146 | 85.5841
Our programme | central | 2044 | 635.458 | 27.688 | 83.3099 | 8 | 71.6496 | 50.0004 | 55.8211 | 53.5775 | 32.6497 | 20.9278 | 55.3037 | 53.22 | 22.0164 | 21.9034 | TRUE | FALSE | TRUE | TRUE | 3.8405e-14 | 1.0721e-14 | 6.8885 | 56.64 | 21.3376 | 42.8275 | 62.6316 | 38 |  | 52.2099 | 31.1 | 0 | 311 | 59.6146 | 81.2409
Our programme | central | 2045 | 654.296 | 31.448 | 86.0469 | 8 | 70.4921 | 45.7444 | 56.2113 | 53.9614 | 32.3781 | 21.5832 | 55.578 | 53.5505 | 21.6447 | 23.4732 | TRUE | FALSE | TRUE | TRUE | 3.1534e-14 | 1.0466e-14 | 6.6718 | 65.79 | 23.869 | 42.8417 | 64.5994 | 40 |  | 53.9469 | 32.1 | 0 | 321 | 59.6146 | 81.6067
Our programme | central | 2046 | 670.284 | 35.208 | 86.0469 | 8 | 70.1154 | 43.6779 | 57.3334 | 54.9652 | 32.9582 | 22.0071 | 56.6618 | 54.5226 | 20.0462 | 24.7797 | TRUE | FALSE | TRUE | TRUE | 2.3746e-14 | 9.1721e-15 | 5.8608 | 74.25 | 26.1553 | 38.7403 | 60.645 | 40 |  | 53.9469 | 32.1 | 0 | 321 | 59.6146 | 73.7288
Our programme | central | 2047 | 681.236 | 38.968 | 86.0469 | 8 | 68.3652 | 42.9291 | 57.9957 | 55.5288 | 33.2022 | 22.3267 | 57.2666 | 55.0424 | 18.1179 | 26.3068 | TRUE | FALSE | TRUE | TRUE | 1.3657e-14 | 7.3775e-15 | 5.0809 | 79.39 | 27.5708 | 34.3168 | 55.9149 | 40 |  | 53.9469 | 32.1 | 0 | 321 | 59.6146 | 65.5529
Our programme | central | 2048 | 691.034 | 42.728 | 86.0469 | 8 | 66.3206 | 42.6396 | 58.6397 | 56.09 | 33.4428 | 22.6472 | 57.8671 | 55.5465 | 15.9997 | 28.1392 | TRUE | TRUE | TRUE | TRUE | 9.8268e-15 | 6.2416e-15 | 4.3592 | 84.12 | 28.8797 | 30.0406 | 51.0896 | 40 |  | 53.9469 | 32.1 | 0 | 321 | 59.6146 | 57.6293
Our programme | central | 2049 | 700.725 | 46.488 | 85.1489 | 8 | 63.8724 | 42.3292 | 59.0459 | 56.4257 | 33.4561 | 22.9696 | 58.2263 | 55.8276 | 14.0159 | 29.8627 | TRUE | TRUE | TRUE | TRUE | 7.9226e-15 | 4.9758e-15 | 3.7576 | 88.97 | 30.1974 | 26.3981 | 46.9008 | 40 |  | 53.0489 | 32.1 | 0 | 321 | 59.6146 | 50.8607
Our programme | central | 2050 | 705.223 | 50.248 | 81.5659 | 8 | 62.9013 | 42.0193 | 59.3659 | 56.722 | 33.5281 | 23.1939 | 58.4742 | 56.0206 | 10.8957 | 33.2601 | TRUE | TRUE | TRUE | TRUE | 6.6862e-15 | 3.776e-15 | 3.043 | 88.71 | 30.3718 | 21.7127 | 40.172 | 40 |  | 49.4659 | 32.1 | 0 | 321 | 59.6146 | 42.231
Our programme | high | 2030 | 344.803 | 3.3089 | 34.4879 | 0 | 74.6673 | 55.5029 | 40.6603 | 40.6385 | 26.2425 | 14.396 | 40.5368 | 40.5162 | 16.6369 | 35.8007 | FALSE | FALSE | FALSE | FALSE | 3.0869 | 0.055915 | 24.7 | 3.58 | 1.735 | 84.8499 | 85.1372 | 0 |  | 34.4879 | 0 | 0 | 0 | 0 | 175.0343
Our programme | high | 2031 | 362.869 | 3.7837 | 37.3079 | 0 | 80.0161 | 55.5029 | 42.0712 | 42.3052 | 27.3866 | 14.9187 | 41.9004 | 42.1138 | 16.0963 | 36.3389 | FALSE | FALSE | FALSE | FALSE | 6.6019 | 0.046025 | 23.3592 | 5.07 | 2.4354 | 84.7829 | 84.8636 | 0 |  | 33.3079 | 4 | 0 | 40 | 0 | 174.3352
Our programme | high | 2032 | 382.238 | 4.458 | 40.6889 | 0 | 86.4936 | 55.5029 | 43.8462 | 44.3435 | 28.8545 | 15.489 | 43.6293 | 44.0822 | 15.6426 | 36.8803 | FALSE | FALSE | FALSE | FALSE | 1.7707 | 0.021969 | 21.8245 | 5.36 | 2.5729 | 83.6534 | 83.4714 | 0 |  | 32.6889 | 8 | 0 | 80 | 0 | 171.8531
Our programme | high | 2033 | 402.822 | 4.458 | 47.0089 | 0 | 85.8818 | 55.5029 | 44.4873 | 44.8751 | 28.9704 | 15.9047 | 44.3604 | 44.721 | 18.1055 | 34.3458 | FALSE | FALSE | FALSE | FALSE | 4.2782 | 0.0097453 | 21.9674 | 5.5 | 2.6374 | 87.6963 | 87.8723 | 4 |  | 35.4089 | 11.6 | 0 | 116 | 0 | 178.8394
Our programme | high | 2034 | 425.413 | 4.458 | 54.2889 | 0 | 85.5065 | 55.5029 | 45.4255 | 45.7118 | 29.2588 | 16.453 | 45.3782 | 45.6504 | 20.739 | 31.7391 | FALSE | FALSE | FALSE | FALSE | 2.9918 | 0.0029922 | 22.2656 | 5.73 | 2.7426 | 92.7557 | 93.2221 | 8 |  | 39.0889 | 15.2 | 0 | 152 | 0 | 187.5467
Our programme | high | 2035 | 450.076 | 5.868 | 60.0789 | 2 | 84.7651 | 55.5029 | 46.5389 | 46.8537 | 29.7463 | 17.1074 | 46.5337 | 46.7137 | 20.5988 | 31.6103 | FALSE | FALSE | TRUE | FALSE | 1.4987 | 6.6796e-15 | 19.2275 | 7.36 | 3.4881 | 84.8402 | 85.5993 | 12 |  | 41.2789 | 18.8 | 0 | 188 | 14.9037 | 170.5678
Our programme | high | 2036 | 483.247 | 5.868 | 65.2469 | 4 | 84.1397 | 55.5029 | 47.7047 | 47.9977 | 29.887 | 18.1108 | 47.7184 | 47.8781 | 22.7524 | 29.1485 | FALSE | FALSE | TRUE | FALSE | 1.4053 | 9.5096e-15 | 18.2671 | 11.06 | 5.1422 | 85.8184 | 87.1547 | 16 |  | 42.8469 | 22.4 | 0 | 224 | 29.8073 | 170.6834
Our programme | high | 2037 | 525.964 | 7.568 | 70.6419 | 6 | 82.7718 | 55.5029 | 49.2336 | 49.8113 | 30.6511 | 19.1602 | 49.2502 | 49.6997 | 24.8329 | 25.7887 | TRUE | FALSE | TRUE | FALSE | 1.1008 | 8.0444e-15 | 16.1533 | 26.12 | 11.2859 | 81.8922 | 94.4695 | 20 |  | 44.6419 | 26 | 0 | 260 | 44.711 | 160.494
Our programme | high | 2038 | 558.403 | 9.168 | 75.4719 | 8 | 81.1551 | 55.5029 | 51.0227 | 51.4036 | 31.3067 | 20.0968 | 50.9272 | 51.267 | 25.8157 | 23.4256 | TRUE | FALSE | TRUE | FALSE | 0.82543 | 1.2372e-14 | 14.5118 | 32.62 | 13.7306 | 77.7882 | 101.145 | 24 |  | 45.8719 | 29.6 | 0 | 296 | 59.6146 | 150.9487
Our programme | high | 2039 | 585.948 | 11.708 | 81.0299 | 8 | 79.9688 | 55.5029 | 52.822 | 52.9037 | 32.1388 | 20.7648 | 52.6164 | 52.7561 | 27.0108 | 21.0755 | TRUE | FALSE | TRUE | FALSE | 0.56536 | 1.4292e-14 | 13.8254 | 35.44 | 14.7879 | 77.4291 | 102.0924 | 28 |  | 47.8299 | 33.2 | 0 | 332 | 59.6146 | 149.1274
Our programme | high | 2040 | 616.965 | 13.588 | 85.7199 | 8 | 78.992 | 55.4256 | 54.011 | 53.8611 | 32.3304 | 21.5307 | 53.7711 | 53.7349 | 29.7412 | 17.8261 | TRUE | FALSE | TRUE | FALSE | 0.63 | 1.5556e-14 | 14.2815 | 42.69 | 17.3479 | 84.0255 | 110.8354 | 32 |  | 48.9199 | 36.8 | 0 | 368 | 59.6146 | 160.1006
Our programme | high | 2041 | 644.531 | 16.408 | 92.5799 | 8 | 77.3384 | 54.5142 | 55.7002 | 55.1951 | 32.8481 | 22.347 | 55.4186 | 55.0547 | 31.0928 | 15.4395 | TRUE | FALSE | TRUE | FALSE | 0.25092 | 1.6887e-14 | 13.8145 | 49.95 | 19.7808 | 84.5653 | 113.1775 | 36 |  | 52.1799 | 40.4 | 0 | 404 | 59.6146 | 159.7473
Our programme | high | 2042 | 672.19 | 20.168 | 98.9999 | 8 | 74.3569 | 53.7572 | 57.2623 | 56.3898 | 33.2145 | 23.1753 | 56.9962 | 56.2247 | 32.2067 | 13.0133 | TRUE | FALSE | TRUE | FALSE | 0.060289 | 1.8848e-14 | 13.0784 | 58.89 | 22.6255 | 83.2098 | 112.7633 | 40 |  | 54.9999 | 44 | 0 | 440 | 59.6146 | 155.912
Our programme | high | 2043 | 694.708 | 23.928 | 106.2799 | 8 | 72.6581 | 52.6376 | 58.3849 | 57.3397 | 33.3699 | 23.9698 | 58.0839 | 57.1611 | 32.159 | 13.4145 | TRUE | FALSE | TRUE | FALSE | 0.00079298 | 1.8791e-14 | 12.704 | 64.35 | 24.3679 | 83.718 | 110.4075 | 44 |  | 58.6799 | 47.6 | 0 | 476 | 59.6146 | 156.8772
Our programme | high | 2044 | 709.671 | 27.688 | 109.0099 | 8 | 71.6496 | 50.0004 | 59.554 | 58.1926 | 33.8598 | 24.3328 | 59.227 | 58.0019 | 31.3209 | 13.8525 | TRUE | FALSE | TRUE | TRUE | 9.3522e-14 | 2.0677e-14 | 12.0209 | 64.05 | 24.4247 | 81.5878 | 108.2192 | 48 |  | 61.4099 | 47.6 | 0 | 476 | 59.6146 | 153.3067
Our programme | high | 2045 | 724.44 | 31.448 | 112.5869 | 8 | 70.4921 | 45.7444 | 60.4312 | 58.6112 | 33.6548 | 24.9564 | 59.9729 | 58.3547 | 30.3976 | 16.1207 | TRUE | TRUE | TRUE | TRUE | 4.0167e-14 | 2.0107e-14 | 11.6085 | 65.36 | 24.9941 | 80.825 | 108.5419 | 52 |  | 64.9869 | 47.6 | 0 | 476 | 59.6146 | 152.8482
Our programme | high | 2046 | 737.93 | 35.208 | 113.5069 | 8 | 70.1154 | 43.6779 | 61.7753 | 59.5851 | 34.2885 | 25.2966 | 61.265 | 59.289 | 28.5271 | 17.5499 | TRUE | TRUE | TRUE | TRUE | 2.8407e-14 | 1.8064e-14 | 10.4961 | 67.55 | 25.8438 | 74.8429 | 102.4318 | 53 |  | 65.9069 | 47.6 | 0 | 476 | 59.6146 | 141.9941
Our programme | high | 2047 | 752.313 | 38.968 | 113.5069 | 8 | 68.3652 | 42.9291 | 62.5082 | 60.2055 | 34.5325 | 25.673 | 61.9588 | 59.8876 | 27.2734 | 18.271 | TRUE | TRUE | TRUE | TRUE | 2.4514e-14 | 1.6443e-14 | 9.6834 | 72.86 | 27.6304 | 70.6324 | 98.7856 | 53 |  | 65.9069 | 47.6 | 0 | 476 | 59.6146 | 134.2613
Our programme | high | 2048 | 766.439 | 42.728 | 113.5069 | 8 | 66.3206 | 42.6396 | 63.2299 | 60.8079 | 34.7732 | 26.0347 | 62.6443 | 60.467 | 26.0192 | 18.9972 | TRUE | TRUE | TRUE | TRUE | 2.381e-14 | 1.5767e-14 | 8.8844 | 79.13 | 29.6438 | 66.2344 | 95.0035 | 53 |  | 65.9069 | 47.6 | 0 | 476 | 59.6146 | 126.0865
Our programme | high | 2049 | 776.227 | 46.488 | 112.6089 | 8 | 63.8724 | 42.3292 | 63.6096 | 61.0931 | 34.7865 | 26.3066 | 62.9716 | 60.7103 | 24.1929 | 20.1731 | TRUE | TRUE | TRUE | TRUE | 2.2091e-14 | 1.4055e-14 | 8.0868 | 81.23 | 30.4662 | 61.3232 | 89.9386 | 53 |  | 65.0089 | 47.6 | 0 | 476 | 59.6146 | 117.2506
Our programme | high | 2050 | 784.736 | 50.248 | 109.9459 | 8 | 62.9013 | 42.0193 | 64.0582 | 61.3869 | 34.9122 | 26.4747 | 63.3614 | 60.9333 | 21.5106 | 22.4301 | TRUE | TRUE | TRUE | TRUE | 1.8893e-14 | 1.2351e-14 | 7.0957 | 81.91 | 30.8834 | 54.7633 | 82.4326 | 54 |  | 62.3459 | 47.6 | 0 | 476 | 59.6146 | 105.3631
Renewables + extra gas | low | 2030 | 323.698 | 3.3089 | 34.4879 | 0 | 74.6673 | 55.5029 | 40.426 | 40.4231 | 26.2425 | 14.1806 | 40.1423 | 40.1393 | 13.7793 | 38.5677 | FALSE | FALSE | FALSE | FALSE | 1.8917 | 0.023973 | 25.1898 | 0.53 | 0.26353 | 82.6324 | 82.6702 | 0 |  | 34.4879 | 0 | 0 | 0 | 0 | 171.5271
Renewables + extra gas | low | 2031 | 332.351 | 3.7837 | 37.3079 | 0 | 81.4161 | 55.5029 | 41.8809 | 42.1287 | 27.5058 | 14.6229 | 41.4648 | 41.6973 | 12.0047 | 40.4657 | FALSE | FALSE | FALSE | FALSE | 4.7608 | 0.013601 | 23.8493 | 0.54 | 0.26839 | 81.2303 | 81.0829 | 0 |  | 33.3079 | 4 | 0 | 40 | 0 | 168.628
Renewables + extra gas | low | 2032 | 341.738 | 4.458 | 40.6889 | 0 | 89.2936 | 55.5029 | 43.6984 | 44.1879 | 29.0929 | 15.095 | 43.1688 | 43.6345 | 10.4773 | 42.1592 | FALSE | FALSE | FALSE | FALSE | 0.36453 | 0.0043658 | 22.2887 | 0.57 | 0.28354 | 78.7079 | 78.4492 | 0 |  | 32.6889 | 8 | 0 | 80 | 0 | 163.7403
Renewables + extra gas | low | 2033 | 351.742 | 4.458 | 47.0089 | 0 | 90.0818 | 55.7029 | 44.2385 | 44.6323 | 29.3349 | 15.2974 | 43.747 | 44.1281 | 11.3126 | 41.1311 | FALSE | FALSE | TRUE | FALSE | 0.035614 | 2.2763e-15 | 22.1068 | 0.89 | 0.44128 | 79.9307 | 79.8312 | 4 |  | 35.4089 | 11.6 | 0 | 116 | 0 | 165.8699
Renewables + extra gas | low | 2034 | 362.296 | 4.458 | 52.7889 | 0 | 96.9065 | 56.7029 | 46.275 | 46.4972 | 30.6822 | 15.815 | 45.7236 | 45.9415 | 10.7625 | 41.8453 | TRUE | FALSE | TRUE | TRUE | 3.5065e-15 | 2.2489e-15 | 21.4626 | 1.52 | 0.75048 | 80.131 | 80.1735 | 8 |  | 39.0889 | 13.7 | 0 | 137 | 0 | 166.2449
Renewables + extra gas | low | 2035 | 372.906 | 5.868 | 54.9789 | 0 | 101.3651 | 57.3029 | 47.6621 | 47.74 | 31.6457 | 16.0943 | 47.0745 | 47.0985 | 9.7494 | 42.9798 | TRUE | FALSE | TRUE | TRUE | 3.2472e-15 | 2.0271e-15 | 19.5121 | 2.34 | 1.1487 | 75.3284 | 75.4781 | 12 |  | 41.2789 | 13.7 | 0 | 137 | 0 | 156.3172
Renewables + extra gas | low | 2036 | 384.269 | 5.868 | 55.6269 | 0 | 104.1397 | 59.0029 | 48.6983 | 48.3457 | 32.0108 | 16.3349 | 48.1012 | 47.7219 | 10.1756 | 42.6006 | TRUE | FALSE | TRUE | TRUE | 3.5847e-15 | 2.259e-15 | 19.1895 | 3.1 | 1.5144 | 76.1186 | 76.3435 | 15 |  | 41.9269 | 13.7 | 0 | 137 | 0 | 157.6946
Renewables + extra gas | low | 2037 | 396.144 | 5.868 | 56.5019 | 0 | 107.0718 | 60.8029 | 49.5184 | 48.9427 | 32.3585 | 16.5842 | 48.9135 | 48.3353 | 10.6003 | 42.2314 | TRUE | FALSE | TRUE | TRUE | 3.8973e-15 | 2.5625e-15 | 18.8656 | 4.55 | 2.2035 | 76.9321 | 77.2731 | 18 |  | 42.8019 | 13.7 | 0 | 137 | 0 | 159.112
Renewables + extra gas | low | 2038 | 407.229 | 7.468 | 56.8119 | 0 | 110.7551 | 62.6029 | 50.8337 | 50.2563 | 33.4826 | 16.7737 | 50.1528 | 49.5731 | 9.6896 | 43.2653 | TRUE | FALSE | TRUE | TRUE | 3.0909e-15 | 2.0215e-15 | 17.0579 | 5.01 | 2.4212 | 71.7818 | 72.1388 | 21 |  | 43.1119 | 13.7 | 0 | 137 | 0 | 148.5311
Renewables + extra gas | low | 2039 | 419.392 | 9.068 | 56.9299 | 0 | 113.2688 | 64.4029 | 51.9634 | 51.3803 | 34.4793 | 16.901 | 51.2312 | 50.6465 | 9.1086 | 43.8214 | TRUE | FALSE | TRUE | TRUE | 2.8955e-15 | 1.7703e-15 | 15.3715 | 6.03 | 2.8994 | 66.7311 | 67.162 | 23 |  | 43.2299 | 13.7 | 0 | 137 | 0 | 138.0382
Renewables + extra gas | low | 2040 | 433.613 | 9.068 | 59.1199 | 0 | 117.092 | 66.5256 | 52.7468 | 52.0799 | 35.0592 | 17.0207 | 52.0418 | 51.3732 | 9.7765 | 43.1978 | TRUE | FALSE | TRUE | TRUE | 2.8741e-15 | 1.9398e-15 | 15.1308 | 6.94 | 3.3239 | 68.1562 | 68.6524 | 27 |  | 44.3199 | 14.8 | 0 | 148 | 0 | 140.5953
Renewables + extra gas | low | 2041 | 450.011 | 9.068 | 62.1199 | 0 | 122.0384 | 68.2142 | 54.0468 | 53.305 | 35.8399 | 17.4651 | 53.3488 | 52.6044 | 10.1093 | 42.8855 | TRUE | FALSE | TRUE | TRUE | 3.0482e-15 | 2.1007e-15 | 14.9077 | 8.15 | 3.8859 | 69.5077 | 70.1045 | 28 |  | 44.8199 | 17.3 | 0 | 173 | 0 | 143.048
Renewables + extra gas | low | 2042 | 464.557 | 9.068 | 64.7199 | 0 | 125.0569 | 69.6572 | 54.8328 | 54.0554 | 36.2454 | 17.81 | 54.151 | 53.3725 | 10.6195 | 42.405 | TRUE | FALSE | TRUE | TRUE | 3.368e-15 | 2.3727e-15 | 14.7944 | 8.63 | 4.1107 | 71.0014 | 71.6545 | 31 |  | 46.7199 | 18 | 0 | 180 | 0 | 145.7665
Renewables + extra gas | low | 2043 | 477.519 | 9.068 | 65.7199 | 0 | 129.1581 | 70.4376 | 55.8655 | 55.0759 | 36.9519 | 18.1239 | 55.1907 | 54.3998 | 10.8892 | 42.2685 | TRUE | FALSE | TRUE | TRUE | 3.2863e-15 | 2.4828e-15 | 14.5912 | 8.76 | 4.1749 | 71.8906 | 72.543 | 31 |  | 46.7199 | 19 | 0 | 190 | 0 | 147.417
Renewables + extra gas | low | 2044 | 490.691 | 9.068 | 68.6299 | 0 | 131.6496 | 69.8004 | 56.2851 | 55.4801 | 37.2694 | 18.2107 | 55.6438 | 54.8402 | 11.7871 | 41.2872 | TRUE | FALSE | TRUE | TRUE | 3.8582e-15 | 3.0396e-15 | 14.6115 | 9.59 | 4.5528 | 74.1554 | 74.9257 | 34 |  | 48.5299 | 20.1 | 0 | 201 | 0 | 151.4681
Renewables + extra gas | low | 2045 | 504.316 | 9.068 | 69.3269 | 0 | 135.7921 | 67.6444 | 57.2353 | 56.4035 | 37.8707 | 18.5328 | 56.6147 | 55.7834 | 12.3133 | 40.8719 | TRUE | FALSE | TRUE | TRUE | 4.0998e-15 | 3.2538e-15 | 14.4947 | 10.36 | 4.9006 | 75.4354 | 76.2544 | 34 |  | 48.4269 | 20.9 | 0 | 209 | 0 | 153.7602
Renewables + extra gas | low | 2046 | 516.137 | 9.068 | 71.3669 | 0 | 138.6154 | 67.5779 | 57.9608 | 57.1315 | 38.3009 | 18.8306 | 57.3516 | 56.5263 | 12.7673 | 40.4037 | TRUE | FALSE | TRUE | TRUE | 4.3769e-15 | 3.5456e-15 | 14.4779 | 11.34 | 5.3458 | 76.9293 | 77.8328 | 36 |  | 50.2669 | 21.1 | 0 | 211 | 0 | 156.3945
Renewables + extra gas | low | 2047 | 526.834 | 9.068 | 72.9669 | 0 | 141.8652 | 68.6291 | 58.7379 | 57.8537 | 38.7254 | 19.1283 | 58.1299 | 57.2502 | 12.9686 | 40.2605 | TRUE | FALSE | TRUE | TRUE | 4.5191e-15 | 3.7872e-15 | 14.3821 | 12.32 | 5.7902 | 77.9158 | 78.8869 | 36 |  | 50.2669 | 22.7 | 0 | 227 | 0 | 158.1754
Renewables + extra gas | low | 2048 | 537.853 | 9.068 | 74.8069 | 0 | 144.3206 | 70.5396 | 59.37 | 58.4769 | 39.0806 | 19.3963 | 58.7695 | 57.8824 | 13.272 | 39.9693 | TRUE | FALSE | TRUE | TRUE | 4.6469e-15 | 3.9851e-15 | 14.312 | 13.57 | 6.3517 | 79.0361 | 80.1071 | 38 |  | 52.1069 | 22.7 | 0 | 227 | 0 | 160.1729
Renewables + extra gas | low | 2049 | 548.276 | 9.068 | 76.0289 | 0 | 147.3724 | 73.7292 | 59.9664 | 58.9948 | 39.3353 | 19.6595 | 59.3612 | 58.3955 | 13.3538 | 39.9468 | TRUE | FALSE | TRUE | TRUE | 4.917e-15 | 3.9943e-15 | 14.18 | 14.55 | 6.7925 | 79.7728 | 80.9465 | 39 |  | 52.1289 | 23.9 | 0 | 239 | 0 | 161.5365
Renewables + extra gas | low | 2050 | 558.75 | 9.068 | 77.3259 | 0 | 149.6013 | 77.9193 | 60.4362 | 59.4586 | 39.5659 | 19.8927 | 59.8317 | 58.8595 | 13.4955 | 39.8626 | TRUE | FALSE | TRUE | TRUE | 9.4751e-15 | 4.448e-15 | 14.0683 | 15.21 | 7.0932 | 80.5959 | 81.8333 | 43 |  | 52.2259 | 25.1 | 0 | 251 | 0 | 163.0782
Renewables + extra gas | central | 2030 | 339.295 | 3.3089 | 34.4879 | 0 | 74.6673 | 55.5029 | 40.5782 | 40.5553 | 26.2425 | 14.3128 | 40.4267 | 40.4038 | 16.1073 | 36.4255 | FALSE | FALSE | FALSE | FALSE | 2.5779 | 0.026022 | 24.7104 | 3.83 | 1.8525 | 83.8047 | 84.1107 | 0 |  | 34.4879 | 0 | 0 | 0 | 0 | 173.3018
Renewables + extra gas | central | 2031 | 355.884 | 3.7837 | 37.3079 | 0 | 83.3161 | 57.7029 | 42.3596 | 42.5848 | 27.7416 | 14.8433 | 42.0897 | 42.2947 | 14.5029 | 38.1288 | FALSE | FALSE | FALSE | FALSE | 1.5138 | 0.015166 | 23.0208 | 5.46 | 2.617 | 82.7149 | 82.9192 | 0 |  | 33.3079 | 4 | 0 | 40 | 0 | 170.9335
Renewables + extra gas | central | 2032 | 373.666 | 4.458 | 40.6889 | 0 | 91.8936 | 59.9029 | 44.4779 | 44.9485 | 29.5384 | 15.4102 | 44.1224 | 44.5601 | 13.4415 | 39.4144 | FALSE | FALSE | FALSE | FALSE | 1.0796 | 0.0048555 | 21.2867 | 6.29 | 3.0062 | 80.7687 | 80.8408 | 0 |  | 32.6889 | 8 | 0 | 80 | 0 | 167.0223
Renewables + extra gas | central | 2033 | 392.593 | 4.458 | 47.0089 | 0 | 100.4818 | 62.1029 | 46.847 | 47.2081 | 31.1403 | 16.0679 | 46.4286 | 46.7704 | 13.1378 | 39.9111 | FALSE | FALSE | TRUE | FALSE | 0.26657 | 3.2279e-15 | 20.445 | 7.55 | 3.59 | 81.6676 | 82.0571 | 4 |  | 35.4089 | 11.6 | 0 | 116 | 0 | 168.653
Renewables + extra gas | central | 2034 | 411.573 | 4.458 | 54.2889 | 0 | 109.0065 | 64.3029 | 49.307 | 49.5782 | 32.8128 | 16.7655 | 48.8371 | 49.1006 | 12.9113 | 40.2818 | TRUE | FALSE | TRUE | FALSE | 0.010787 | 3.4933e-15 | 19.7266 | 8.28 | 3.9307 | 82.6571 | 83.1779 | 8 |  | 39.0889 | 15.2 | 0 | 152 | 0 | 170.4042
Renewables + extra gas | central | 2035 | 433.422 | 5.868 | 57.1789 | 0 | 117.3651 | 66.5029 | 51.6891 | 51.8307 | 34.5037 | 17.3271 | 51.1723 | 51.2714 | 12.0463 | 41.2853 | TRUE | FALSE | TRUE | TRUE | 4.782e-15 | 3.4304e-15 | 17.6862 | 11.97 | 5.5933 | 78.2988 | 79.1464 | 12 |  | 41.2789 | 15.9 | 0 | 159 | 0 | 161.2605
Renewables + extra gas | central | 2036 | 461.449 | 5.868 | 61.2469 | 0 | 124.5397 | 70.8029 | 53.8839 | 53.7869 | 35.7994 | 17.9875 | 53.3503 | 53.2373 | 12.7371 | 40.7312 | TRUE | FALSE | TRUE | TRUE | 5.5138e-15 | 4.348e-15 | 17.1174 | 16.63 | 7.6418 | 80.3814 | 81.6568 | 16 |  | 42.8469 | 18.4 | 0 | 184 | 0 | 164.8911
Renewables + extra gas | central | 2037 | 488.675 | 5.868 | 65.1419 | 0 | 131.6718 | 75.0029 | 56.0377 | 55.6749 | 37.0376 | 18.6372 | 55.4869 | 55.1306 | 13.2829 | 40.2538 | TRUE | FALSE | TRUE | TRUE | 6.5583e-15 | 5.155e-15 | 16.6372 | 21.98 | 9.9265 | 82.5001 | 84.2377 | 20 |  | 44.6419 | 20.5 | 0 | 205 | 0 | 168.5951
Renewables + extra gas | central | 2038 | 513.806 | 7.468 | 67.2719 | 0 | 138.5551 | 78.9029 | 58.5719 | 57.945 | 38.8292 | 19.1158 | 57.9646 | 57.3439 | 12.7397 | 40.8956 | TRUE | FALSE | TRUE | TRUE | 6.132e-15 | 4.7023e-15 | 14.9969 | 27.6 | 12.261 | 78.3169 | 80.4528 | 24 |  | 45.8719 | 21.4 | 0 | 214 | 0 | 159.7637
Renewables + extra gas | central | 2039 | 536.367 | 9.068 | 69.2299 | 0 | 143.9688 | 82.3029 | 60.9055 | 59.9721 | 40.468 | 19.5042 | 60.2559 | 59.3278 | 12.3104 | 41.2674 | TRUE | FALSE | TRUE | TRUE | 5.7767e-15 | 4.3617e-15 | 13.5656 | 31.3 | 13.7796 | 74.0182 | 76.4245 | 28 |  | 47.8299 | 21.4 | 0 | 214 | 0 | 150.6891
Renewables + extra gas | central | 2040 | 563.928 | 9.068 | 73.1199 | 0 | 151.892 | 86.5256 | 62.922 | 61.8132 | 41.8498 | 19.9634 | 62.2816 | 61.1825 | 12.9441 | 40.7151 | TRUE | FALSE | TRUE | TRUE | 4.8956e-15 | 4.0948e-15 | 13.292 | 40.34 | 17.3287 | 76.4821 | 79.56 | 32 |  | 48.9199 | 24.2 | 0 | 242 | 0 | 155
Renewables + extra gas | central | 2041 | 582.761 | 9.068 | 76.3799 | 0 | 157.0384 | 88.5142 | 64.4459 | 63.1743 | 42.7168 | 20.4575 | 63.8059 | 62.5474 | 13.292 | 40.4237 | TRUE | FALSE | TRUE | TRUE | 5.1941e-15 | 4.4368e-15 | 13.2076 | 42.98 | 18.3751 | 78.4059 | 81.7251 | 36 |  | 52.1799 | 24.2 | 0 | 242 | 0 | 158.4071
Renewables + extra gas | central | 2042 | 602.352 | 9.068 | 79.1999 | 0 | 161.4569 | 90.7572 | 65.6644 | 64.2908 | 43.3724 | 20.9184 | 65.0351 | 63.6737 | 13.7861 | 40.0261 | TRUE | FALSE | TRUE | TRUE | 1.9153e-14 | 5.0956e-15 | 13.136 | 47.77 | 20.1923 | 80.448 | 84.144 | 40 |  | 54.9999 | 24.2 | 0 | 242 | 0 | 161.9705
Renewables + extra gas | central | 2043 | 621.073 | 9.068 | 81.9599 | 0 | 167.0581 | 92.4376 | 67.1392 | 65.8113 | 44.4362 | 21.3752 | 66.5176 | 65.2008 | 14.0575 | 39.8232 | TRUE | FALSE | TRUE | TRUE | 3.3992e-14 | 5.5595e-15 | 12.97 | 53.71 | 22.3884 | 81.8207 | 85.8483 | 43 |  | 57.7599 | 24.2 | 0 | 242 | 0 | 164.3512
Renewables + extra gas | central | 2044 | 635.458 | 9.068 | 83.7699 | 0 | 170.6496 | 92.0004 | 67.8302 | 66.4076 | 44.888 | 21.5195 | 67.2225 | 65.8141 | 14.7058 | 39.1984 | TRUE | FALSE | TRUE | TRUE | 5.1173e-14 | 6.741e-15 | 13.0416 | 56.64 | 23.4435 | 84.4387 | 88.7604 | 46 |  | 59.5699 | 24.2 | 0 | 242 | 0 | 168.9212
Renewables + extra gas | central | 2045 | 654.296 | 9.068 | 83.9669 | 0 | 175.1921 | 90.6444 | 69.0219 | 67.5077 | 45.6061 | 21.9016 | 68.4319 | 66.9322 | 15.3622 | 38.7522 | TRUE | FALSE | TRUE | TRUE | 6.6706e-14 | 8.1652e-15 | 12.9901 | 65.79 | 26.5518 | 86.437 | 91.2177 | 46 |  | 59.4669 | 24.5 | 0 | 245 | 0 | 172.258
Renewables + extra gas | central | 2046 | 670.284 | 9.068 | 86.2069 | 0 | 179.4154 | 91.1779 | 70.2332 | 68.5542 | 46.2628 | 22.2915 | 69.6471 | 67.9848 | 15.7102 | 38.4412 | TRUE | FALSE | TRUE | TRUE | 8.0682e-14 | 8.829e-15 | 12.9717 | 74.25 | 29.3391 | 88.2998 | 93.6343 | 48 |  | 61.3069 | 24.9 | 0 | 249 | 0 | 175.3525
Renewables + extra gas | central | 2047 | 681.236 | 9.068 | 87.7069 | 0 | 182.6652 | 92.2291 | 71.0273 | 69.268 | 46.6831 | 22.5848 | 70.4405 | 68.6969 | 15.8318 | 38.3819 | TRUE | FALSE | TRUE | TRUE | 9.1859e-14 | 9.0066e-15 | 12.9266 | 79.39 | 31.0193 | 89.3881 | 95.024 | 48 |  | 61.3069 | 26.4 | 0 | 264 | 0 | 177.2082
Renewables + extra gas | central | 2048 | 691.034 | 9.068 | 89.5469 | 0 | 185.0206 | 94.0396 | 71.5722 | 69.8585 | 47.0265 | 22.832 | 70.9877 | 69.2885 | 15.9683 | 38.2911 | TRUE | FALSE | TRUE | TRUE | 9.8389e-14 | 9.57e-15 | 12.8965 | 84.12 | 32.5486 | 90.418 | 96.344 | 50 |  | 63.1469 | 26.4 | 0 | 264 | 0 | 178.9642
Renewables + extra gas | central | 2049 | 700.725 | 9.068 | 90.4689 | 0 | 187.9724 | 97.0292 | 72.1509 | 70.3222 | 47.2537 | 23.0685 | 71.5596 | 69.7463 | 15.9399 | 38.347 | TRUE | FALSE | TRUE | TRUE | 1.1326e-13 | 9.8106e-15 | 12.8094 | 88.97 | 34.1367 | 91.058 | 97.2708 | 51 |  | 63.1689 | 27.3 | 0 | 273 | 0 | 180.068
Renewables + extra gas | central | 2050 | 705.223 | 9.068 | 91.4659 | 0 | 188.7013 | 100.3193 | 72.2584 | 70.4102 | 47.2352 | 23.1751 | 71.6652 | 69.8312 | 15.9021 | 38.3996 | TRUE | FALSE | TRUE | TRUE | 1.1964e-13 | 1.0179e-14 | 12.7727 | 88.71 | 34.1774 | 91.3904 | 97.6253 | 55 |  | 63.2659 | 28.2 | 0 | 282 | 0 | 180.79
Renewables + extra gas | high | 2030 | 344.803 | 3.3089 | 34.4879 | 0 | 74.6673 | 55.5029 | 40.6603 | 40.6385 | 26.2425 | 14.396 | 40.5368 | 40.5162 | 16.6369 | 35.8007 | FALSE | FALSE | FALSE | FALSE | 3.0869 | 0.055915 | 24.7 | 3.58 | 1.735 | 84.8499 | 85.1372 | 0 |  | 34.4879 | 0 | 0 | 0 | 0 | 175.0343
Renewables + extra gas | high | 2031 | 362.869 | 3.7837 | 37.3079 | 0 | 83.9161 | 58.9029 | 42.6333 | 42.8676 | 27.9091 | 14.9585 | 42.3848 | 42.5943 | 14.8716 | 37.771 | FALSE | FALSE | FALSE | FALSE | 6.4649 | 0.036766 | 22.9171 | 5.07 | 2.4391 | 83.7971 | 83.8996 | 0 |  | 33.3079 | 4 | 0 | 40 | 0 | 172.7669
Renewables + extra gas | high | 2032 | 382.238 | 4.458 | 40.6889 | 0 | 92.6936 | 61.3029 | 44.7908 | 45.2832 | 29.7297 | 15.5535 | 44.46 | 44.9083 | 13.8628 | 39.027 | FALSE | FALSE | FALSE | FALSE | 1.6407 | 0.014926 | 21.1865 | 5.36 | 2.5759 | 82.0572 | 81.927 | 0 |  | 32.6889 | 8 | 0 | 80 | 0 | 169.2695
Renewables + extra gas | high | 2033 | 402.822 | 4.458 | 47.0089 | 0 | 103.3818 | 63.8029 | 47.6309 | 48.0141 | 31.6783 | 16.3358 | 47.2039 | 47.5641 | 13.1172 | 39.8952 | FALSE | FALSE | FALSE | FALSE | 0.66228 | 0.004398 | 20.2416 | 5.5 | 2.6482 | 82.9495 | 83.1424 | 4 |  | 35.4089 | 11.6 | 0 | 116 | 0 | 171.0216
Renewables + extra gas | high | 2034 | 425.413 | 4.458 | 54.2889 | 0 | 113.2065 | 66.5029 | 50.4011 | 50.6911 | 33.5573 | 17.1339 | 49.9159 | 50.1957 | 12.85 | 40.264 | FALSE | FALSE | TRUE | FALSE | 0.098103 | 3.7806e-15 | 19.4695 | 5.73 | 2.7628 | 84.3056 | 84.6186 | 8 |  | 39.0889 | 15.2 | 0 | 152 | 0 | 173.465
Renewables + extra gas | high | 2035 | 450.076 | 5.868 | 60.0789 | 0 | 122.7651 | 69.1029 | 53.1475 | 53.4858 | 35.6371 | 17.8486 | 52.6105 | 52.902 | 11.9157 | 41.349 | TRUE | FALSE | TRUE | FALSE | 0.02125 | 3.642e-15 | 17.46 | 7.36 | 3.5267 | 80.2694 | 80.7393 | 12 |  | 41.2789 | 18.8 | 0 | 188 | 0 | 164.998
Renewables + extra gas | high | 2036 | 483.247 | 5.868 | 65.2469 | 0 | 131.4397 | 74.2029 | 55.6995 | 55.8694 | 37.2112 | 18.6581 | 55.1465 | 55.2941 | 12.6095 | 40.7449 | TRUE | FALSE | TRUE | FALSE | 0.021826 | 4.617e-15 | 16.8871 | 11.06 | 5.2236 | 83.0379 | 83.8325 | 16 |  | 42.8469 | 22.4 | 0 | 224 | 0 | 169.9552
Renewables + extra gas | high | 2037 | 525.964 | 5.868 | 70.6419 | 0 | 141.8718 | 80.8029 | 58.7698 | 58.6998 | 39.1064 | 19.5934 | 58.2108 | 58.1439 | 13.5509 | 39.9715 | TRUE | FALSE | TRUE | FALSE | 0.020941 | 5.8001e-15 | 16.1664 | 26.12 | 11.7103 | 86.1351 | 88.1516 | 20 |  | 44.6419 | 26 | 0 | 260 | 0 | 175.3039
Renewables + extra gas | high | 2038 | 558.403 | 7.468 | 75.4719 | 0 | 151.3551 | 85.8029 | 61.92 | 61.7348 | 41.4242 | 20.3106 | 61.2991 | 61.1199 | 13.0213 | 40.5915 | TRUE | FALSE | TRUE | FALSE | 0.0048625 | 5.324e-15 | 14.573 | 32.62 | 14.3901 | 82.5455 | 85.0359 | 24 |  | 45.8719 | 29.6 | 0 | 296 | 0 | 167.6092
Renewables + extra gas | high | 2039 | 585.948 | 9.068 | 79.8299 | 0 | 158.1688 | 90.0029 | 64.6817 | 64.3347 | 43.4621 | 20.8726 | 64.022 | 63.679 | 12.6554 | 40.9083 | TRUE | FALSE | TRUE | TRUE | 1.6399e-14 | 5.4509e-15 | 13.2558 | 35.44 | 15.5682 | 78.8407 | 81.5557 | 28 |  | 47.8299 | 32 | 0 | 320 | 0 | 159.7148
Renewables + extra gas | high | 2040 | 616.965 | 9.068 | 84.5199 | 0 | 166.392 | 94.7256 | 66.8112 | 66.3407 | 44.9189 | 21.4218 | 66.1628 | 65.6974 | 13.3379 | 40.3335 | TRUE | FALSE | TRUE | TRUE | 3.784e-14 | 5.7869e-15 | 13.0951 | 42.69 | 18.4558 | 82.2302 | 85.5501 | 32 |  | 48.9199 | 35.6 | 0 | 356 | 0 | 165.8151
Renewables + extra gas | high | 2041 | 644.531 | 9.068 | 88.9799 | 0 | 174.2384 | 98.0142 | 69.1366 | 68.4005 | 46.2663 | 22.1342 | 68.4862 | 67.7623 | 13.7089 | 39.9998 | TRUE | FALSE | TRUE | TRUE | 5.452e-14 | 6.6497e-15 | 12.961 | 49.95 | 21.2642 | 84.8733 | 88.7934 | 36 |  | 52.1799 | 36.8 | 0 | 368 | 0 | 170.4832
Renewables + extra gas | high | 2042 | 672.19 | 9.068 | 92.4999 | 0 | 180.3569 | 101.5572 | 71.0942 | 70.0596 | 47.2939 | 22.7656 | 70.4566 | 69.4352 | 14.3287 | 39.4708 | TRUE | FALSE | TRUE | TRUE | 6.8404e-14 | 7.6008e-15 | 12.8813 | 58.89 | 24.5834 | 87.7804 | 92.397 | 40 |  | 54.9999 | 37.5 | 0 | 375 | 0 | 175.5637
Renewables + extra gas | high | 2043 | 694.708 | 9.068 | 96.1799 | 0 | 187.2581 | 103.7376 | 73.3041 | 71.9633 | 48.6178 | 23.3454 | 72.6703 | 71.3412 | 14.5729 | 39.3407 | TRUE | FALSE | TRUE | TRUE | 8.081e-14 | 8.2098e-15 | 12.739 | 64.35 | 26.6015 | 89.6568 | 94.5806 | 44 |  | 58.6799 | 37.5 | 0 | 375 | 0 | 178.8526
Renewables + extra gas | high | 2044 | 709.671 | 9.068 | 98.9099 | 0 | 190.8496 | 103.4004 | 74.309 | 72.6754 | 49.1268 | 23.5486 | 73.6838 | 72.0666 | 15.1581 | 38.8642 | TRUE | FALSE | TRUE | TRUE | 9.5191e-14 | 1.1315e-14 | 12.8868 | 64.05 | 26.5429 | 92.9432 | 97.9036 | 48 |  | 61.4099 | 37.5 | 0 | 375 | 0 | 184.7534
Renewables + extra gas | high | 2045 | 724.44 | 9.068 | 102.4869 | 0 | 195.0921 | 101.4444 | 75.5338 | 73.9756 | 50.0016 | 23.974 | 74.9237 | 73.3758 | 15.5238 | 38.6186 | TRUE | TRUE | TRUE | TRUE | 1.0381e-13 | 1.0772e-14 | 12.9016 | 65.36 | 27.0178 | 94.9113 | 99.848 | 52 |  | 64.9869 | 37.5 | 0 | 375 | 0 | 188.2171
Renewables + extra gas | high | 2046 | 737.93 | 9.068 | 106.1669 | 0 | 198.1154 | 101.5779 | 76.4133 | 74.9064 | 50.5549 | 24.3515 | 75.8092 | 74.3162 | 15.8601 | 38.2633 | TRUE | TRUE | TRUE | TRUE | 1.1025e-13 | 1.1493e-14 | 12.9902 | 67.55 | 27.8104 | 97.2281 | 102.3431 | 56 |  | 68.6669 | 37.5 | 0 | 375 | 0 | 192.284
Renewables + extra gas | high | 2047 | 752.313 | 9.068 | 109.8469 | 0 | 202.6652 | 103.2291 | 77.5852 | 76.1181 | 51.3386 | 24.7794 | 76.9775 | 75.5258 | 15.9315 | 38.213 | TRUE | TRUE | TRUE | TRUE | 1.0576e-13 | 1.1344e-14 | 12.9302 | 72.86 | 29.699 | 98.6256 | 104.0823 | 60 |  | 72.3469 | 37.5 | 0 | 375 | 0 | 194.6866
Renewables + extra gas | high | 2048 | 766.439 | 9.068 | 110.7669 | 0 | 206.3206 | 105.6396 | 78.5937 | 76.9477 | 51.8381 | 25.1097 | 77.9869 | 76.3555 | 16.0952 | 38.1048 | TRUE | TRUE | TRUE | TRUE | 1.155e-13 | 1.2822e-14 | 12.8811 | 79.13 | 31.8707 | 100.0389 | 105.9396 | 61 |  | 73.2669 | 37.5 | 0 | 375 | 0 | 197.0979
Renewables + extra gas | high | 2049 | 776.227 | 9.068 | 111.7089 | 0 | 209.2724 | 108.6292 | 79.1787 | 77.4475 | 52.0823 | 25.3652 | 78.5667 | 76.8509 | 16.0676 | 38.1337 | TRUE | TRUE | TRUE | TRUE | 1.1567e-13 | 1.2985e-14 | 12.8297 | 81.23 | 32.6642 | 100.9042 | 106.9756 | 63 |  | 74.2089 | 37.5 | 0 | 375 | 0 | 198.7075
Renewables + extra gas | high | 2050 | 784.736 | 9.068 | 111.8059 | 0 | 210.4013 | 112.6193 | 79.4891 | 77.6076 | 52.0846 | 25.5229 | 78.8793 | 77.0135 | 16.1638 | 38.0642 | TRUE | FALSE | TRUE | TRUE | 1.2695e-13 | 1.658e-14 | 12.8309 | 81.91 | 32.9866 | 101.9928 | 108.1558 | 67 |  | 74.3059 | 37.5 | 0 | 375 | 0 | 200.7861
95% clean constraint | low | 2030 | 323.698 | 3.3089 | 34.4879 | 0 | 74.6673 | 55.5029 |  | 35.5057 | 26.2425 | 9.2631 |  | 36.0714 | 15.9949 | 31.7775 | FALSE | FALSE | FALSE | FALSE | 27.4496 | 9.3803 | 4.9998 | 0.53 | 0.26353 | 15.4878 | 15.485 | 0 |  | 34.4879 | 0 | 0 | 0 | 0 | 31.3099
95% clean constraint | low | 2031 | 332.351 | 3.7837 | 33.3079 | 0 | 81.4161 | 55.5029 |  | 37.134 | 27.3426 | 9.7914 |  | 37.5249 | 14.2004 | 34.1464 | FALSE | FALSE | FALSE | FALSE | 31.5294 | 9.0051 | 4.9999 | 0.54 | 0.26839 | 16.1587 | 16.1559 | 0 |  | 33.3079 | 0 | 0 | 0 | 0 | 32.7307
95% clean constraint | low | 2032 | 341.738 | 4.458 | 32.6889 | 0 | 89.2936 | 55.5029 |  | 39.1916 | 28.7666 | 10.4251 |  | 39.4263 | 12.6373 | 36.3224 | FALSE | FALSE | FALSE | FALSE | 25.4776 | 7.758 | 4.9995 | 0.57 | 0.28354 | 16.8729 | 16.8693 | 0 |  | 32.6889 | 0 | 0 | 0 | 0 | 34.3104
95% clean constraint | low | 2033 | 351.742 | 4.458 | 31.7289 | 0 | 90.0818 | 55.7029 |  | 39.0642 | 28.6469 | 10.4173 |  | 39.3883 | 13.6145 | 35.3464 | FALSE | FALSE | FALSE | FALSE | 27.5978 | 8.968 | 4.9998 | 0.89 | 0.44128 | 17.2329 | 17.2279 | 0 |  | 31.7289 | 0 | 0 | 0 | 0 | 34.8779
95% clean constraint | low | 2034 | 362.296 | 4.458 | 31.7289 | 0 | 96.9065 | 56.7029 |  | 40.5533 | 29.6937 | 10.8596 |  | 40.8133 | 13.0431 | 36.3689 | FALSE | FALSE | FALSE | FALSE | 28.1721 | 8.9235 | 4.9999 | 1.52 | 0.75048 | 17.8415 | 17.8331 | 0 |  | 31.7289 | 0 | 0 | 0 | 0 | 36.1116
95% clean constraint | low | 2035 | 372.906 | 5.868 | 30.2389 | 0 | 101.3651 | 57.3029 |  | 41.8877 | 30.4425 | 11.4452 |  | 42.0394 | 11.958 | 37.8051 | FALSE | FALSE | FALSE | FALSE | 26.8352 | 7.8804 | 4.9984 | 2.34 | 1.1487 | 18.5421 | 18.5324 | 0 |  | 30.2389 | 0 | 0 | 0 | 0 | 37.6243
95% clean constraint | low | 2036 | 384.269 | 5.868 | 29.0469 | 0 | 104.1397 | 59.0029 |  | 42.3168 | 30.7002 | 11.6166 |  | 42.5055 | 12.4003 | 37.4663 | FALSE | FALSE | FALSE | FALSE | 28.4784 | 8.5978 | 4.9993 | 3.1 | 1.5144 | 19.0418 | 19.0275 | 1 |  | 29.0469 | 0 | 0 | 0 | 0 | 38.5606
95% clean constraint | low | 2037 | 396.144 | 5.868 | 29.0019 | 0 | 107.0718 | 60.8029 |  | 42.8066 | 30.9942 | 11.8124 |  | 43.0305 | 12.8381 | 37.1582 | FALSE | FALSE | FALSE | FALSE | 30.0738 | 9.3 | 4.9982 | 4.55 | 2.2035 | 19.5612 | 19.5367 | 3 |  | 29.0019 | 0 | 0 | 0 | 0 | 39.5124
95% clean constraint | low | 2038 | 407.229 | 7.468 | 28.3919 | 0 | 110.7551 | 62.6029 |  | 44.4482 | 32.0646 | 12.3836 |  | 44.5752 | 11.8569 | 38.393 | FALSE | FALSE | FALSE | FALSE | 28.4059 | 8.0633 | 4.998 | 5.01 | 2.4212 | 20.2866 | 20.2617 | 5 |  | 28.3919 | 0 | 0 | 0 | 0 | 41.069
95% clean constraint | low | 2039 | 419.392 | 9.068 | 28.5099 | 0 | 113.2688 | 64.4029 |  | 45.9565 | 33.0612 | 12.8953 |  | 46.0222 | 11.2328 | 39.1675 | FALSE | FALSE | FALSE | FALSE | 27.1705 | 7.14 | 4.9968 | 6.03 | 2.8994 | 21.0057 | 20.9816 | 7 |  | 28.5099 | 0 | 0 | 0 | 0 | 42.5371
95% clean constraint | low | 2040 | 433.613 | 9.068 | 27.7599 | 0 | 117.092 | 66.5256 |  | 46.3784 | 33.4888 | 12.8896 |  | 46.5076 | 11.9428 | 38.5205 | FALSE | FALSE | FALSE | FALSE | 29.6641 | 8.3116 | 4.9985 | 6.94 | 3.3239 | 21.7671 | 21.7292 | 9 |  | 27.7599 | 0 | 0 | 0 | 0 | 43.9334
95% clean constraint | low | 2041 | 450.011 | 9.068 | 28.2599 | 0 | 122.0384 | 68.2142 |  | 47.3962 | 34.1676 | 13.2286 |  | 47.5559 | 12.3117 | 38.2742 | FALSE | FALSE | FALSE | FALSE | 31.8558 | 9.2777 | 4.9976 | 8.15 | 3.8859 | 22.5069 | 22.4716 | 10 |  | 28.2599 | 0 | 0 | 0 | 0 | 45.2573
95% clean constraint | low | 2042 | 464.557 | 9.068 | 28.3199 | 0 | 125.0569 | 69.6572 |  | 47.8817 | 34.4371 | 13.4446 |  | 48.0944 | 12.877 | 37.6901 | FALSE | FALSE | FALSE | FALSE | 34.1546 | 10.4125 | 4.9975 | 8.63 | 4.1107 | 23.1259 | 23.0896 | 11 |  | 28.3199 | 0 | 0 | 0 | 0 | 46.3408
95% clean constraint | low | 2043 | 477.519 | 9.068 | 28.3199 | 0 | 129.1581 | 70.4376 |  | 48.8154 | 35.1029 | 13.7125 |  | 49.0552 | 13.1732 | 37.3808 | FALSE | FALSE | FALSE | FALSE | 35.5453 | 10.8621 | 4.9978 | 8.76 | 4.1749 | 23.7348 | 23.6941 | 11 |  | 28.3199 | 0 | 0 | 0 | 0 | 47.5196
95% clean constraint | low | 2044 | 490.691 | 9.068 | 28.2899 | 0 | 131.6496 | 69.8004 |  | 48.865 | 35.2681 | 13.5969 |  | 49.1951 | 14.1527 | 36.3986 | FALSE | FALSE | FALSE | FALSE | 38.9936 | 12.6614 | 4.9974 | 9.59 | 4.5528 | 24.3816 | 24.3441 | 12 |  | 28.2899 | 0 | 0 | 0 | 0 | 48.5221
95% clean constraint | low | 2045 | 504.316 | 9.068 | 28.1869 | 0 | 135.7921 | 67.6444 |  | 49.6785 | 35.8368 | 13.8417 |  | 50.0601 | 14.7192 | 35.8305 | FALSE | FALSE | FALSE | FALSE | 40.9269 | 13.4829 | 4.9978 | 10.36 | 4.9006 | 24.9801 | 24.9395 | 12 |  | 28.1869 | 0 | 0 | 0 | 0 | 49.6066
95% clean constraint | low | 2046 | 516.137 | 9.068 | 28.1869 | 0 | 138.6154 | 67.5779 |  | 50.1651 | 36.1515 | 14.0137 |  | 50.5876 | 15.2049 | 35.4607 | FALSE | FALSE | FALSE | FALSE | 43.2724 | 14.7218 | 4.9983 | 11.34 | 5.3458 | 25.4706 | 25.4263 | 12 |  | 28.1869 | 0 | 0 | 0 | 0 | 50.4123
95% clean constraint | low | 2047 | 526.834 | 9.068 | 28.1869 | 0 | 141.8652 | 68.6291 |  | 50.7488 | 36.5106 | 14.2381 |  | 51.1869 | 15.4134 | 35.3624 | FALSE | FALSE | FALSE | FALSE | 44.8816 | 15.4478 | 4.9979 | 12.32 | 5.7902 | 25.9545 | 25.9097 | 12 |  | 28.1869 | 0 | 0 | 0 | 0 | 51.2893
95% clean constraint | low | 2048 | 537.853 | 9.068 | 28.1869 | 0 | 144.3206 | 70.5396 |  | 51.174 | 36.7585 | 14.4156 |  | 51.637 | 15.7266 | 35.1204 | FALSE | FALSE | FALSE | FALSE | 46.6738 | 16.3098 | 4.9976 | 13.57 | 6.3517 | 26.4363 | 26.3869 | 12 |  | 28.1869 | 0 | 0 | 0 | 0 | 52.143
95% clean constraint | low | 2049 | 548.276 | 9.068 | 28.2089 | 0 | 147.3724 | 73.7292 |  | 51.596 | 36.9642 | 14.6318 |  | 52.0602 | 15.7946 | 35.1923 | FALSE | FALSE | FALSE | FALSE | 47.968 | 16.8124 | 4.9983 | 14.55 | 6.7925 | 26.9372 | 26.8789 | 13 |  | 28.2089 | 0 | 0 | 0 | 0 | 53.0734
95% clean constraint | low | 2050 | 558.75 | 9.068 | 28.3059 | 0 | 149.6013 | 77.9193 |  | 51.9574 | 37.1459 | 14.8115 |  | 52.4316 | 15.9315 | 35.1004 | FALSE | FALSE | FALSE | FALSE | 49.3115 | 17.3655 | 4.9984 | 15.21 | 7.0932 | 27.4254 | 27.3638 | 17 |  | 28.3059 | 0 | 0 | 0 | 0 | 53.9823
95% clean constraint | central | 2030 | 339.295 | 3.3089 | 34.4879 | 0 | 74.6673 | 55.5029 |  | 35.5324 | 26.2425 | 9.2899 |  | 36.2943 | 18.3432 | 29.7473 | FALSE | FALSE | FALSE | FALSE | 30.7001 | 11.2011 | 4.9998 | 3.83 | 1.8525 | 15.9582 | 15.936 | 0 |  | 34.4879 | 0 | 0 | 0 | 0 | 31.9723
95% clean constraint | central | 2031 | 355.884 | 3.7837 | 33.3079 | 0 | 83.3161 | 57.7029 |  | 37.4829 | 27.5784 | 9.9046 |  | 38.0787 | 16.6936 | 32.1302 | FALSE | FALSE | FALSE | FALSE | 30.5749 | 10.9307 | 4.9999 | 5.46 | 2.617 | 17.0156 | 16.9848 | 0 |  | 33.3079 | 0 | 0 | 0 | 0 | 34.14
95% clean constraint | central | 2032 | 373.666 | 4.458 | 32.6889 | 0 | 91.8936 | 59.9029 |  | 39.8172 | 29.2121 | 10.6051 |  | 40.2975 | 15.5932 | 33.8439 | FALSE | FALSE | FALSE | FALSE | 30.3939 | 10.1021 | 4.9999 | 6.29 | 3.0062 | 18.0879 | 18.0538 | 0 |  | 32.6889 | 0 | 0 | 0 | 0 | 36.3627
95% clean constraint | central | 2033 | 392.593 | 4.458 | 32.6489 | 0 | 100.4818 | 62.1029 |  | 41.6499 | 30.506 | 11.144 |  | 42.0909 | 15.3284 | 34.6347 | FALSE | FALSE | FALSE | FALSE | 32.203 | 10.6421 | 4.9999 | 7.55 | 3.59 | 19.0758 | 19.0369 | 1 |  | 32.6489 | 0 | 0 | 0 | 0 | 38.2859
95% clean constraint | central | 2034 | 411.573 | 4.458 | 32.6489 | 0 | 109.0065 | 64.3029 |  | 43.514 | 31.8168 | 11.6971 |  | 43.9216 | 15.1148 | 35.3275 | FALSE | FALSE | FALSE | FALSE | 34.1931 | 11.328 | 4.999 | 8.28 | 3.9307 | 20.0323 | 19.9922 | 1 |  | 32.6489 | 0 | 0 | 0 | 0 | 40.1299
95% clean constraint | central | 2035 | 433.422 | 5.868 | 32.9989 | 0 | 117.3651 | 66.5029 |  | 45.9579 | 33.3718 | 12.5861 |  | 46.267 | 14.1801 | 36.7136 | FALSE | FALSE | FALSE | FALSE | 33.5659 | 10.268 | 4.9981 | 11.97 | 5.5933 | 21.2892 | 21.2364 | 3 |  | 32.9989 | 0 | 0 | 0 | 0 | 42.6841
95% clean constraint | central | 2036 | 461.449 | 5.868 | 32.7269 | 0 | 124.5397 | 70.8029 |  | 47.5331 | 34.4581 | 13.075 |  | 47.8969 | 14.8876 | 36.2743 | FALSE | FALSE | FALSE | FALSE | 37.5013 | 12.0285 | 4.9985 | 16.63 | 7.6418 | 22.552 | 22.4791 | 5 |  | 32.7269 | 0 | 0 | 0 | 0 | 44.9914
95% clean constraint | central | 2037 | 488.675 | 5.868 | 32.6819 | 0 | 131.6718 | 75.0029 |  | 49.0654 | 35.5033 | 13.5621 |  | 49.4733 | 15.4578 | 35.9222 | FALSE | FALSE | FALSE | FALSE | 41.3265 | 13.7538 | 4.9982 | 21.98 | 9.9265 | 23.7838 | 23.6944 | 7 |  | 32.6819 | 0 | 0 | 0 | 0 | 47.229
95% clean constraint | central | 2038 | 513.806 | 7.468 | 32.9919 | 0 | 138.5551 | 78.9029 |  | 51.5748 | 37.2044 | 14.3704 |  | 51.9229 | 14.8719 | 36.7482 | FALSE | FALSE | FALSE | FALSE | 41.0127 | 12.8073 | 4.9989 | 27.6 | 12.261 | 25.1635 | 25.0505 | 10 |  | 32.9919 | 0 | 0 | 0 | 0 | 49.9158
95% clean constraint | central | 2039 | 536.367 | 9.068 | 34.0299 | 0 | 143.9688 | 82.3029 |  | 53.8882 | 38.7895 | 15.0986 |  | 54.1942 | 14.4249 | 37.2866 | FALSE | FALSE | FALSE | FALSE | 40.5227 | 11.8848 | 4.9986 | 31.3 | 13.7796 | 26.3883 | 26.2635 | 13 |  | 34.0299 | 0 | 0 | 0 | 0 | 52.2317
95% clean constraint | central | 2040 | 563.928 | 9.068 | 33.2799 | 0 | 151.892 | 86.5256 |  | 55.3243 | 39.9497 | 15.3746 |  | 55.6802 | 15.0699 | 36.8696 | FALSE | FALSE | FALSE | FALSE | 44.7763 | 13.6995 | 4.9987 | 40.34 | 17.3287 | 27.7921 | 27.64 | 15 |  | 33.2799 | 0 | 0 | 0 | 0 | 54.7755
95% clean constraint | central | 2041 | 582.761 | 9.068 | 35.6199 | 0 | 157.0384 | 88.5142 |  | 56.5211 | 40.763 | 15.758 |  | 56.9077 | 15.4453 | 36.6058 | FALSE | FALSE | FALSE | FALSE | 47.4631 | 14.9196 | 4.9993 | 42.98 | 18.3751 | 28.6464 | 28.4816 | 18 |  | 35.6199 | 0 | 0 | 0 | 0 | 56.1874
95% clean constraint | central | 2042 | 602.352 | 9.068 | 35.6799 | 0 | 161.4569 | 90.7572 |  | 57.3236 | 41.2575 | 16.0661 |  | 57.7544 | 15.965 | 36.1782 | FALSE | FALSE | FALSE | FALSE | 50.6628 | 16.4061 | 4.9989 | 47.77 | 20.1923 | 29.5066 | 29.3287 | 19 |  | 35.6799 | 0 | 0 | 0 | 0 | 57.6703
95% clean constraint | central | 2043 | 621.073 | 9.068 | 35.6799 | 0 | 167.0581 | 92.4376 |  | 58.5915 | 42.1602 | 16.4313 |  | 59.0449 | 16.245 | 35.9431 | FALSE | FALSE | FALSE | FALSE | 52.8568 | 17.1366 | 4.999 | 53.71 | 22.3884 | 30.3913 | 30.206 | 19 |  | 35.6799 | 0 | 0 | 0 | 0 | 59.3047
95% clean constraint | central | 2044 | 635.458 | 9.068 | 35.6499 | 0 | 170.6496 | 92.0004 |  | 58.8921 | 42.5047 | 16.3874 |  | 59.4049 | 16.934 | 35.3483 | FALSE | FALSE | FALSE | FALSE | 56.8596 | 19.2545 | 4.9989 | 56.64 | 23.4435 | 31.1156 | 30.9204 | 20 |  | 35.6499 | 0 | 0 | 0 | 0 | 60.4544
95% clean constraint | central | 2045 | 654.296 | 9.068 | 35.5469 | 0 | 175.1921 | 90.6444 |  | 59.8802 | 43.2105 | 16.6697 |  | 60.4478 | 17.5931 | 34.7709 | FALSE | FALSE | FALSE | FALSE | 60.05 | 20.6377 | 4.9988 | 65.79 | 26.5518 | 31.9385 | 31.726 | 20 |  | 35.5469 | 0 | 0 | 0 | 0 | 61.9178
95% clean constraint | central | 2046 | 670.284 | 9.068 | 35.5469 | 0 | 179.4154 | 91.1779 |  | 60.6745 | 43.7435 | 16.931 |  | 61.2669 | 17.9388 | 34.6122 | FALSE | FALSE | FALSE | FALSE | 62.9983 | 22.1085 | 4.9992 | 74.25 | 29.3391 | 32.6404 | 32.3962 | 20 |  | 35.5469 | 0 | 0 | 0 | 0 | 63.1083
95% clean constraint | central | 2047 | 681.236 | 9.068 | 35.5469 | 0 | 182.6652 | 92.2291 |  | 61.2593 | 44.1026 | 17.1566 |  | 61.8586 | 18.0587 | 34.583 | FALSE | FALSE | FALSE | FALSE | 64.673 | 22.8719 | 4.9989 | 79.39 | 31.0193 | 33.1414 | 32.8854 | 20 |  | 35.5469 | 0 | 0 | 0 | 0 | 63.9969
95% clean constraint | central | 2048 | 691.034 | 9.068 | 35.5469 | 0 | 185.0206 | 94.0396 |  | 61.666 | 44.3386 | 17.3274 |  | 62.2756 | 18.198 | 34.5069 | FALSE | FALSE | FALSE | FALSE | 66.2623 | 23.6091 | 4.999 | 84.12 | 32.5486 | 33.5865 | 33.3221 | 20 |  | 35.5469 | 0 | 0 | 0 | 0 | 64.7833
95% clean constraint | central | 2049 | 700.725 | 9.068 | 35.5689 | 0 | 187.9724 | 97.0292 |  | 62.0669 | 44.5291 | 17.5378 |  | 62.6701 | 18.1613 | 34.6326 | FALSE | FALSE | FALSE | FALSE | 67.3205 | 23.9496 | 4.999 | 88.97 | 34.1367 | 34.0614 | 33.786 | 21 |  | 35.5689 | 0 | 0 | 0 | 0 | 65.6527
95% clean constraint | central | 2050 | 705.223 | 9.068 | 35.6659 | 0 | 188.7013 | 100.3193 |  | 62.0928 | 44.4739 | 17.6189 |  | 62.6946 | 18.1324 | 34.6253 | FALSE | FALSE | FALSE | FALSE | 67.8425 | 24.0805 | 4.999 | 88.71 | 34.1774 | 34.2839 | 34.0062 | 25 |  | 35.6659 | 0 | 0 | 0 | 0 | 66.0775
95% clean constraint | high | 2030 | 344.803 | 3.3089 | 34.4879 | 0 | 74.6673 | 55.5029 |  | 35.5409 | 26.2425 | 9.2984 |  | 36.3561 | 18.9001 | 29.0462 | FALSE | FALSE | FALSE | FALSE | 32.6699 | 12.4843 | 4.9998 | 3.58 | 1.735 | 16.1089 | 16.088 | 0 |  | 34.4879 | 0 | 0 | 0 | 0 | 32.1624
95% clean constraint | high | 2031 | 362.869 | 3.7837 | 33.3079 | 0 | 83.9161 | 58.9029 |  | 37.7003 | 27.746 | 9.9543 |  | 38.3342 | 17.0776 | 31.5854 | FALSE | FALSE | FALSE | FALSE | 37.172 | 12.0607 | 4.9999 | 5.07 | 2.4391 | 17.267 | 17.2377 | 0 |  | 33.3079 | 0 | 0 | 0 | 0 | 34.5527
95% clean constraint | high | 2032 | 382.238 | 4.458 | 32.6889 | 0 | 92.6936 | 61.3029 |  | 40.0682 | 29.4034 | 10.6648 |  | 40.5945 | 16.0459 | 33.2511 | FALSE | FALSE | FALSE | FALSE | 32.56 | 11.3936 | 4.9999 | 5.36 | 2.5759 | 18.4053 | 18.376 | 0 |  | 32.6889 | 0 | 0 | 0 | 0 | 36.8819
95% clean constraint | high | 2033 | 402.822 | 4.458 | 34.4889 | 0 | 103.3818 | 63.8029 |  | 42.5297 | 31.1514 | 11.3783 |  | 42.9766 | 15.33 | 34.5355 | FALSE | FALSE | FALSE | FALSE | 34.0233 | 11.676 | 5 | 5.5 | 2.6482 | 19.5364 | 19.5089 | 3 |  | 34.4889 | 0 | 0 | 0 | 0 | 39.1027
95% clean constraint | high | 2034 | 425.413 | 4.458 | 34.4889 | 0 | 113.2065 | 66.5029 |  | 44.685 | 32.6687 | 12.0163 |  | 45.0971 | 15.0996 | 35.2706 | FALSE | FALSE | FALSE | FALSE | 36.5311 | 12.6194 | 4.9988 | 5.73 | 2.7628 | 20.6629 | 20.6376 | 3 |  | 34.4889 | 0 | 0 | 0 | 0 | 41.2584
95% clean constraint | high | 2035 | 450.076 | 5.868 | 34.8389 | 0 | 122.7651 | 69.1029 |  | 47.4902 | 34.4943 | 12.9958 |  | 47.8045 | 14.1319 | 36.5899 | FALSE | FALSE | FALSE | FALSE | 36.1514 | 11.6507 | 4.9971 | 7.36 | 3.5267 | 22.054 | 22.0246 | 5 |  | 34.8389 | 0 | 0 | 0 | 0 | 44.0648
95% clean constraint | high | 2036 | 483.247 | 5.868 | 34.5669 | 0 | 131.4397 | 74.2029 |  | 49.3942 | 35.8142 | 13.58 |  | 49.7667 | 14.8654 | 36.1268 | FALSE | FALSE | FALSE | FALSE | 40.9996 | 13.8886 | 4.9981 | 11.06 | 5.2236 | 23.5517 | 23.5069 | 7 |  | 34.5669 | 0 | 0 | 0 | 0 | 46.7728
95% clean constraint | high | 2037 | 525.964 | 5.868 | 35.4419 | 0 | 141.8718 | 80.8029 |  | 51.8221 | 37.5088 | 14.3134 |  | 52.2622 | 15.8041 | 35.6357 | FALSE | FALSE | FALSE | FALSE | 46.8303 | 16.3444 | 4.9971 | 26.12 | 11.7103 | 25.4917 | 25.3894 | 10 |  | 35.4419 | 0 | 0 | 0 | 0 | 50.2882
95% clean constraint | high | 2038 | 558.403 | 7.468 | 36.6719 | 0 | 151.3551 | 85.8029 |  | 54.9886 | 39.6798 | 15.3088 |  | 55.37 | 15.2388 | 36.4757 | FALSE | FALSE | FALSE | FALSE | 47.2386 | 15.5619 | 4.9986 | 32.62 | 14.3901 | 27.233 | 27.1016 | 14 |  | 36.6719 | 0 | 0 | 0 | 0 | 53.5774
95% clean constraint | high | 2039 | 585.948 | 9.068 | 36.7899 | 0 | 158.1688 | 90.0029 |  | 57.6355 | 41.5123 | 16.1232 |  | 57.9837 | 14.8711 | 36.8974 | FALSE | FALSE | FALSE | FALSE | 47.4895 | 14.8822 | 4.9987 | 35.44 | 15.5682 | 28.6904 | 28.5489 | 16 |  | 36.7899 | 0 | 0 | 0 | 0 | 56.2945
95% clean constraint | high | 2040 | 616.965 | 9.068 | 36.0399 | 0 | 166.392 | 94.7256 |  | 59.1316 | 42.7149 | 16.4167 |  | 59.5381 | 15.5865 | 36.3831 | FALSE | FALSE | FALSE | FALSE | 52.8456 | 17.4502 | 4.999 | 42.69 | 18.4558 | 30.2238 | 30.0633 | 18 |  | 36.0399 | 0 | 0 | 0 | 0 | 59.0236
95% clean constraint | high | 2041 | 644.531 | 9.068 | 37.4599 | 0 | 174.2384 | 98.0142 |  | 60.8684 | 43.9059 | 16.9624 |  | 61.3037 | 15.9766 | 36.196 | FALSE | FALSE | FALSE | FALSE | 56.8459 | 19.2006 | 4.999 | 49.95 | 21.2642 | 31.4869 | 31.2998 | 20 |  | 37.4599 | 0 | 0 | 0 | 0 | 61.2066
95% clean constraint | high | 2042 | 672.19 | 9.068 | 37.5199 | 0 | 180.3569 | 101.5572 |  | 62.1372 | 44.7439 | 17.3932 |  | 62.6248 | 16.6183 | 35.6927 | FALSE | FALSE | FALSE | FALSE | 61.3845 | 21.2837 | 4.9988 | 58.89 | 24.5834 | 32.7135 | 32.4985 | 21 |  | 37.5199 | 0 | 0 | 0 | 0 | 63.3367
95% clean constraint | high | 2043 | 694.708 | 9.068 | 37.5199 | 0 | 187.2581 | 103.7376 |  | 63.6961 | 45.853 | 17.8431 |  | 64.2034 | 16.8718 | 35.5136 | FALSE | FALSE | FALSE | FALSE | 64.3101 | 22.3498 | 4.9982 | 64.35 | 26.6015 | 33.7715 | 33.556 | 21 |  | 37.5199 | 0 | 0 | 0 | 0 | 65.278
95% clean constraint | high | 2044 | 709.671 | 9.068 | 38.4099 | 0 | 190.8496 | 103.4004 |  | 64.0702 | 46.2546 | 17.8156 |  | 64.6343 | 17.509 | 34.9337 | FALSE | FALSE | FALSE | FALSE | 68.779 | 24.8413 | 4.9986 | 64.05 | 26.5429 | 34.514 | 34.2932 | 23 |  | 38.4099 | 0 | 0 | 0 | 0 | 66.3933
95% clean constraint | high | 2045 | 724.44 | 9.068 | 40.1469 | 0 | 195.0921 | 101.4444 |  | 65.1305 | 47.0221 | 18.1085 |  | 65.7318 | 17.9074 | 34.4716 | FALSE | FALSE | FALSE | FALSE | 71.271 | 25.9219 | 4.9983 | 65.36 | 27.0178 | 35.1685 | 34.9545 | 25 |  | 40.1469 | 0 | 0 | 0 | 0 | 67.4742
95% clean constraint | high | 2046 | 737.93 | 9.068 | 40.1469 | 0 | 198.1154 | 101.5779 |  | 65.6502 | 47.3605 | 18.2897 |  | 66.2812 | 18.2663 | 34.1808 | FALSE | FALSE | FALSE | FALSE | 74.4653 | 27.789 | 4.9985 | 67.55 | 27.8104 | 35.7195 | 35.5001 | 25 |  | 40.1469 | 0 | 0 | 0 | 0 | 68.3538
95% clean constraint | high | 2047 | 752.313 | 9.068 | 40.1469 | 0 | 202.6652 | 103.2291 |  | 66.5292 | 47.9295 | 18.5998 |  | 67.1638 | 18.3365 | 34.2067 | FALSE | FALSE | FALSE | FALSE | 76.5451 | 28.7265 | 4.998 | 72.86 | 29.699 | 36.3877 | 36.1581 | 25 |  | 40.1469 | 0 | 0 | 0 | 0 | 69.5516
95% clean constraint | high | 2048 | 766.439 | 9.068 | 40.1469 | 0 | 206.3206 | 105.6396 |  | 67.2336 | 48.3752 | 18.8584 |  | 67.8776 | 18.4892 | 34.154 | FALSE | FALSE | FALSE | FALSE | 78.7792 | 29.7358 | 4.9985 | 79.13 | 31.8707 | 37.0385 | 36.7928 | 25 |  | 40.1469 | 0 | 0 | 0 | 0 | 70.7078
95% clean constraint | high | 2049 | 776.227 | 9.068 | 40.1689 | 0 | 209.2724 | 108.6292 |  | 67.6347 | 48.5657 | 19.069 |  | 68.274 | 18.4597 | 34.2341 | FALSE | FALSE | FALSE | FALSE | 80.0217 | 30.2873 | 4.9982 | 81.23 | 32.6642 | 37.5038 | 37.2548 | 26 |  | 40.1689 | 0 | 0 | 0 | 0 | 71.5613
95% clean constraint | high | 2050 | 784.736 | 9.068 | 40.2659 | 0 | 210.4013 | 112.6193 |  | 67.7413 | 48.5681 | 19.1732 |  | 68.3914 | 18.5679 | 34.1126 | FALSE | FALSE | FALSE | FALSE | 81.543 | 31.0333 | 4.9989 | 81.91 | 32.9866 | 37.8889 | 37.6243 | 30 |  | 40.2659 | 0 | 0 | 0 | 0 | 72.2455

## Demand pathways
Annual electricity demand inputs
Three complete NESO FES 2025 pathways. Source fiscal-year totals are assigned to same-numbered model years. No probability is assigned to a pathway; 2029 is retained for schedule construction.
Pathway | Year | Annual TWh | Source
Falling Behind | 2029 | 316.344 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Falling Behind | 2030 | 323.698 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Falling Behind | 2031 | 332.351 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Falling Behind | 2032 | 341.738 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Falling Behind | 2033 | 351.742 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Falling Behind | 2034 | 362.296 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Falling Behind | 2035 | 372.906 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Falling Behind | 2036 | 384.269 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Falling Behind | 2037 | 396.144 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Falling Behind | 2038 | 407.229 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Falling Behind | 2039 | 419.392 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Falling Behind | 2040 | 433.613 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Falling Behind | 2041 | 450.011 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Falling Behind | 2042 | 464.557 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Falling Behind | 2043 | 477.519 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Falling Behind | 2044 | 490.691 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Falling Behind | 2045 | 504.316 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Falling Behind | 2046 | 516.137 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Falling Behind | 2047 | 526.834 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Falling Behind | 2048 | 537.853 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Falling Behind | 2049 | 548.276 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Falling Behind | 2050 | 558.75 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Holistic Transition | 2029 | 326.293 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Holistic Transition | 2030 | 339.295 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Holistic Transition | 2031 | 355.884 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Holistic Transition | 2032 | 373.666 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Holistic Transition | 2033 | 392.593 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Holistic Transition | 2034 | 411.573 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Holistic Transition | 2035 | 433.422 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Holistic Transition | 2036 | 461.449 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Holistic Transition | 2037 | 488.675 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Holistic Transition | 2038 | 513.806 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Holistic Transition | 2039 | 536.367 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Holistic Transition | 2040 | 563.928 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Holistic Transition | 2041 | 582.761 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Holistic Transition | 2042 | 602.352 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Holistic Transition | 2043 | 621.073 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Holistic Transition | 2044 | 635.458 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Holistic Transition | 2045 | 654.296 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Holistic Transition | 2046 | 670.284 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Holistic Transition | 2047 | 681.236 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Holistic Transition | 2048 | 691.034 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Holistic Transition | 2049 | 700.725 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Holistic Transition | 2050 | 705.223 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Electric Engagement | 2029 | 328.975 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Electric Engagement | 2030 | 344.803 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Electric Engagement | 2031 | 362.869 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Electric Engagement | 2032 | 382.238 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Electric Engagement | 2033 | 402.822 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Electric Engagement | 2034 | 425.413 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Electric Engagement | 2035 | 450.076 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Electric Engagement | 2036 | 483.247 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Electric Engagement | 2037 | 525.964 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Electric Engagement | 2038 | 558.403 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Electric Engagement | 2039 | 585.948 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Electric Engagement | 2040 | 616.965 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Electric Engagement | 2041 | 644.531 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Electric Engagement | 2042 | 672.19 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Electric Engagement | 2043 | 694.708 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Electric Engagement | 2044 | 709.671 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Electric Engagement | 2045 | 724.44 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Electric Engagement | 2046 | 737.93 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Electric Engagement | 2047 | 752.313 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Electric Engagement | 2048 | 766.439 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Electric Engagement | 2049 | 776.227 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year
Electric Engagement | 2050 | 784.736 | NESO FES 2025 ED1; annual fiscal total assigned to the same model year

## Opening fleet
Opening fleet ¦ individual cohorts and vintages
GW means installed power; GWh means stored energy. Dates may be sourced or estimated as recorded. Renewable contract expiry does not force physical retirement. Anonymous forecast completions are not contracted capacity.
ID | Name | Technology | Capacity | Unit | Online | Retire | Stage | Basis | Estimate | Source
GAS-000185 | SUTTON BRIDGE POWER GENERATION | gas | 0.819 | GW | 1999-01-01 | 2039-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000377 | Severn Power Ltd | gas | 0.85 | GW | 2010-01-01 | 2050-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000197 | Seabank Power Ltd | gas | 1.205 | GW | 2000-01-01 | 2040-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000169 | EP SHB LTD | gas | 1.4 | GW | 1997-01-01 | 2037-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000376 | EP Langage Ltd | gas | 0.905 | GW | 2010-01-01 | 2050-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000941 | Carrington Power | gas | 0.884 | GW | 2016-01-01 | 2056-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000178 | Rocksavage Power Company Ltd | gas | 0.81 | GW | 1998-01-01 | 2038-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000222 | Coryton Energy Company Ltd | gas | 0.8 | GW | 2002-01-01 | 2042-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000250 | Spalding Energy Company Ltd | gas | 0.95 | GW | 2004-01-01 | 2044-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-001280 | Spalding Expansion OCGT | gas | 0.299 | GW | 2019-01-01 | 2059-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000354 | Marchwood Power | gas | 0.898 | GW | 2009-01-01 | 2049-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000151 | Little Barford | gas | 0.735 | GW | 1995-01-01 | 2035-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000170 | Kings Lynn | gas | 0.395 | GW | 1997-01-01 | 2037-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000176 | Didcot B | gas | 1.49 | GW | 1998-01-01 | 2038-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000210 | Cheshire | gas | 0.06 | GW | 2000-01-01 | 2040-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000212 | Great Yarmouth | gas | 0.42 | GW | 2001-01-01 | 2041-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000282 | Hythe | gas | 0.053 | GW | 2005-01-01 | 2045-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000375 | Staythorpe | gas | 1.828 | GW | 2010-01-01 | 2050-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000453 | Pembroke | gas | 2.325 | GW | 2012-01-01 | 2052-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-001275 | Grimsby | gas | 0.04 | GW | 2018-01-01 | 2058-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000120 | Peterhead | gas | 1.18 | GW | 1980-01-01 | 2031-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000123 | Keadby | gas | 0.732 | GW | 1996-01-01 | 2036-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000152 | Medway | gas | 0.755 | GW | 1995-01-01 | 2035-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000182 | Burghfield | gas | 0.05 | GW | 1998-01-01 | 2038-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000183 | Chickerell | gas | 0.05 | GW | 1999-01-01 | 2039-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-001553 | Keadby 2 | gas | 0.84 | GW | 2023-01-01 | 2063-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000502 | West Burton CCGT | gas | 1.332 | GW | 2013-01-01 | 2053-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000136 | Killingholme | gas | 0.619 | GW | 1992-01-01 | 2032-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000162 | Connahs Quay | gas | 1.38 | GW | 1996-01-01 | 2036-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000179 | Cottam Development Centre | gas | 0.445 | GW | 1999-01-01 | 2039-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000186 | Enfield | gas | 0.408 | GW | 1999-01-01 | 2039-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000138 | Rye House | gas | 0.715 | GW | 1993-01-01 | 2033-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000195 | Damhead Creek | gas | 0.805 | GW | 2000-01-01 | 2040-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000196 | Shoreham | gas | 0.42 | GW | 2000-01-01 | 2040-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000221 | Blackburn | gas | 0.06 | GW | 2002-01-01 | 2042-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
XXX-001661 | VPI Immingham B | gas | 0.299 | GW | 2026-01-01 | 2066-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
GAS-000144 | Peterborough Power Station | gas | 0.245 | GW | 1993-01-01 | 2033-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
XXX-001525 | Croydon | gas | 0.05 | GW | 2005-01-01 | 2045-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
XXX-001526 | Derby | gas | 0.05 | GW | 1997-01-01 | 2037-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
XXX-001527 | Exeter | gas | 0.05 | GW | 2000-01-01 | 2040-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
XXX-001528 | Heartlands | gas | 0.1 | GW | 1998-01-01 | 2038-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
XXX-001529 | Peterborough Power Station PPL2 Gas Engines | gas | 0.049 | GW | 2018-01-01 | 2058-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
XXX-001530 | Thornhill | gas | 0.04 | GW | 1997-01-01 | 2037-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
XXX-001531 | Viking | gas | 0.05 | GW | 2000-01-01 | 2040-01-01 | Aggregate/named cohort | Listed installed MW; assumed retained into 2030 | Retirement estimated: commissioning year +40, no earlier than 2031 for a currently listed plant. Site year may predate replacement turbines; not an operator closure announcement. | data/evidence/dukes_stations.xlsx
forecast-gas-residual | Unidentified non-CHP gas / scope residual | gas | 6.5979 | GW | 2030-01-01 | 2055-01-01 | Aggregate/named cohort | 2030 outlook total less listed non-CHP gas | Forecast-conditioned opening capacity; not a list of committed projects. Assumed new in 2030, life25. Cost before programme boundary excluded. | data/evidence/tyo2026_es1.csv
NUC-000126 | Hartlepool | nuclear | 1.185 | GW | 1983-01-01 | 2030-04-01 | Aggregate/named cohort | Listed capacity; announced AGR March2030 endpoint | Retire 1April2030, conditional on safe continued operation; no later extension credited. | data/evidence/dukes_stations.xlsx; https://www.edfenergy.com/media-centre/uk-energy-security-supported-further-nuclear-power-station-life-extensions
NUC-000127 | Heysham 1 | nuclear | 1.06 | GW | 1983-01-01 | 2030-04-01 | Aggregate/named cohort | Listed capacity; announced AGR March2030 endpoint | Retire 1April2030, conditional on safe continued operation; no later extension credited. | data/evidence/dukes_stations.xlsx; https://www.edfenergy.com/media-centre/uk-energy-security-supported-further-nuclear-power-station-life-extensions
NUC-000131 | Heysham 2 | nuclear | 1.24 | GW | 1988-01-01 | 2030-04-01 | Aggregate/named cohort | Listed capacity; announced AGR March2030 endpoint | Retire 1April2030, conditional on safe continued operation; no later extension credited. | data/evidence/dukes_stations.xlsx; https://www.edfenergy.com/media-centre/uk-energy-security-supported-further-nuclear-power-station-life-extensions
NUC-000132 | Torness | nuclear | 1.2 | GW | 1988-01-01 | 2030-04-01 | Aggregate/named cohort | Listed capacity; announced AGR March2030 endpoint | Retire 1April2030, conditional on safe continued operation; no later extension credited. | data/evidence/dukes_stations.xlsx; https://www.edfenergy.com/media-centre/uk-energy-security-supported-further-nuclear-power-station-life-extensions
NUC-000159 | Sizewell B | nuclear | 1.198 | GW | 1995-01-01 | 2055-01-01 | Announced extension; conditional completion | Listed capacity; announced AGR March2030 endpoint | July2026 agreed heads of terms support operation to2055. Final contract and regulatory approvals remain conditions. January2055 is a simplified annual boundary. Generic inherited nuclear cost allowance retained; not a project-specific refinancing/refurbishment account. | https://www.gov.uk/government/news/sizewell-b-power-plant-given-lifetime-extension-to-2055; https://www.edfenergy.com/media-centre/milestone-moment-sizewell-b-life-extension-agreement
HPC-1 | Hinkley Point C unit 1 | nuclear | 1.63 | GW | 2030-06-01 | 2090-06-01 | Aggregate/named cohort | Named project; accounts valuation commissioning assumption | June date is an assumption, not guaranteed delivery; no commissioning ramp-up. Life60. Existing project capital excluded from incremental programme spending. | https://www.gov.uk/government/publications/desnz-annual-report-and-accounts-2025-to-2026/financial-statements
HPC-2 | Hinkley Point C unit 2 | nuclear | 1.63 | GW | 2031-06-01 | 2091-06-01 | Aggregate/named cohort | Named project; accounts valuation commissioning assumption | June date is an assumption, not guaranteed delivery; no commissioning ramp-up. Life60. Existing project capital excluded from incremental programme spending. | https://www.gov.uk/government/publications/desnz-annual-report-and-accounts-2025-to-2026/financial-statements
REPD-1018 | Fen Farm Solar Park | solar | 0.001 | GW | 2011-07-11 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1019 | Manor Farm | solar | 0.0047 | GW | 2011-07-25 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1020 | Nanterrow Farm | solar | 0.0047 | GW | 2011-07-25 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1021 | Howton Farm | solar | 0.0044 | GW | 2011-07-22 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1022 | East Langford Farm | solar | 0.005 | GW | 2011-07-25 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1023 | Trevemper solar farm | solar | 0.0017 | GW | 2011-09-20 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1024 | Chester Energy (East Woolley Farm) | solar | 0.005 | GW | 2012-06-01 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1028 | Chynoweth Farm | solar | 0.0029 | GW | 2011-07-25 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1029 | Carlton Farm Solar farm | solar | 0.005 | GW | 2011-10-31 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1032 | Wheal Jane | solar | 0.0014 | GW | 2011-07-06 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1034 | Cantelupe Solar Farm | solar | 0.005 | GW | 2013-02-28 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1035 | Benbole Farm | solar | 0.002 | GW | 2011-07-28 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1039 | Langage Solar Farm | solar | 0.005 | GW | 2011-07-15 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1040 | Grange Solar Farm | solar | 0.0046 | GW | 2011-07-13 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1041 | Ebbsfleet Farm Solar Farm | solar | 0.0049 | GW | 2011-09-05 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1042 | Westcott Venture Park Phase 2 & 3 | solar | 0.0013 | GW | 2012-09-01 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1046 | Summerway Drove | solar | 0.002 | GW | 2011-09-01 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1047 | Puriton Solar Farm | solar | 0.0046 | GW | 2011-10-01 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1048 | Toyota Solar Farm | solar | 0.0046 | GW | 2011-07-25 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1049 | Long Sutton Butterfly And Wildlife Park | solar | 0.0017 | GW | 2011-07-14 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1050 | Long Sutton Butterfly And Wildlife Park (extension) | solar | 0.001 | GW | 2011-07-14 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1053 | Springhill Solar Park (Northwick) | solar | 0.005 | GW | 2013-02-01 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1054 | Westmill Farm - PV | solar | 0.005 | GW | 2011-07-19 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1055 | Rhosygilwen Solar Farm | solar | 0.001 | GW | 2011-07-09 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1056 | Llancayo Solar Farm | solar | 0.0039 | GW | 2011-07-01 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1058 | Shacks Barn Solar Farm | solar | 0.005 | GW | 2013-03-28 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1059 | Carines Farm Solar Array | solar | 0.001 | GW | 2013-03-30 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1060 | Trigon Solar Farm | solar | 0.007 | GW | 2013-03-08 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1062 | Chittering Solar Farm Extension | solar | 0.0063 | GW | 2013-03-21 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1064 | Tredinnick Fields | solar | 0.0058 | GW | 2013-03-15 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1065 | Summercourt Solar Farm (Glebe Farm) | solar | 0.0011 | GW | 2013-03-30 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1067 | Higher Trevartha Farm | solar | 0.003 | GW | 2013-03-31 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1070 | Beechgrove Farm | solar | 0.004 | GW | 2011-07-01 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1076 | PARK WOOD SOLAR FARM | solar | 0.005 | GW | 2011-09-29 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1078 | Promens Solar | solar | 0.0017 | GW | 2011-07-21 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1079 | Malmesbury Solar | solar | 0.005 | GW | 2011-07-25 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1080 | Trefullock Solar Farm | solar | 0.005 | GW | 2011-07-07 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1081 | Lower Coombe Farm Solar | solar | 0.001 | GW | 2011-06-24 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1082 | Durrants Farm Solar | solar | 0.0045 | GW | 2011-07-01 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1084 | Dunsfold Park Solar Farm | solar | 0.002 | GW | 2011-07-26 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1085 | Alan Bartlett & Sons Solar | solar | 0.0012 | GW | 2013-03-31 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1086 | Tavells Lane Solar Farm | solar | 0.0053 | GW | 2013-03-20 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1088 | LITTLE TREVEASE SOLAR PARK | solar | 0.0053 | GW | 2013-03-20 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1089 | Cobbs Cross Solar Park | solar | 0.005 | GW | 2013-03-30 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1090 | NOTTINGTON LANE SOLAR FARM | solar | 0.005 | GW | 2013-03-30 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1091 | RUDGE FARM SOLAR FARM | solar | 0.007 | GW | 2013-03-28 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1094 | CRINACOTT SOLAR FARM (Pyworthy) | solar | 0.0067 | GW | 2013-03-31 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1095 | Chawton Farm Solar Farm | solar | 0.0032 | GW | 2013-03-22 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1096 | VENTNOR ROAD SOLAR PARK | solar | 0.0048 | GW | 2013-03-23 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1097 | ROOKERY FARM SOLAR FARM | solar | 0.0053 | GW | 2013-06-03 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1098 | Little White Alice Solar Park | solar | 0.0013 | GW | 2013-04-30 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1103 | Park Wall Solar Park | solar | 0.005 | GW | 2013-03-21 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1108 | Hall Farm Solar park | solar | 0.015 | GW | 2016-02-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1128 | Oulton Airfield Solar Farm (Phase 1) | solar | 0.005 | GW | 2016-02-18 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1157 | Chalcroft Solar Park | solar | 0.0063 | GW | 2013-03-24 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1158 | Bradford Solar Park | solar | 0.0053 | GW | 2013-03-21 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1160 | Lower Coombe Farm (Bean Field) | solar | 0.001 | GW | 2012-08-31 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1161 | Ffos Las Racecourse | solar | 0.0055 | GW | 2012-06-30 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1163 | Woodforde Farm | solar | 0.009 | GW | 2013-03-31 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1165 | Kingston Farm | solar | 0.005 | GW | 2011-10-01 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1166 | Spriggs Farm | solar | 0.012 | GW | 2013-06-30 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1169 | Rotherdale Farm | solar | 0.005 | GW | 2015-01-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1171 | Turves Solar Farm | solar | 0.005 | GW | 2013-03-19 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1173 | Rexton Cross | solar | 0.002 | GW | 2013-05-01 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1176 | Hatchlands Farm | solar | 0.0052 | GW | 2013-03-25 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1184 | Land At Potash Farm | solar | 0.007 | GW | 2013-03-30 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1198 | Land at Upper Clayhill Farm | solar | 0.0049 | GW | 2015-12-16 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1203 | Towerbrook Farm (Banwell Solar Farm) | solar | 0.0072 | GW | 2015-03-27 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1208 | Twin Elm Solar Farm | solar | 0.001 | GW | 2012-07-25 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1223 | Hardingham Solar Farm | solar | 0.0148 | GW | 2014-01-05 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1226 | Hollamoor Farm (PV) | solar | 0.002 | GW | 2013-08-01 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1229 | Langlands Solar Farm | solar | 0.0021 | GW | 2013-03-20 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1230 | Langunnett Solar Farm | solar | 0.0062 | GW | 2013-03-28 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1232 | Manston Solar Farm | solar | 0.0099 | GW | 2013-03-28 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1233 | Marsh House Solar Park | solar | 0.0055 | GW | 2015-03-21 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1237 | Morrisons roof mounted solar | solar | 0.002 | GW | 2013-11-15 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1240 | Rickfield Farm solar park | solar | 0.001 | GW | 2014-11-01 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1243 | Tump Solar Farm | solar | 0.005 | GW | 2017-03-08 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1244 | West Farm (Solar) | solar | 0.0077 | GW | 2013-03-28 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1247 | Owls Lodge Farm | solar | 0.005 | GW | 2013-02-28 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1252 | Beckley Solar Farm | solar | 0.0017 | GW | 2012-07-27 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1269 | Oakham Farm | solar | 0.008 | GW | 2016-02-22 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1272 | Limberlost Farm | solar | 0.0015 | GW | 2013-03-22 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1273 | Office Field | solar | 0.0072 | GW | 2013-03-28 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1274 | Sandys Moor Road | solar | 0.0029 | GW | 2013-08-31 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1275 | Skylark Meadow Solar park | solar | 0.005 | GW | 2013-03-19 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1278 | Aldi Distribution Centre - Darlington | solar | 0.0012 | GW | 2014-03-26 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1282 | Bishops Sutton | solar | 0.012 | GW | 2014-03-27 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1283 | Blackawton Solar Farm | solar | 0.003 | GW | 2014-09-30 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1284 | BMW UK Manufacturing Ltd | solar | 0.003 | GW | 2014-11-05 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1285 | Land to the East of Burton Lane | solar | 0.0026 | GW | 2016-03-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1292 | Land west of Hawkspur Green (Hill Hall Solar) | solar | 0.0049 | GW | 2016-12-09 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1294 | Kingspan Insulation Solar Installation | solar | 0.005 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1298 | Langley Hall Farm | solar | 0.0024 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1299 | Pond Farm | solar | 0.0036 | GW | 2014-07-03 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1303 | Nether Mill Farm | solar | 0.0031 | GW | 2014-09-01 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1304 | NEWNTON DAIRY FARM | solar | 0.0072 | GW | 2014-03-19 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1306 | Pierces Farm | solar | 0.0017 | GW | 2015-03-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1308 | Rew Farm Solar Farm | solar | 0.0061 | GW | 2014-03-27 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1314 | Westbury (Closed) Landfill Site | solar | 0.0035 | GW | 2014-08-05 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1315 | Wiggin Hill Solar Farm - Phase 2 | solar | 0.0041 | GW | 2015-03-14 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1320 | Grain Harvesters Ltd | solar | 0.001 | GW | 2014-12-01 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1322 | Hyde Farm | solar | 0.0108 | GW | 2014-11-13 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1324 | St Francis Farm | solar | 0.004 | GW | 2015-03-19 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1325 | Bishop’s Waltham Solar Farm | solar | 0.012 | GW | 2017-02-17 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1328 | Nova Scotia Farm solar park | solar | 0.0139 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1329 | Hall Farm, East Beckham | solar | 0.0102 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1330 | Cefn Betingau Farm | solar | 0.009 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1331 | Hill Farm Solar Park (VoWH) | solar | 0.0148 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1332 | Wix Lodge | solar | 0.0187 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1333 | Saxley Farm | solar | 0.005 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1335 | Snarlton Farm (Melksham solar farm) | solar | 0.0496 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1338 | Lackford Estate Solar Park | solar | 0.0209 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1339 | Colpmans Farm | solar | 0.005 | GW | 2012-04-17 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1340 | Porvair International Ltd | solar | 0.0018 | GW | 2012-10-04 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1341 | Willsland Solar farm | solar | 0.0032 | GW | 2013-03-21 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1342 | Frying Down Copse Solar Farm | solar | 0.005 | GW | 2012-04-16 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1343 | Wilmingham Lane Solar Farm | solar | 0.007 | GW | 2013-03-14 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1344 | Chilton Cantelo Solar Farm | solar | 0.005 | GW | 2013-02-28 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1346 | Beaford Brook Solar Park | solar | 0.0052 | GW | 2013-06-03 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1348 | Hayford Farm | solar | 0.0089 | GW | 2014-09-10 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1349 | Halse Farm | solar | 0.0082 | GW | 2013-03-28 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1352 | STRETE FARM SOLAR FARM | solar | 0.0048 | GW | 2013-03-08 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1353 | Tregassow Farm - Solar Modules | solar | 0.006 | GW | 2013-03-28 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1355 | Higher Hatherleigh Solar Farm extension | solar | 0.0015 | GW | 2013-03-28 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1356 | Pont Andrew Solar Farm | solar | 0.0015 | GW | 2012-07-31 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1358 | Cairnhill Farm solar park | solar | 0.0024 | GW | 2015-09-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1359 | Manston Solar Farm extension (Westwood) | solar | 0.0092 | GW | 2014-03-28 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1362 | Newlands Farm Solar | solar | 0.0205 | GW | 2014-03-29 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1367 | Fen Road | solar | 0.0014 | GW | 2014-07-22 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1374 | Long Meadow Farm | solar | 0.0041 | GW | 2015-12-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1380 | Liverton Farm | solar | 0.0048 | GW | 2015-03-19 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1382 | Home Farm (Knowlton - solar) | solar | 0.0115 | GW | 2014-03-30 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1384 | Lake Farm | solar | 0.005 | GW | 2011-07-01 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1385 | Parkhouse Corner (Orta Solar) | solar | 0.0066 | GW | 2013-02-23 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1386 | Sandhill Solar Park | solar | 0.002 | GW | 2011-07-13 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1387 | Mingay Farm | solar | 0.005 | GW | 2011-07-14 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1388 | Jordanston Solar Farm | solar | 0.005 | GW | 2013-03-28 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1390 | Aldi Distribution Centre - Neston | solar | 0.0012 | GW | 2014-03-24 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1394 | Rodbourne Rail Farm - Solar Park | solar | 0.0076 | GW | 2013-08-02 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1404 | Barnby Moor | solar | 0.004 | GW | 2015-03-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1416 | Knockworthy Farm | solar | 0.0035 | GW | 2013-08-31 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1418 | Raglington Farm | solar | 0.0058 | GW | 2013-08-31 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1421 | Stables Farm | solar | 0.0015 | GW | 2012-08-07 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1423 | Luson Farm | solar | 0.0019 | GW | 2013-02-26 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1428 | Kellygreen Farm | solar | 0.004 | GW | 2016-03-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1429 | Grove Farm (solar) | solar | 0.0035 | GW | 2015-03-24 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1433 | Marston Solar Farm | solar | 0.0049 | GW | 2011-07-18 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1435 | Tredown Solar Farm | solar | 0.0012 | GW | 2013-08-27 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1439 | Slaughtergate Farm | solar | 0.0018 | GW | 2013-03-20 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1441 | Kia Ora Farm | solar | 0.0018 | GW | 2013-03-21 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1442 | Ellicombe Farm | solar | 0.0014 | GW | 2013-03-18 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1443 | Southcombe Farm | solar | 0.0012 | GW | 2013-03-20 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1445 | West Bradley Farm | solar | 0.0015 | GW | 2012-08-03 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1446 | Whiddon Farm | solar | 0.001 | GW | 2013-03-25 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1449 | Lovedean Farm | solar | 0.0045 | GW | 2013-03-28 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1450 | Higher Knapp Farm | solar | 0.0015 | GW | 2013-03-21 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1453 | Park Farm | solar | 0.004 | GW | 2013-03-02 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1454 | Dunkeswell Airfield | solar | 0.002 | GW | 2015-03-11 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1463 | Langenhoe Solar Farm | solar | 0.0213 | GW | 2015-03-04 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1464 | Kentishes Solar Farm | solar | 0.005 | GW | 2016-12-13 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1467 | Marley Thatch Solar Farm | solar | 0.0063 | GW | 2013-03-31 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1468 | Newlands Farm (East Devon) | solar | 0.005 | GW | 2013-03-20 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1473 | Goldthorpe | solar | 0.0015 | GW | 2014-05-21 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1474 | Barley Wood Farm Lane | solar | 0.0054 | GW | 2015-03-20 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1476 | Battens Farm Solar Park | solar | 0.011 | GW | 2014-03-15 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1478 | Combermere Abbey | solar | 0.014 | GW | 2015-03-29 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1480 | Foxburrow Farm | solar | 0.008 | GW | 2014-10-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1484 | Great Houndbeare Farm | solar | 0.01 | GW | 2017-03-31 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1485 | Condover (Green Farm) | solar | 0.0102 | GW | 2015-03-24 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1489 | Hurst Farm | solar | 0.005 | GW | 2014-05-19 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1490 | Ikea Distribution Centre | solar | 0.0017 | GW | 2015-12-23 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1491 | Jaguar Land Rover | solar | 0.0058 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1494 | Leverton Ings | solar | 0.012 | GW | 2014-03-28 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1497 | Little Morton Solar Farm | solar | 0.0143 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1498 | Lodge Farm - Orston | solar | 0.0124 | GW | 2014-03-28 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1500 | Lowther Farms | solar | 0.0018 | GW | 2014-07-28 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1501 | Mackies Dairy PV | solar | 0.0018 | GW | 2015-09-28 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1502 | Mingay Farm - extension | solar | 0.0193 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1503 | Redcourt Farm | solar | 0.0033 | GW | 2015-03-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1506 | Sowerby Lodge Farm | solar | 0.005 | GW | 2018-06-30 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1507 | Stone Hill | solar | 0.0026 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1509 | Taunton Racecourse | solar | 0.0015 | GW | 2015-03-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1510 | The Stables | solar | 0.0018 | GW | 2014-08-22 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1513 | Vantage Point | solar | 0.0014 | GW | 2011-09-29 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1515 | Wilsom Farm | solar | 0.011 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1516 | Woodlands Farm Solar Park | solar | 0.01 | GW | 2015-03-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1518 | Bowerhouse Farm | solar | 0.0083 | GW | 2015-03-29 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1519 | Brickyard Barn | solar | 0.0041 | GW | 2014-11-27 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1520 | Bronwylfa Reservoir | solar | 0.003 | GW | 2015-06-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1521 | Land At Court Farm | solar | 0.0022 | GW | 2016-03-16 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1522 | Crapnell Farm Solar Farm | solar | 0.0054 | GW | 2014-03-28 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1525 | Danes Farm - extension | solar | 0.0105 | GW | 2016-03-11 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1527 | Ellough Airfield (Resubmission) | solar | 0.0132 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1528 | Ermine Street Farm solar park | solar | 0.0325 | GW | 2014-07-29 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1529 | Eynsham Solar Farm | solar | 0.0132 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1531 | Ford Farm (Ashurst) | solar | 0.01 | GW | 2016-02-29 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1536 | Priors Byne Farm | solar | 0.0076 | GW | 2016-01-20 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1537 | Scottow Moor - RAF Coltishall Solar Farm (Phase 1) | solar | 0.032 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1538 | Owls Lodge Farm Extension | solar | 0.005 | GW | 2013-12-31 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1540 | Hawksland Solar | solar | 0.0031 | GW | 2013-03-28 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1541 | Middle Treworder Farm | solar | 0.005 | GW | 2013-03-30 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1542 | Black Bush Farm | solar | 0.0027 | GW | 2014-07-01 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1543 | Goonhilly Downs - PV | solar | 0.0045 | GW | 2014-03-19 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1544 | Higher Tregarne Solar Farm | solar | 0.005 | GW | 2013-04-07 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1545 | Causilgey Solar Farm | solar | 0.005 | GW | 2013-03-31 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1546 | Ninnis Farm Solar | solar | 0.005 | GW | 2013-03-30 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1547 | Trelow Farm | solar | 0.0016 | GW | 2012-03-01 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1548 | Hewas Solar Farm | solar | 0.005 | GW | 2013-05-07 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1549 | Great Knowle Farm Solar | solar | 0.003 | GW | 2012-07-27 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1550 | Airfield Farm PV | solar | 0.005 | GW | 2012-03-29 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1551 | Lower Bodiniel Farm | solar | 0.005 | GW | 2012-03-15 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1552 | Shelswell Park Solar Farm | solar | 0.005 | GW | 2013-03-22 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1553 | Chittering Solar Farm | solar | 0.005 | GW | 2012-06-28 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1554 | Kernow Solar Farm | solar | 0.005 | GW | 2012-11-30 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1555 | Limes Farm Solar Farm | solar | 0.0046 | GW | 2013-03-28 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1557 | Bratton Fleming Solar Farm | solar | 0.005 | GW | 2013-03-21 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1558 | Lee Farm | solar | 0.005 | GW | 2012-07-31 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1560 | Woodlands Barton Solar Farm | solar | 0.0049 | GW | 2013-03-13 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1561 | Winsdon Farm | solar | 0.005 | GW | 2014-01-28 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1562 | The Manor of Cadland Estate | solar | 0.005 | GW | 2012-07-23 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1563 | Trenouth Farm | solar | 0.0036 | GW | 2012-06-01 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1564 | Callington Solar Farm | solar | 0.0064 | GW | 2014-01-17 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1566 | St Columb Major Solar Farm | solar | 0.007 | GW | 2014-03-14 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1567 | Crossways Pit Solar Farm | solar | 0.005 | GW | 2013-03-28 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1569 | Ayshford Court Farm | solar | 0.005 | GW | 2013-03-28 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1570 | Andover Solar Farm | solar | 0.005 | GW | 2013-03-22 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1571 | Oving Solar Farm | solar | 0.005 | GW | 2012-08-14 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1572 | Grange Farm (Cornwall) | solar | 0.005 | GW | 2013-02-28 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1573 | Shipton Bellinger - Park House Corner Solar Farm | solar | 0.0054 | GW | 2013-02-21 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1574 | Wyld Meadow Solar Farm | solar | 0.0048 | GW | 2012-04-01 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1575 | Shooters Bottom Solar Park | solar | 0.007 | GW | 2014-02-05 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1576 | Goldenhaye Field Solar Farm | solar | 0.002 | GW | 2013-04-15 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1577 | Clearwell Farm - solar | solar | 0.002 | GW | 2015-12-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1578 | Danes Farm | solar | 0.0033 | GW | 2011-07-31 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1580 | Langstone Court Road Solar Farm | solar | 0.0025 | GW | 2013-01-11 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1581 | Five Oaks Solar Farm | solar | 0.005 | GW | 2011-12-01 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1582 | Culworth House Solar Farm | solar | 0.003 | GW | 2015-01-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1583 | Warleigh Barton Solar Farm | solar | 0.005 | GW | 2013-03-20 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1584 | Trenoweth Solar Farm | solar | 0.0025 | GW | 2013-03-28 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1585 | Wymeswold Airfield | solar | 0.034 | GW | 2013-03-28 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1586 | Higher Hatherleigh Solar Farm | solar | 0.0035 | GW | 2013-03-28 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1587 | Barton Solar Farm | solar | 0.0012 | GW | 2012-07-27 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1588 | Clann Solar Farm | solar | 0.0014 | GW | 2014-11-04 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1589 | Dolmans Hill (Redbridge Farm) Solar Arrays | solar | 0.005 | GW | 2014-01-03 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1590 | North Norfolk Business Centre Solar Park | solar | 0.011 | GW | 2014-02-28 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1591 | Horsacott Farm Solar Park | solar | 0.0064 | GW | 2013-03-29 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1592 | Broxted Solar Farm (Stradishall Airfield) | solar | 0.0316 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1593 | Pentylands Farm | solar | 0.019 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1594 | Trefinnick Farm | solar | 0.005 | GW | 2013-10-01 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1595 | Four Burrows Solar farm | solar | 0.0072 | GW | 2015-01-12 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1598 | Rudbaxton Solar Park | solar | 0.0108 | GW | 2014-03-08 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1601 | Hope Solar Farm | solar | 0.0073 | GW | 2014-01-23 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1603 | Culmhead Solar Farm | solar | 0.0075 | GW | 2014-01-26 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1604 | Wheal Alfred Road Solar Farm | solar | 0.0035 | GW | 2013-04-30 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1605 | Blatchworthy Farm | solar | 0.0015 | GW | 2013-04-29 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1606 | Parsonage Barn (extension) | solar | 0.0076 | GW | 2013-06-28 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1607 | BIOSSENCE SOLAR PARK | solar | 0.0045 | GW | 2011-07-31 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1609 | HENDRA HOLIDAY PARK SOLAR FARM | solar | 0.0012 | GW | 2011-08-07 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1610 | EASTACOMBE SOLAR FARM | solar | 0.0036 | GW | 2012-07-01 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1611 | Lodge Farm Solar Farm | solar | 0.005 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-1612 | Wrexham Social Housing PV | solar | 0.0054 | GW | 2012-08-01 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1614 | Creathorne Farm - Solar Farm | solar | 0.0018 | GW | 2014-08-01 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1616 | First Wessex Housing Properties (multiple) | solar | 0.001 | GW | 2015-12-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1617 | Higher Pirzwell Solar Farm | solar | 0.0012 | GW | 2012-07-26 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1618 | Broadgate Solar Farm | solar | 0.0011 | GW | 2012-07-27 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1619 | CRAYSMARSH SOLAR FARM | solar | 0.0018 | GW | 2012-11-26 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1620 | SOLAR PARK - WHITCHURCH FARM | solar | 0.0065 | GW | 2014-01-17 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1622 | THE HOLLIES SOLAR PARK - SKEGNESS | solar | 0.0086 | GW | 2013-06-07 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1623 | AMBLESTON SOLAR PANELS | solar | 0.006 | GW | 2012-01-25 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1626 | Ford Farm Solar Farm | solar | 0.005 | GW | 2013-05-02 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1630 | Canworthy Water | solar | 0.041 | GW | 2014-12-10 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1631 | Foxcombe Farm Solar Park | solar | 0.005 | GW | 2013-06-10 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1634 | Liddeston Ridge Solar Park (Milford Haven) | solar | 0.005 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1639 | Bodwen Solar Park | solar | 0.0055 | GW | 2017-02-15 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1641 | Treswarrow Solar Park | solar | 0.0065 | GW | 2015-03-18 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1642 | Carnemough Farm Solar Park | solar | 0.007 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1646 | Aller Court Farm Solar Park | solar | 0.005 | GW | 2017-04-01 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1648 | Derriton Fields Solar Farm | solar | 0.0118 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1649 | Cleave Farm Solar Park | solar | 0.0047 | GW | 2013-10-25 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1655 | Four Burrows Farm (Extension 2) | solar | 0.0063 | GW | 2014-11-03 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1656 | Chelworth Industrial Estate Solar Park | solar | 0.001 | GW | 2014-02-24 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1658 | Drapers Farm Solar Park | solar | 0.006 | GW | 2014-03-30 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1659 | Week Farm Solar Park | solar | 0.0033 | GW | 2014-03-28 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1661 | Langton Farm Solar park | solar | 0.0044 | GW | 2015-12-03 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1663 | Says Court Farm solar park | solar | 0.0198 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1667 | Ketton solar farm | solar | 0.009 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1669 | The Manor of Cadland Estate - extension | solar | 0.003 | GW | 2014-02-07 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1671 | Rowles Farm solar park | solar | 0.013 | GW | 2015-03-14 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1672 | Ryston Estate Solar Park | solar | 0.0048 | GW | 2015-05-07 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1673 | Reaches Farm Solar Park | solar | 0.0061 | GW | 2014-03-21 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1681 | Watchfield Lawn | solar | 0.0102 | GW | 2014-03-12 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1694 | Bicker Fen (previously Manor Farm) | solar | 0.0226 | GW | 2024-03-12 | 2054-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1699 | Witches Solar Farm | solar | 0.005 | GW | 2013-02-19 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1713 | Burntstalk Solar Park | solar | 0.0115 | GW | 2013-03-30 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1714 | Claypit Moor Solar Farm (Lexham) | solar | 0.0079 | GW | 2013-03-29 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1715 | Holton Airfield | solar | 0.011 | GW | 2013-12-19 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1716 | Goose Willow Farm | solar | 0.0115 | GW | 2013-12-23 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1717 | Chediston Hall Solar Park | solar | 0.0123 | GW | 2013-05-24 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1718 | Burthy Farm | solar | 0.01 | GW | 2015-03-20 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1719 | Caeremlyn Solar Farm | solar | 0.018 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1720 | Hazard Farm | solar | 0.0064 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1721 | Home Farm (Merton - solar) | solar | 0.0183 | GW | 2013-11-12 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1723 | Rudge Hill Farm | solar | 0.0015 | GW | 2013-10-25 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1724 | Sevor Farm | solar | 0.0093 | GW | 2013-11-30 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1725 | Marsh Farm | solar | 0.014 | GW | 2014-01-22 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1726 | Four Burrows Solar farm (Extension 1) | solar | 0.0015 | GW | 2014-02-23 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1727 | Old Rides solar Farm | solar | 0.008 | GW | 2014-01-15 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1728 | Parabel North Beer Solar Farm | solar | 0.0068 | GW | 2013-03-31 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1729 | Crockers Hele | solar | 0.0013 | GW | 2013-09-15 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1730 | Bentley Motors Ltd 1 | solar | 0.0051 | GW | 2013-03-21 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1731 | Northwick Estate (Extension) | solar | 0.0022 | GW | 2013-05-31 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1732 | North Of Field Barn | solar | 0.001 | GW | 2014-08-01 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1735 | Wroughton Airfield Solar Park | solar | 0.041 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1736 | Forest Heath Solar Farm | solar | 0.005 | GW | 2014-02-04 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1737 | Abbey Farm | solar | 0.009 | GW | 2014-03-19 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1743 | Land at Soho Farm | solar | 0.0015 | GW | 2014-03-24 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1744 | Land South West Of Apollo Business Park | solar | 0.0017 | GW | 2014-04-15 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1746 | Manor Farm (Monmouthshire) | solar | 0.0105 | GW | 2016-06-23 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1747 | Land at Mill Farm | solar | 0.001 | GW | 2013-11-04 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1748 | Land at East Farm | solar | 0.0068 | GW | 2013-11-09 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1750 | New Rendy Farm | solar | 0.0048 | GW | 2013-12-15 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1751 | Reydon Farm | solar | 0.0039 | GW | 2015-03-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1752 | Copley Farm | solar | 0.03 | GW | 2016-01-13 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1753 | Ellough Airfield (Ellough 2 extension) | solar | 0.01 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1754 | Nanteague Farm | solar | 0.0077 | GW | 2015-02-05 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1755 | Grange Farm (Burton Pedwardine) | solar | 0.015 | GW | 2014-04-30 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1756 | Wheat Leasows Solar Park | solar | 0.004 | GW | 2014-12-01 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1757 | Honington Solar Farm | solar | 0.0136 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1758 | Hill Farm Solar Park | solar | 0.0102 | GW | 2014-05-30 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1761 | Homeland Solar Farm | solar | 0.0132 | GW | 2014-03-01 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1762 | East Fairlee | solar | 0.0073 | GW | 2015-02-12 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1763 | Fairwind Farm | solar | 0.01 | GW | 2014-09-30 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1764 | Redlands Farm | solar | 0.0062 | GW | 2015-02-18 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1765 | Fenton Home Farm | solar | 0.0313 | GW | 2014-09-12 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1766 | Abbots Ripton Solar Farm | solar | 0.0247 | GW | 2014-03-27 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1767 | South Lees Farm | solar | 0.011 | GW | 2014-06-22 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1768 | Southwick Estate | solar | 0.048 | GW | 2015-03-10 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1769 | Waterloo solar park | solar | 0.0146 | GW | 2015-03-19 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1772 | Ketton solar farm - phase 2 | solar | 0.003 | GW | 2015-01-10 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1774 | Oak Cottage | solar | 0.0049 | GW | 2015-08-21 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1775 | Sycamore Farm | solar | 0.02 | GW | 2014-05-30 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1776 | North Wayton Farm | solar | 0.005 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1777 | South Creake Solar Farm | solar | 0.026 | GW | 2016-03-11 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1781 | Pen Y Cae solar farm | solar | 0.0069 | GW | 2015-03-26 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1783 | Rose And Crown Farm | solar | 0.03 | GW | 2016-03-18 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1784 | Wickfield Farm | solar | 0.005 | GW | 2017-03-21 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1785 | Rookery Farm | solar | 0.0038 | GW | 2015-03-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1787 | Seaview Farm | solar | 0.0017 | GW | 2016-03-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1788 | Chelveston Airfield - extension | solar | 0.0035 | GW | 2014-09-30 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1804 | Huddlesford Farm | solar | 0.001 | GW | 2016-04-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1806 | Park Lane | solar | 0.001 | GW | 2016-04-04 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1811 | Gypsom Solar Farm | solar | 0.005 | GW | 2017-03-31 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1813 | Polmaugan Farm | solar | 0.005 | GW | 2014-07-03 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1815 | Land at Gilley's Mill Dam | solar | 0.005 | GW | 2016-03-21 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1816 | East Lenham Solar Farm | solar | 0.0066 | GW | 2014-03-30 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1817 | Steventon Solar Park | solar | 0.01 | GW | 2014-06-19 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1818 | Westwood Farm Solar Park | solar | 0.0051 | GW | 2015-01-12 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1820 | Meadow Farm solar park | solar | 0.006 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1823 | Sutton Mawr Farm | solar | 0.0075 | GW | 2014-03-04 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1824 | Carloggas Farm Solar Park | solar | 0.0083 | GW | 2015-03-17 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1826 | Lincoln Farm | solar | 0.0114 | GW | 2016-03-25 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1827 | Llwyn Du Solar Farm | solar | 0.008 | GW | 2015-02-26 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1828 | West Hill Farm (solar) | solar | 0.0073 | GW | 2014-07-29 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1832 | Elms Farm | solar | 0.029 | GW | 2015-03-16 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1834 | Rock Farm / Goldborough Farm (Rookwood) | solar | 0.005 | GW | 2015-03-02 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1835 | Great Wilbraham Solar Farm | solar | 0.0381 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1836 | Somerton Door Farm | solar | 0.0087 | GW | 2015-03-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1838 | Barugh Farm | solar | 0.005 | GW | 2016-01-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1840 | Lains Farm | solar | 0.005 | GW | 2016-03-24 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1842 | Great Seabrook Farm | solar | 0.005 | GW | 2015-09-28 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1843 | Cotgrave solar farm | solar | 0.0049 | GW | 2015-07-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1846 | Parkview solar park | solar | 0.0065 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1848 | Overton | solar | 0.004 | GW | 2015-12-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1850 | Lower Basset Down Farm | solar | 0.0105 | GW | 2016-03-18 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1862 | Morfa Farm | solar | 0.002 | GW | 2016-12-19 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1864 | Barton Close Farm | solar | 0.0055 | GW | 2016-02-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1865 | Wiggin Hill Solar Farm - Phase 1 | solar | 0.0068 | GW | 2015-03-14 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1872 | Wilton Farm (pv) | solar | 0.0095 | GW | 2015-06-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1874 | Canada Farm | solar | 0.0083 | GW | 2014-12-02 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1875 | Hoback Farm | solar | 0.0131 | GW | 2014-11-01 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1876 | The Rainbows Solar Farm | solar | 0.004 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1878 | Salcey Solar Farm | solar | 0.005 | GW | 2014-09-25 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1884 | Hillsmoor Solar Farm | solar | 0.0012 | GW | 2017-07-27 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1885 | Desford Solar Farm | solar | 0.005 | GW | 2016-03-23 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1886 | Iwood Lane Solar Farm | solar | 0.008 | GW | 2014-12-19 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1889 | Playters Solar Farm | solar | 0.0086 | GW | 2016-02-26 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1890 | Bypass Nurseries Solar Farm | solar | 0.0033 | GW | 2014-07-28 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1892 | Warrington Home Solar Scheme | solar | 0.0053 | GW | 2016-01-01 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1893 | Babergh Home Solar Scheme | solar | 0.0028 | GW | 2016-06-01 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1894 | Mid Suffolk Home Solar Scheme | solar | 0.0048 | GW | 2016-01-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1895 | Garn Solar Farm | solar | 0.0074 | GW | 2014-05-12 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1896 | Trethosa Farm Solar Park | solar | 0.0048 | GW | 2015-10-09 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1897 | Garvinack Farm Solar Park | solar | 0.007 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1898 | Caswell Farm Solar Park | solar | 0.0067 | GW | 2016-03-23 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1899 | Epwell Grounds Farm solar park | solar | 0.007 | GW | 2014-12-10 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1900 | Pant-Y-Moch Farm | solar | 0.005 | GW | 2016-01-06 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1902 | Woolbridge Solar Park | solar | 0.005 | GW | 2014-06-18 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1903 | Tengore Lane | solar | 0.0036 | GW | 2015-02-12 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1904 | Manor Farm (Dorset) | solar | 0.005 | GW | 2014-06-09 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1905 | Hadlow Place solar farm | solar | 0.0143 | GW | 2015-03-27 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1906 | Bassingbourn Solar Farm | solar | 0.0144 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1907 | Lower Pennington Farm | solar | 0.0027 | GW | 2014-06-27 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1908 | Goose Willow Farm - extension | solar | 0.007 | GW | 2014-03-01 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1909 | Avenue Farm | solar | 0.0073 | GW | 2015-03-20 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1910 | Sywell Road | solar | 0.005 | GW | 2017-03-23 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1912 | Gosfield Airfield | solar | 0.0126 | GW | 2015-02-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1913 | Exning | solar | 0.0299 | GW | 2015-03-27 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1914 | Grange Farm (Avon) | solar | 0.021 | GW | 2014-12-11 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1915 | Land at East Farm - extension | solar | 0.006 | GW | 2016-03-01 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1918 | Laughton Level | solar | 0.007 | GW | 2015-03-26 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1919 | Croydon / Church Farm (Royston) | solar | 0.0165 | GW | 2015-03-20 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1920 | Hadley Farm (Orta Membury Solar Farm) | solar | 0.017 | GW | 2015-03-26 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1923 | Manor Farm (Wiltshire) | solar | 0.0063 | GW | 2015-08-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1924 | Tonge Corner Farm | solar | 0.022 | GW | 2016-03-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1925 | Oaklands Farm | solar | 0.0069 | GW | 2015-03-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1927 | North East of Ainderby Steeple | solar | 0.0059 | GW | 2017-03-24 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1930 | Errol Estate | solar | 0.013 | GW | 2016-03-19 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1931 | Grange Farm | solar | 0.006 | GW | 2015-03-13 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1938 | Wraysbury Landfill | solar | 0.0048 | GW | 2017-03-21 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1940 | Wisbridge Farm | solar | 0.0093 | GW | 2014-10-01 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1942 | Caddington Solar Farm (Phase 1) | solar | 0.003 | GW | 2014-12-11 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1943 | Capeland Farm | solar | 0.0083 | GW | 2015-02-27 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1944 | Castle Combe Circuit | solar | 0.012 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1945 | Castle Eaton Farm | solar | 0.0178 | GW | 2014-03-30 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1946 | Chancery Farm (Ardleigh) | solar | 0.0119 | GW | 2016-03-29 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1947 | Clapham solar farm | solar | 0.0075 | GW | 2016-03-01 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1949 | Chelveston Airfield | solar | 0.016 | GW | 2014-02-28 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1950 | Chisbon Solar Farm (Frowick Lane) | solar | 0.013 | GW | 2015-03-05 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1951 | Clawdd Ddu PV | solar | 0.0135 | GW | 2014-03-26 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1952 | Congresbury Solar Farm | solar | 0.0071 | GW | 2015-12-19 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1953 | Abergelli Glas Solar Farm | solar | 0.0077 | GW | 2015-03-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1954 | Anthony Estate Solar Farm | solar | 0.0047 | GW | 2015-07-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1955 | Aston House Solar Farm | solar | 0.02 | GW | 2015-03-27 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1957 | Bakers Farm (solar) | solar | 0.012 | GW | 2015-03-20 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1958 | Balls Wood Solar Farm | solar | 0.0087 | GW | 2015-12-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1959 | Barn Farm | solar | 0.0042 | GW | 2015-08-14 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1961 | Bay Farm | solar | 0.0081 | GW | 2014-03-01 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1963 | Berwick solar farm | solar | 0.0082 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1964 | Bidwell Solar Farm | solar | 0.005 | GW | 2015-04-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1966 | Bilsham Farm | solar | 0.0145 | GW | 2014-11-10 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1968 | Blackwell Grange Solar Farm | solar | 0.005 | GW | 2017-03-15 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1969 | Blenches Mill | solar | 0.0061 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1970 | Bobbing solar farm | solar | 0.0113 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1971 | Bodmin 2 Solar Farm | solar | 0.0053 | GW | 2015-03-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1973 | Bottom Plain | solar | 0.01 | GW | 2014-12-04 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1974 | Braydon Manor Farm | solar | 0.0087 | GW | 2016-01-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1975 | Brynwhilach Solar Park | solar | 0.004 | GW | 2021-11-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1976 | Bulls Head Farm North | solar | 0.0047 | GW | 2014-10-02 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1978 | Burrowton Farm | solar | 0.005 | GW | 2016-09-18 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1981 | Ebbsfleet Solar Farm | solar | 0.005 | GW | 2014-03-15 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1982 | Court Colman solar park | solar | 0.015 | GW | 2015-11-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1983 | Cowdown Lane | solar | 0.04 | GW | 2016-03-23 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1984 | Crannaford Solar Farm | solar | 0.0125 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1985 | Cwmcaesingrug Farm | solar | 0.01 | GW | 2015-03-02 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1987 | Decoy Farm House Solar Modules | solar | 0.006 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1990 | Hadley Solar Farm | solar | 0.0066 | GW | 2015-12-16 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1991 | Hall Farm Solar Farm (Newbold Verdon) | solar | 0.005 | GW | 2015-12-08 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1992 | Hammond Court Farm | solar | 0.015 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1994 | Hatch Penn Farm PV | solar | 0.001 | GW | 2014-03-08 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1995 | Hayford Farm - extension | solar | 0.0082 | GW | 2015-03-26 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1998 | High Penn Solar Park | solar | 0.0096 | GW | 2014-03-30 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-1999 | Highfields Farm (Braintree) | solar | 0.0028 | GW | 2014-03-28 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2000 | Highfields Farm (Colchester) | solar | 0.0122 | GW | 2014-03-28 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2001 | Hill End Farm | solar | 0.0028 | GW | 2014-03-29 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2004 | Holwell Hill | solar | 0.006 | GW | 2016-05-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2005 | Hook Valley Solar Park | solar | 0.017 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2006 | Partridge Farm | solar | 0.0106 | GW | 2016-03-24 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2007 | Aspatria | solar | 0.019 | GW | 2015-03-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2008 | Penare Farm Solar Farm | solar | 0.011 | GW | 2014-03-18 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2009 | Pencoose Farm | solar | 0.0085 | GW | 2015-03-27 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2010 | Pensipple Farm | solar | 0.005 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2011 | Pingewood Road South | solar | 0.0158 | GW | 2015-03-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2012 | Pingry Farm - Phase 1 | solar | 0.0034 | GW | 2014-03-24 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2013 | Pitworthy Farm Solar Park | solar | 0.0156 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2014 | Primrose Hill Farm | solar | 0.0037 | GW | 2015-03-25 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2015 | Pyde Drove | solar | 0.007 | GW | 2014-03-27 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2016 | Race farm | solar | 0.0061 | GW | 2014-03-21 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2017 | Radcliffe Solar Farm | solar | 0.0042 | GW | 2015-06-13 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2019 | Redhall Industrial Estate | solar | 0.005 | GW | 2014-08-08 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2020 | Ring O Bells Farm | solar | 0.005 | GW | 2016-08-18 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2021 | Roanhead Farm | solar | 0.0065 | GW | 2015-03-21 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2022 | Rotherdale Farm - extension | solar | 0.009 | GW | 2015-03-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2023 | Roundponds Farm Solar Park | solar | 0.0135 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2024 | Hopton Road Industrial Estate | solar | 0.0013 | GW | 2014-08-01 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2026 | Field House Solar / Hursley Road | solar | 0.0064 | GW | 2015-03-24 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2027 | Kencot Hill Solar Farm | solar | 0.037 | GW | 2014-10-30 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2028 | KERNICK MICA DAM - SOLAR FARM | solar | 0.012 | GW | 2014-03-29 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2030 | Landmead Farm (East Hanney) | solar | 0.046 | GW | 2014-12-19 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2032 | Lower Newton Farm | solar | 0.0115 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2033 | Lower Slade Farm | solar | 0.0041 | GW | 2015-11-26 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2034 | Lower Ufford Lane | solar | 0.0011 | GW | 2015-06-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2035 | Lynt Farm | solar | 0.027 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2036 | Marchington Solar Farm | solar | 0.0043 | GW | 2016-03-23 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2039 | Monksham Solar Farm | solar | 0.0107 | GW | 2014-03-30 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2040 | Moorhouse Lane | solar | 0.0018 | GW | 2015-05-11 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2041 | Morton Wood Farm | solar | 0.0048 | GW | 2016-03-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2043 | Natewood Farm | solar | 0.0089 | GW | 2015-01-27 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2044 | Netley Landfill Solar | solar | 0.012 | GW | 2017-03-31 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2045 | New Stone House | solar | 0.0125 | GW | 2015-03-16 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2046 | North Creake Airfield | solar | 0.02 | GW | 2014-03-27 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2047 | North of Newton Farm | solar | 0.003 | GW | 2014-03-19 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2049 | Roves Farm (Solar) | solar | 0.0127 | GW | 2015-02-24 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2050 | Salhouse Solar Farm | solar | 0.005 | GW | 2015-10-20 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2051 | Norton Hall | solar | 0.0028 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2052 | Oaklands Plantation | solar | 0.005 | GW | 2016-01-29 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2053 | Ockendon Landfill Solar Farm | solar | 0.038 | GW | 2023-09-01 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2054 | Packington Solar Farm | solar | 0.0139 | GW | 2015-03-16 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2055 | SAUNDERCROFT SOLAR FARM | solar | 0.007 | GW | 2014-03-29 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2056 | Sedbury Park | solar | 0.005 | GW | 2015-03-27 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2057 | Six Hills Solar Farm | solar | 0.0187 | GW | 2015-03-24 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2058 | South Newton Farm | solar | 0.0113 | GW | 2014-03-19 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2059 | Southdown Quarry | solar | 0.0015 | GW | 2015-12-21 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2060 | Southfield Farm Solar Park | solar | 0.0115 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2061 | Spittleborough Farm | solar | 0.012 | GW | 2014-03-25 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2062 | Stanton solar park | solar | 0.005 | GW | 2015-03-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2063 | Stantway Solar Farm | solar | 0.005 | GW | 2014-03-29 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2064 | Stonebarrow Farm | solar | 0.008 | GW | 2014-01-30 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2065 | Stowbridge Farm | solar | 0.024 | GW | 2014-03-28 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2066 | Stratton Hall Solar Park | solar | 0.0116 | GW | 2014-03-07 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2067 | Sutton Montis Road Solar Park / Sutton Bridge Solar Farm | solar | 0.0054 | GW | 2015-02-10 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2068 | Thame solar farm | solar | 0.0043 | GW | 2016-12-16 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2071 | The Flit | solar | 0.0105 | GW | 2015-03-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2072 | The Old Airfield | solar | 0.005 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2073 | Thorne Farm | solar | 0.0062 | GW | 2014-11-05 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2074 | Tiers Cross Solar Farm | solar | 0.024 | GW | 2014-10-25 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2075 | Tilmanstone Colliery | solar | 0.01 | GW | 2016-01-25 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2076 | Toggam Farm | solar | 0.0125 | GW | 2016-03-24 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2077 | Tower Hill Farm | solar | 0.0081 | GW | 2015-03-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2078 | Toyota Motor Manufacturing Uk - Deeside | solar | 0.0038 | GW | 2014-08-26 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2079 | Trench Farm | solar | 0.0072 | GW | 2015-03-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2080 | Troughton Farm | solar | 0.03 | GW | 2016-03-23 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2081 | Turweston Solar Farm | solar | 0.0167 | GW | 2014-12-19 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2082 | Upper Farm solar park | solar | 0.012 | GW | 2015-03-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2083 | Upper Huntingford Farm | solar | 0.0077 | GW | 2016-01-16 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2084 | Walnut Yard (Phase 1) | solar | 0.0018 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2085 | Water Eaton Farm / Port Farm | solar | 0.0348 | GW | 2015-03-25 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2086 | Wedgehill Farm | solar | 0.013 | GW | 2015-01-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2088 | West Raynham | solar | 0.0499 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2089 | Westerfield Farm | solar | 0.0125 | GW | 2015-03-25 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2090 | Westover Farm | solar | 0.007 | GW | 2014-03-30 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2091 | Whitley Farm (1 of 2) | solar | 0.0035 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2092 | Whitley Farm (2 of 2) | solar | 0.0035 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2093 | Whitton Mawr | solar | 0.006 | GW | 2017-05-15 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2095 | Winham Farm | solar | 0.005 | GW | 2015-12-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2096 | Woden Park | solar | 0.005 | GW | 2014-03-26 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2098 | West Kingsmill Farm Solar Park | solar | 0.0016 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2101 | Bommertown Solar Farm | solar | 0.005 | GW | 2015-12-16 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2102 | West Ditchen Farm | solar | 0.005 | GW | 2016-02-26 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2103 | Lower Marsh Farm | solar | 0.005 | GW | 2014-03-24 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2104 | Bodorgan Solar Farm | solar | 0.0126 | GW | 2014-06-20 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2105 | Chapel Lane Parley Solar Farm Phase 2 | solar | 0.036 | GW | 2014-08-29 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2107 | Arkwright Solar Farm | solar | 0.008 | GW | 2015-12-18 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2108 | Charity Farm (Burlton Solar Farm) | solar | 0.0144 | GW | 2016-08-02 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2109 | Verwood Solar Farm | solar | 0.0204 | GW | 2015-02-25 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2110 | Parciau Farm Solar Park | solar | 0.0139 | GW | 2015-03-23 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2111 | Smith Hall Farm Solar Park | solar | 0.005 | GW | 2016-03-29 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2112 | Bystock Solar Farm | solar | 0.0041 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2114 | Bedborough Farm | solar | 0.007 | GW | 2016-02-26 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2117 | Cranham Golf Course Solar Park | solar | 0.0026 | GW | 2016-12-21 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2118 | Hurcott Copse Solar Farm | solar | 0.01 | GW | 2015-03-20 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2120 | Grange Farm Solar Farm | solar | 0.0049 | GW | 2013-08-28 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2121 | Trehawke Barton (Doddycross) Solar Farm | solar | 0.0106 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2125 | Newton Ferrers solar park | solar | 0.0195 | GW | 2016-03-29 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2126 | Nancrossa Farm solar park | solar | 0.006 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2127 | Pitts Farm | solar | 0.0026 | GW | 2014-03-28 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2128 | Walmoor Farm solar park | solar | 0.004 | GW | 2015-03-27 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2129 | Trequite Farm solar park | solar | 0.0099 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2132 | Bentley Estate | solar | 0.005 | GW | 2015-12-17 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2133 | New Row Farm | solar | 0.0039 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2135 | MALMAYNES HALL FARM | solar | 0.012 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2136 | Crucis Park | solar | 0.0125 | GW | 2014-07-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2137 | Treguff Farm | solar | 0.0044 | GW | 2015-02-11 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2138 | Kenardington Place Farm | solar | 0.007 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2139 | Henbury Quarry | solar | 0.0039 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2140 | Grange Farm (Kirkby on Bain) | solar | 0.009 | GW | 2015-03-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2143 | Boxted Airfield | solar | 0.0188 | GW | 2015-03-19 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2144 | Rectory Farm/Emberton | solar | 0.009 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2145 | St Francis Court Farm | solar | 0.004 | GW | 2017-02-01 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2150 | Berry Court Farm | solar | 0.0042 | GW | 2016-12-01 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2151 | Walkers Wood Solar Park | solar | 0.027 | GW | 2015-03-10 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2152 | Odell Glebe Solar Farm | solar | 0.0168 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2153 | Hunstrete (Wilmington Farm) | solar | 0.0023 | GW | 2014-12-30 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2154 | Lower Severalls Farm | solar | 0.0108 | GW | 2017-10-18 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2157 | Burton Farm | solar | 0.0044 | GW | 2015-03-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2158 | Sundorne Grove | solar | 0.02 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2159 | Lower End Farm | solar | 0.0049 | GW | 2015-06-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2160 | Skegness Solar Park | solar | 0.0049 | GW | 2015-12-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2162 | Land north of Temple Normanton | solar | 0.0049 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2164 | Helland Meads | solar | 0.0012 | GW | 2014-11-01 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2165 | Crow Trees Farm | solar | 0.0047 | GW | 2016-03-23 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2166 | Priest Weston | solar | 0.001 | GW | 2015-03-10 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2169 | Horam | solar | 0.0081 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2171 | Turves/Burtnhouse Solar Farm Extension | solar | 0.0047 | GW | 2015-01-21 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2173 | Coombe Farm | solar | 0.008 | GW | 2015-03-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2174 | Higher Hill Farm (extension) | solar | 0.0015 | GW | 2016-05-01 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2175 | Mount Farm | solar | 0.022 | GW | 2016-03-23 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2176 | Hafod-Y-Dafal Farm | solar | 0.014 | GW | 2015-12-22 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2178 | Barr Farm | solar | 0.0018 | GW | 2015-04-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2179 | BAE Samlesbury Aerodrome | solar | 0.002 | GW | 2015-05-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2180 | Shoals Hook Farm | solar | 0.0121 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2181 | Manor Farm | solar | 0.005 | GW | 2015-03-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2182 | Littlewood Farm | solar | 0.014 | GW | 2015-03-26 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2184 | Cherry Tree Farm | solar | 0.005 | GW | 2016-03-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2185 | Lodge Farm | solar | 0.0024 | GW | 2015-09-25 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2186 | Bumpers Farm Phase 1 | solar | 0.005 | GW | 2017-03-25 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2187 | Birch Airfield | solar | 0.0056 | GW | 2015-06-29 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2188 | Gaultney Solar Park | solar | 0.0205 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2190 | Puriton Landfill Solar Farm | solar | 0.0114 | GW | 2015-12-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2192 | Hunciecroft Farm | solar | 0.008 | GW | 2015-03-06 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2196 | Rolleston Park Farm | solar | 0.0187 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2200 | Prestop Park Farm | solar | 0.016 | GW | 2015-03-21 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2201 | Yardwall Manor | solar | 0.003 | GW | 2015-06-08 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2202 | Royston Solar Farm (Phase 1) (a) | solar | 0.005 | GW | 2016-01-29 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2203 | Bradenstoke solar park | solar | 0.0698 | GW | 2016-09-21 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2204 | Deepdale Farm | solar | 0.008 | GW | 2016-06-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2205 | Manor Farm (Horton) | solar | 0.005 | GW | 2016-04-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2206 | Penrhiwarwydd Farm | solar | 0.0085 | GW | 2015-03-26 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2208 | Nowhere Farm | solar | 0.0081 | GW | 2015-03-20 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2210 | Langar Lane | solar | 0.01 | GW | 2016-06-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2211 | Pitchford | solar | 0.0102 | GW | 2015-03-29 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2212 | Condover Airfield | solar | 0.0123 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2213 | Askern Colliery solar farm | solar | 0.005 | GW | 2015-08-14 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2215 | Maesgwyn solar farm | solar | 0.0075 | GW | 2017-02-15 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2216 | Church Farm | solar | 0.0062 | GW | 2015-12-16 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2217 | Folly Farm | solar | 0.0131 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2218 | Stowbridge Farm - Extension (Phase 2) | solar | 0.01 | GW | 2015-03-20 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2219 | Black Peak Farm | solar | 0.0318 | GW | 2015-03-25 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2221 | Jubilee Farm, Barnby Moor | solar | 0.005 | GW | 2017-03-15 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2225 | Newnham Estate | solar | 0.014 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2226 | Wambrook Farm | solar | 0.0041 | GW | 2015-08-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2227 | Gawcott Fields Farm | solar | 0.0092 | GW | 2015-12-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2228 | Mount Mill Farm | solar | 0.012 | GW | 2015-03-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2231 | Handley Park | solar | 0.005 | GW | 2016-03-24 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2232 | Tollgate Farm | solar | 0.0043 | GW | 2016-03-16 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2233 | North Farm (Spetisbury) | solar | 0.0116 | GW | 2015-03-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2234 | Chapel Lane Parley Solar Farm Phase 3 | solar | 0.004 | GW | 2015-09-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2237 | GDL Wymeswold Solar Farm/land off the A6006 | solar | 0.0061 | GW | 2016-02-16 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2238 | Hillhouse Farm | solar | 0.0285 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2239 | Gib Lane (Aston Clinton solar park) | solar | 0.0242 | GW | 2015-03-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2240 | Outwood Farm (Phase 1) | solar | 0.005 | GW | 2016-03-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2241 | Raventhorpe Farm | solar | 0.038 | GW | 2015-03-21 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2242 | Manor Farm (Castle Cary) | solar | 0.0018 | GW | 2017-03-06 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2243 | Maes Bach Farm | solar | 0.0049 | GW | 2015-11-19 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2244 | Sheepbridge Court Farm | solar | 0.005 | GW | 2015-12-20 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2247 | Elton solar farm | solar | 0.005 | GW | 2015-08-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2248 | Cross Roads Plantation | solar | 0.005 | GW | 2015-06-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2249 | Munceys Farm | solar | 0.0316 | GW | 2015-03-25 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2252 | Luscott Barton | solar | 0.013 | GW | 2015-11-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2253 | Kinmel 1 CIC | solar | 0.005 | GW | 2016-06-27 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2255 | Owls Hatch Road | solar | 0.048 | GW | 2015-03-29 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2258 | Wilbees Farm | solar | 0.005 | GW | 2016-10-21 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2259 | Winterbrook | solar | 0.0012 | GW | 2015-10-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2260 | Welbeck Solar / Hazel Gap | solar | 0.016 | GW | 2015-03-19 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2261 | Homestead Farm (Alderton) | solar | 0.0176 | GW | 2015-03-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2263 | Arna Wood Solar | solar | 0.0062 | GW | 2017-03-31 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2264 | Knottingley A | solar | 0.005 | GW | 2016-03-29 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2265 | Clayhill Farm | solar | 0.01 | GW | 2016-06-24 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2266 | Paddock Wood | solar | 0.0092 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2268 | Wick Farm (Burnham on Crouch) | solar | 0.005 | GW | 2015-12-17 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2271 | Netherfield Lane | solar | 0.0197 | GW | 2015-03-23 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2272 | Upper Meadowley Farm | solar | 0.0107 | GW | 2017-03-31 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2274 | Wick Farm Solar Park | solar | 0.0146 | GW | 2016-07-01 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2277 | High Leas | solar | 0.0065 | GW | 2015-12-18 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2278 | Atherstone | solar | 0.0147 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2279 | The Elms | solar | 0.0104 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2280 | Hunters Race Solar Park | solar | 0.0093 | GW | 2014-07-23 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2281 | Parham Airfield (Great Glenham) | solar | 0.0175 | GW | 2013-12-04 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2282 | Chapel Lane Parley Solar Farm Phase 1 | solar | 0.02 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2283 | Welbeck Colliery | solar | 0.0113 | GW | 2014-07-25 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2284 | Priory Farm | solar | 0.0031 | GW | 2014-03-29 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2285 | Norrington Common Solar Farm | solar | 0.01 | GW | 2014-07-04 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2286 | Hendre Fawr Farm | solar | 0.0116 | GW | 2015-03-06 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2288 | Northmoor | solar | 0.005 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2296 | Manor Farm - Shripney | solar | 0.005 | GW | 2016-03-07 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2298 | Chelwood Solar Farm | solar | 0.005 | GW | 2015-12-10 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2299 | Manor Farm - Pertenhall | solar | 0.015 | GW | 2015-10-17 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2300 | Hardingham Solar Farm - extension | solar | 0.0052 | GW | 2015-02-19 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2307 | Brooks Farm Solar Park | solar | 0.008 | GW | 2015-03-28 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2308 | Christchurch Energy | solar | 0.018 | GW | 2015-03-27 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2309 | Yarburgh Grove Farm | solar | 0.0081 | GW | 2015-11-12 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2312 | Taplins Farm solar park | solar | 0.0059 | GW | 2016-06-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2314 | Homestead Farm | solar | 0.0107 | GW | 2015-12-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2319 | The Kickles | solar | 0.005 | GW | 2016-03-22 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2320 | Eakring Solar Farm | solar | 0.0119 | GW | 2015-03-20 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2321 | Egmanton Solar Farm | solar | 0.0142 | GW | 2015-03-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2323 | Branston solar park | solar | 0.0189 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2325 | Golden Hill | solar | 0.0062 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2326 | Chapel Hill | solar | 0.008 | GW | 2015-03-27 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2327 | Pen Rhiw Caradog | solar | 0.0047 | GW | 2017-02-24 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2329 | Vine Farm Solar Park | solar | 0.045 | GW | 2016-03-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2331 | Coombeshead Solar Farm | solar | 0.008 | GW | 2015-03-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2332 | Decoy Farm | solar | 0.005 | GW | 2015-11-13 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2333 | Easington Farm (Chalgrove) | solar | 0.0213 | GW | 2015-03-17 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2334 | Gelliwern Isaf Farm | solar | 0.006 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2335 | Sawmills Solar Farm | solar | 0.0065 | GW | 2015-03-16 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2336 | Walland Farm | solar | 0.005 | GW | 2015-02-04 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2338 | Weycock Road | solar | 0.007 | GW | 2016-03-02 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2342 | Higher Bye Farm | solar | 0.0068 | GW | 2015-03-19 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2343 | Cockhill Solar Farm | solar | 0.02 | GW | 2015-03-26 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2344 | Bentham Farm | solar | 0.008 | GW | 2015-07-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2345 | Boscombe Airfield | solar | 0.0123 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2347 | Shotwick Solar Farm | solar | 0.0722 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2348 | Winnards Perch Solar Farm | solar | 0.0038 | GW | 2013-07-31 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2351 | Lodge Farm (Poulshot) | solar | 0.0145 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2352 | Glebe Farm Solar Energy Park | solar | 0.015 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2353 | Bryn yr Odyn Solar Farm | solar | 0.015 | GW | 2015-02-28 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2354 | Rhyd-y-Pandy Solar Farm | solar | 0.006 | GW | 2015-03-06 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2355 | Saron Road solar park | solar | 0.0067 | GW | 2015-02-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2356 | Tiln Farm solar park | solar | 0.008 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2357 | Langford Solar Farm | solar | 0.013 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2358 | Stokes Marsh Farm | solar | 0.0166 | GW | 2015-03-12 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2359 | West Hall Solar Farm | solar | 0.007 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2360 | Stowbridge Farm - Extension (Phase 1) | solar | 0.01 | GW | 2015-03-20 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2361 | Bourne Park (Solar) | solar | 0.005 | GW | 2015-03-19 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2362 | Hall Farm | solar | 0.0051 | GW | 2015-03-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2363 | Brynteg Farm | solar | 0.0162 | GW | 2014-12-22 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2364 | Stonepit Farm | solar | 0.005 | GW | 2014-07-28 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2365 | Yerbeston Gate Farm | solar | 0.0061 | GW | 2015-11-25 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2366 | Grange Farm (Lincolnshire) | solar | 0.0127 | GW | 2015-03-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2367 | Molehill Farm | solar | 0.018 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2368 | Pashley Farm | solar | 0.0115 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2369 | Fiskerton Airfield (Phase 1) | solar | 0.012 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2370 | Hendai Farm | solar | 0.0134 | GW | 2015-03-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2372 | Bury Lane Fruit Farm | solar | 0.024 | GW | 2014-12-19 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2373 | Marsh Farm Hilperton | solar | 0.0091 | GW | 2015-03-14 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2375 | Ashlawn Farm | solar | 0.0068 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2376 | Cuckoo Grove Farm | solar | 0.0061 | GW | 2015-03-26 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2377 | Gedling Solar Farm | solar | 0.0057 | GW | 2015-03-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2378 | Bilsthorpe Quarry Solar Park | solar | 0.0048 | GW | 2014-11-18 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2379 | Littlebourne | solar | 0.017 | GW | 2014-11-13 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2380 | Wellingborough Solar Farm | solar | 0.0085 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2381 | Baglan Bay Solar Farm - Phase 1 | solar | 0.005 | GW | 2014-03-30 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2382 | Gover Farm Solar Park | solar | 0.008 | GW | 2014-10-24 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2383 | Kerriers Solar Park | solar | 0.0096 | GW | 2014-09-19 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2384 | Hullavington Solar Park | solar | 0.007 | GW | 2015-02-03 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2385 | Crossness Sewage Works PV | solar | 0.0015 | GW | 2011-07-27 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2386 | Higher Hill Farm | solar | 0.005 | GW | 2011-09-26 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2387 | Manor Farm (Keinton Mandeville) | solar | 0.001 | GW | 2011-07-15 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2388 | Walton WTW PV | solar | 0.0018 | GW | 2011-07-30 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2389 | Wolseley National Distribution Centre | solar | 0.002 | GW | 2014-03-18 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2470 | East Anglia 3 (EA 3) | offshore | 1.4 | GW | 2030-01-01 | 2060-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2030-01-01. | data/evidence/repd.csv
REPD-2472 | Hornsea 3 | offshore | 2.955 | GW | 2030-01-01 | 2060-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2030-01-01. | data/evidence/repd.csv
REPD-2479 | Hywind Scotland Pilot Park (Hywind 2) Demonstrator | offshore | 0.03 | GW | 2017-10-27 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2485 | Beatrice Demonstrator | offshore | 0.01 | GW | 2007-07-17 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2487 | Burbo Bank | offshore | 0.09 | GW | 2007-10-18 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2488 | Gunfleet Sands - (Demo) Extension | offshore | 0.012 | GW | 2013-04-19 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2489 | Gunfleet Sands II | offshore | 0.0648 | GW | 2009-07-24 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2490 | Gunfleet Sands Offshore Wind Scheme | offshore | 0.108 | GW | 2009-07-24 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2491 | Inner Dowsing | offshore | 0.0972 | GW | 2008-04-20 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2492 | Kentish Flats | offshore | 0.09 | GW | 2005-09-10 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2493 | Lynn | offshore | 0.0972 | GW | 2008-03-15 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2494 | North Hoyle | offshore | 0.06 | GW | 2003-12-01 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2495 | Rhyl Flats | offshore | 0.09 | GW | 2009-12-28 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2496 | Robin Rigg East | offshore | 0.084 | GW | 2010-04-28 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2497 | Robin Rigg West | offshore | 0.09 | GW | 2009-07-18 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2498 | Scroby Sands | offshore | 0.06 | GW | 2004-03-01 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2499 | Thanet | offshore | 0.3 | GW | 2010-09-16 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2500 | Walney 1 | offshore | 0.1836 | GW | 2011-05-30 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2502 | Hornsea 2 - Optimus and Breesea | offshore | 1.32 | GW | 2022-08-31 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2504 | Kentish Flats 2 | offshore | 0.0495 | GW | 2015-09-14 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2505 | European Offshore Wind Deployment Centre (EOWDC) (Aberdeen Bay - Demonstration site) | offshore | 0.0968 | GW | 2018-09-07 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2506 | Walney 2 | offshore | 0.1836 | GW | 2012-04-06 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2509 | Ormonde Offshore | offshore | 0.15 | GW | 2012-02-22 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2510 | Greater Gabbard Wind Farm | offshore | 0.504 | GW | 2012-09-07 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2511 | London Array Phase 1 | offshore | 0.63 | GW | 2013-04-06 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2512 | Sheringham Shoal | offshore | 0.317 | GW | 2012-10-29 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2513 | Centrica (Lincs) | offshore | 0.27 | GW | 2013-07-24 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2514 | Teeside Offshore Wind Farm | offshore | 0.062 | GW | 2013-08-31 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2515 | Race Bank (Phase 1) | offshore | 0.2898 | GW | 2017-06-08 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2517 | Dogger Bank C (was Teesside A) | offshore | 1.2 | GW | 2030-01-01 | 2060-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2030-01-01. | data/evidence/repd.csv
REPD-2519 | West of Duddon Sands | offshore | 0.389 | GW | 2014-10-30 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2520 | Rampion Offshore Wind Farm (Hastings Zone) | offshore | 0.4 | GW | 2017-11-26 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2521 | Beatrice | offshore | 0.588 | GW | 2019-08-05 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2522 | Neart na Gaoithe | offshore | 0.45 | GW | 2025-07-01 | 2055-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2523 | Blyth Offshore Wind Test Site | offshore | 0.0415 | GW | 2017-10-22 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2524 | East Anglia 1 (EA 1) | offshore | 0.714 | GW | 2020-07-28 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2525 | Hornsea 1 - Heron & Njord | offshore | 1.218 | GW | 2019-12-01 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2526 | Galloper Wind Farm | offshore | 0.353 | GW | 2018-03-30 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2527 | Inch Cape | offshore | 1.08 | GW | 2030-01-01 | 2060-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2030-01-01. | data/evidence/repd.csv
REPD-2528 | Levenmouth demonstration turbine (Fife Energy Park) | offshore | 0.007 | GW | 2014-03-31 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2532 | Triton Knoll | offshore | 0.857 | GW | 2022-01-13 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2533 | Walney 3 | offshore | 0.659 | GW | 2018-09-13 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2534 | Moray East | offshore | 0.95 | GW | 2022-04-01 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2538 | Dudgeon East | offshore | 0.402 | GW | 2017-10-15 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2539 | Burbo Bank Extension (Burbo Bank 2) | offshore | 0.258 | GW | 2017-04-27 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2540 | Seagreen | offshore | 1.075 | GW | 2023-10-16 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2541 | Dogger Bank A & B (was Creyke Beck A & B) | offshore | 2.4 | GW | 2030-01-01 | 2060-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2030-01-01. | data/evidence/repd.csv
REPD-2543 | Gwynt y Mor | offshore | 0.576 | GW | 2015-06-18 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2544 | Humber Gateway A | offshore | 0.219 | GW | 2015-05-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2545 | Westermost Rough A | offshore | 0.21 | GW | 2015-05-26 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2546 | Barrow | offshore | 0.09 | GW | 2006-04-01 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2555 | South Beach Wind Turbine (Somerton) | onshore | 0.0015 | GW | 2000-07-22 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2556 | Swaffham 1 - Ecotech Wind Park | onshore | 0.0015 | GW | 1999-08-16 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2559 | Mynydd Gorddu Wind Farm | onshore | 0.0102 | GW | 1998-04-18 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2563 | Cefn Croes Wind Farm | onshore | 0.0585 | GW | 2005-01-25 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2564 | Carno 'B' Wind Farm | onshore | 0.0168 | GW | 1996-10-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2565 | Carno 'A' Wind Farm | onshore | 0.0168 | GW | 1996-10-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2566 | Cemmaes 'B' Wind Farm | onshore | 0.0034 | GW | 2002-02-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2567 | Trysglwyn Wind Farm | onshore | 0.0056 | GW | 1996-05-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2568 | Hafoty Ucha '2' and '3' Wind Turbine | onshore | 0.0026 | GW | 2002-12-15 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2574 | Royal Seaforth Dock Wind Farm | onshore | 0.003 | GW | 1999-04-24 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2576 | Cemmaes 'C' Wind Farm | onshore | 0.0153 | GW | 2002-02-23 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2582 | Llanbabo Wind Farm | onshore | 0.0204 | GW | 1997-10-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2586 | Tow Law Wind Farm | onshore | 0.0026 | GW | 2001-12-30 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2587 | Kirkheaton Wind Farm | onshore | 0.0018 | GW | 2000-05-22 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2613 | Great Orton Wind Farm (Extension) | onshore | 0.0023 | GW | 2000-02-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2618 | Wharrels Hill Wind Farm | onshore | 0.0104 | GW | 2007-08-07 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2624 | Siddick Wind Farm | onshore | 0.0042 | GW | 1996-08-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2625 | Oldside Wind Farm | onshore | 0.0054 | GW | 1996-09-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2626 | Haverigg Extension Wind Farm | onshore | 0.0024 | GW | 1998-07-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2630 | Blaen Bowi Wind Farm | onshore | 0.0039 | GW | 2002-07-30 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2636 | Parc-Cynog Wind Farm | onshore | 0.0036 | GW | 2001-02-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2653 | Moel Maelogen A | onshore | 0.0026 | GW | 2003-01-30 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2659 | Out Newton Wind Farm | onshore | 0.009 | GW | 2002-01-31 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2672 | Brockholes Wind Cluster | onshore | 0.0024 | GW | 2013-02-18 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2673 | Kilbraur Windfarm Farlary - Extension | onshore | 0.02 | GW | 2011-09-01 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2674 | Maesgwyn | onshore | 0.026 | GW | 2011-04-14 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2680 | Spicer Hill Wind Farm | onshore | 0.0069 | GW | 2013-02-15 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2683 | Ford Motor Company Ltd (Extension) | onshore | 0.002 | GW | 2011-08-12 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2687 | FMC Technologies | onshore | 0.0015 | GW | 2011-12-07 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2691 | Boyndie Airfield Extension | onshore | 0.0023 | GW | 2010-01-04 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2694 | Blue Gates Farm | onshore | 0.0015 | GW | 2010-03-01 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2695 | Celcon Blocks Ltd | onshore | 0.002 | GW | 2016-04-15 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2697 | Hammar's Hill | onshore | 0.0043 | GW | 2010-09-20 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2704 | F M C Land, Pitreavie Business Park | onshore | 0.0015 | GW | 2011-10-31 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2708 | Strath of Brydock - Extension | onshore | 0.0023 | GW | 2009-12-01 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2711 | Hare Hill (East Ayrshire) | onshore | 0.0132 | GW | 2000-11-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2713 | Kirkby Moor | onshore | 0.0048 | GW | 1993-01-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2715 | Bambers II | onshore | 0.0046 | GW | 2006-11-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2723 | Millennium Extension II | onshore | 0.015 | GW | 2011-04-01 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2724 | Cairnmore Farm | onshore | 0.0026 | GW | 2010-07-10 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2741 | St Fergus Moss Wind Farm | onshore | 0.006 | GW | 2012-12-18 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2742 | West Hill, Flotta | onshore | 0.002 | GW | 2010-07-01 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2747 | Chelker Reservoir (Retention of Turbines) | onshore | 0.0012 | GW | 2004-05-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2757 | Whitelee Windfarm Extension phase 2 | onshore | 0.109 | GW | 2013-01-15 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2758 | Hill of Balquhindachy extension | onshore | 0.0017 | GW | 2010-07-09 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2776 | Taff Ely Wind Farm | onshore | 0.009 | GW | 1993-10-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2780 | Mossmorran Wind Farm | onshore | 0.0046 | GW | 2015-12-01 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2782 | Courtstone Wind Turbine | onshore | 0.0023 | GW | 2009-06-04 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2796 | Lairg Wind Farm | onshore | 0.0075 | GW | 2012-01-01 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2804 | G24 Innovations Turbine | onshore | 0.0023 | GW | 2011-07-12 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2822 | Mornflake Oats Wind Turbine | onshore | 0.0023 | GW | 2012-01-18 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2839 | Clochnahill Wind Farm | onshore | 0.0052 | GW | 2012-01-20 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2860 | Strathallan Wind Farm | onshore | 0.0207 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-2867 | St John Hill | onshore | 0.0077 | GW | 2013-03-07 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2873 | Bryn Blaen Wind Farm | onshore | 0.0138 | GW | 2019-01-01 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2875 | MARCH SEWAGE TREATMENT WORKS - WIND TURBINE | onshore | 0.002 | GW | 2012-09-01 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2902 | Burnfoot Hill | onshore | 0.026 | GW | 2010-10-26 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2921 | Chelker Reservoir | onshore | 0.0013 | GW | 1992-06-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2922 | Strath of Brydock | onshore | 0.0046 | GW | 2009-06-01 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2923 | House O'Hill | onshore | 0.005 | GW | 2010-10-04 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2928 | Bagmoor | onshore | 0.016 | GW | 2009-07-01 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2932 | Croda Chemicals Europe | onshore | 0.003 | GW | 2008-10-01 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2935 | Eastman Chemicals, Workington | onshore | 0.004 | GW | 2006-10-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2938 | Lindhurst Wind Farm | onshore | 0.015 | GW | 2010-11-04 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2940 | Craigengelt | onshore | 0.02 | GW | 2010-03-31 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2942 | Saltend Wind Turbine | onshore | 0.0013 | GW | 2007-11-01 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2943 | Loftsome Bridge | onshore | 0.0013 | GW | 2008-02-01 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2944 | Nissan Wind Farm | onshore | 0.004 | GW | 2005-11-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2950 | Parc Cynog Extension | onshore | 0.0084 | GW | 2009-11-01 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2952 | Ranson Moor (phase 1) | onshore | 0.006 | GW | 2007-05-01 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2953 | Ranson Moor Wind Farm (Phase 2) | onshore | 0.004 | GW | 2007-05-01 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2955 | West Durham Wind Farm | onshore | 0.024 | GW | 2009-05-01 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2956 | Dyffryn Brodyn Wind Farm | onshore | 0.0055 | GW | 1994-12-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2965 | North Red Bog | onshore | 0.0016 | GW | 2008-06-23 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2968 | Milton Keynes Wind Farm | onshore | 0.014 | GW | 2010-09-25 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2983 | Broom Hill Farm | onshore | 0.008 | GW | 2009-02-16 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2986 | Winscales Moor | onshore | 0.006 | GW | 2009-05-01 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2988 | Wind Farm Africa Alive | onshore | 0.0041 | GW | 2011-06-01 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2991 | Beinn Tharsuinn Extension (Beinn nan Oighrean) | onshore | 0.0046 | GW | 2009-07-01 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-2999 | St John's Well | onshore | 0.0024 | GW | 2009-07-15 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3002 | Hellrigg Wind farm | onshore | 0.0092 | GW | 2011-09-14 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3015 | Bryn titli Windfarm | onshore | 0.0099 | GW | 1994-06-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3019 | Delabole (Repowering) | onshore | 0.0092 | GW | 2011-02-01 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3021 | Whittlesey | onshore | 0.009 | GW | 2008-09-03 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3028 | Advanced Manufacturing Research Centre | onshore | 0.0026 | GW | 2009-01-20 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3034 | Solutia UK Ltd | onshore | 0.005 | GW | 2009-12-17 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3050 | High Haswell Wind Farm | onshore | 0.004 | GW | 2011-03-10 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3057 | Llandinam Windfarm | onshore | 0.031 | GW | 1993-01-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3061 | Goonhilly Downs Wind Farm Repower | onshore | 0.012 | GW | 2010-11-01 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3068 | MSD Cramlington | onshore | 0.004 | GW | 2011-01-20 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3075 | Skelmonae Wind Farm | onshore | 0.0032 | GW | 2009-12-20 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3077 | Carn Vean | onshore | 0.01 | GW | 2008-10-30 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3078 | Dewlay Cheese Wind Turbine | onshore | 0.002 | GW | 2010-11-01 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3090 | Myres Hill | onshore | 0.0018 | GW | 2001-11-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3092 | High Sharpley Wind Farm | onshore | 0.0026 | GW | 2006-12-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3093 | National Wind Turbine Test Site | onshore | 0.0047 | GW | 2001-02-15 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3096 | Little Cheyne Court Wind Farm | onshore | 0.0598 | GW | 2009-06-01 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3101 | Long Hill Road | onshore | 0.002 | GW | 2005-01-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3105 | Ness point Wind Turbine 1 | onshore | 0.0023 | GW | 2004-12-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3108 | Causeymire | onshore | 0.0483 | GW | 2004-06-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3109 | Hadyard Hill | onshore | 0.12 | GW | 2006-05-08 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3110 | Hare Hill (B) | onshore | 0.0027 | GW | 2004-07-02 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3114 | Crystal Rig Phase 1 | onshore | 0.0625 | GW | 2004-06-30 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3116 | Black Law | onshore | 0.124 | GW | 2004-05-31 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3117 | Ardrossan | onshore | 0.024 | GW | 2003-12-19 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3119 | Braes O'Doune | onshore | 0.072 | GW | 2006-09-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3120 | Thorfinn Wind Farm - NM1500 | onshore | 0.0015 | GW | 2000-04-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3126 | Boulfruich | onshore | 0.013 | GW | 2005-08-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3128 | Bicker Fen | onshore | 0.0267 | GW | 2008-07-28 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3129 | Stags Holt | onshore | 0.018 | GW | 2007-10-01 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3132 | Glass Moor | onshore | 0.016 | GW | 2005-12-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3133 | Gedney Marsh | onshore | 0.012 | GW | 2008-07-15 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3135 | Ben Aketil | onshore | 0.023 | GW | 2007-09-01 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3147 | Knabs Ridge Windfarm | onshore | 0.016 | GW | 2008-04-22 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3149 | Kelburn | onshore | 0.028 | GW | 2012-05-02 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3155 | Ramsey 1 | onshore | 0.0018 | GW | 2008-09-30 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3157 | Bambers Farm | onshore | 0.0096 | GW | 2004-11-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3158 | Ford Wind Park - Dagenham | onshore | 0.0059 | GW | 2004-06-17 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3159 | Swaffham Plashes II | onshore | 0.0018 | GW | 2003-07-15 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3161 | Shooters Bottom Wind Park | onshore | 0.002 | GW | 2008-06-16 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3171 | Caton Moor Windfarm Repowering | onshore | 0.016 | GW | 2006-06-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3172 | Moel Maelogen A Phase 2 | onshore | 0.0117 | GW | 2008-10-01 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3177 | Scout Moor Windfarm | onshore | 0.065 | GW | 2008-06-01 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3179 | The Haven | onshore | 0.0012 | GW | 2003-11-05 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3186 | The Hollies | onshore | 0.0026 | GW | 2008-01-01 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3190 | Tullo Farm | onshore | 0.0175 | GW | 2010-09-07 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3194 | Avonmouth Port | onshore | 0.006 | GW | 2007-08-20 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3200 | Dummuie | onshore | 0.0123 | GW | 2007-01-01 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3201 | Earlsburn | onshore | 0.0375 | GW | 2007-02-01 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3202 | Kilbraur Windfarm | onshore | 0.0475 | GW | 2008-06-14 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3205 | Achany Wind Farm | onshore | 0.038 | GW | 2010-10-11 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3207 | Bilbster Wind Farm | onshore | 0.0039 | GW | 2008-02-01 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3210 | Green Park | onshore | 0.002 | GW | 2005-10-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3214 | Carcant Windfarm | onshore | 0.006 | GW | 2010-11-02 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3218 | Butterwick Moor | onshore | 0.0205 | GW | 2011-04-01 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3220 | Hagshaw Hill Wind Farm Extension | onshore | 0.026 | GW | 2008-10-01 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3223 | Southern Law | onshore | 0.0052 | GW | 2008-07-10 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3229 | Llangwyryfon | onshore | 0.0094 | GW | 2004-02-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3232 | Pates Hill | onshore | 0.014 | GW | 2010-01-20 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3233 | Roskrow Wind Turbines | onshore | 0.0017 | GW | 2007-12-01 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3236 | Greendykeside | onshore | 0.004 | GW | 2007-11-01 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3247 | Loscar Farm | onshore | 0.0045 | GW | 2011-01-01 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3248 | Langley Moor | onshore | 0.008 | GW | 2008-08-13 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3258 | Arecleoch Windfarm | onshore | 0.12 | GW | 2011-06-14 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3260 | Mark Hill | onshore | 0.056 | GW | 2011-06-01 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3264 | Westmill Wind Farm | onshore | 0.0065 | GW | 2008-01-01 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3272 | Lodge Farm 1 | onshore | 0.001 | GW | 2006-08-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3277 | Carno 'A'and 'B' Wind Farm, (Extension) | onshore | 0.0156 | GW | 2009-03-01 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3285 | Achairn | onshore | 0.0062 | GW | 2009-05-20 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3290 | High Hedley Hope 2 (Extension) | onshore | 0.0052 | GW | 2008-06-25 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3292 | Beinn an Tuirc | onshore | 0.0297 | GW | 2001-12-23 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3294 | Cnoc Donn Arnicle | onshore | 0.015 | GW | 2001-10-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3295 | Beinn Ghlas Wind Farm | onshore | 0.0078 | GW | 1999-06-25 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3296 | Bendealt Wind Farm, Highland | onshore | 0.009 | GW | 1997-09-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3297 | Meall an Tuirc Wind Farm | onshore | 0.017 | GW | 1997-09-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3298 | An Suidhe | onshore | 0.0193 | GW | 2010-08-04 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3299 | Bowbeat Emly Bank / Rough Side | onshore | 0.0312 | GW | 2002-09-15 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3306 | Arnish Moor | onshore | 0.0039 | GW | 2006-12-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3307 | Burgar Hill | onshore | 0.005 | GW | 2006-12-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3308 | Thorfinn Wind Farm - NM2000 | onshore | 0.0023 | GW | 2000-04-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3309 | Hill of Lybster | onshore | 0.0049 | GW | 2003-02-08 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3310 | Burradale Hill | onshore | 0.0037 | GW | 2000-12-16 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3311 | Glens of Foudland | onshore | 0.026 | GW | 2005-07-22 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3313 | Castle Pill - Repowering | onshore | 0.0032 | GW | 2009-06-01 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3317 | Whitelaw Brae Wind Farm | onshore | 0.057 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-3321 | New Holland | onshore | 0.001 | GW | 2014-10-20 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3328 | Cumberhead West Wind Farm | onshore | 0.126 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-3354 | Weston Airfield Wind Turbines | onshore | 0.0036 | GW | 2015-03-15 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3359 | Orton Park Farm | onshore | 0.0016 | GW | 2017-06-15 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3361 | PROMISED LAND FARM | onshore | 0.001 | GW | 2014-10-22 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3368 | Nethercott Farm | onshore | 0.0015 | GW | 2016-12-15 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3370 | Bonerbo Wind Turbines | onshore | 0.0015 | GW | 2014-12-15 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3371 | Aberarder Wind Farm | onshore | 0.0499 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-3378 | Princes Gate Spring Water | onshore | 0.0016 | GW | 2014-09-03 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3380 | Phase 1 Bettyhill Wind Farm | onshore | 0.005 | GW | 2013-06-04 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3382 | Sibelco Brassington | onshore | 0.0023 | GW | 2016-09-15 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3387 | Beinn an Tuirc Windfarm Phase 3 | onshore | 0.0499 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-3390 | Lambrigg Wind Farm | onshore | 0.0065 | GW | 2001-09-22 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3391 | Askam | onshore | 0.0046 | GW | 1999-07-13 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3392 | Bears Down Wind Farm | onshore | 0.0098 | GW | 2001-08-31 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3396 | Welton Of Creuchies | onshore | 0.0092 | GW | 2018-01-23 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3398 | Droop Hill Wind Farm x | onshore | 0.0046 | GW | 2014-07-01 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3403 | Denhill | onshore | 0.0023 | GW | 2011-06-01 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3404 | Haddo | onshore | 0.0046 | GW | 2011-05-25 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3405 | Gairnieston Farm | onshore | 0.0023 | GW | 2010-11-01 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3408 | Burgar Hill (land Near), Evie | onshore | 0.0023 | GW | 2009-11-01 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3415 | Tod Hill Farm Wind Turbines | onshore | 0.012 | GW | 2015-01-22 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3429 | Moorhouse Farm | onshore | 0.001 | GW | 2018-05-15 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3432 | Royd Moor | onshore | 0.0059 | GW | 1993-12-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3433 | Stroupster Wind Farm - additional turbine | onshore | 0.0023 | GW | 2015-10-15 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3435 | Gordonbush (extension) | onshore | 0.047 | GW | 2021-01-01 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3437 | Little Belhus Restoration Site | onshore | 0.001 | GW | 2016-09-23 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3440 | Crystal Rig Wind Farm Phase 2a | onshore | 0.138 | GW | 2010-10-25 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3448 | Clachan Flats Wind Farm | onshore | 0.015 | GW | 2008-12-01 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3449 | Fen Farm | onshore | 0.016 | GW | 2008-04-17 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3450 | Darracott Moor | onshore | 0.0026 | GW | 2011-05-06 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3453 | Lochhead Farm | onshore | 0.006 | GW | 2009-07-01 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3457 | Toddleburn | onshore | 0.0276 | GW | 2010-10-12 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3458 | Crimp Wind Farm | onshore | 0.0024 | GW | 2011-04-01 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3466 | Hedley Hope | onshore | 0.0024 | GW | 2001-12-30 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3467 | Tangy Wind Farm/Tangy 1 | onshore | 0.0128 | GW | 2002-12-26 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3479 | Coldham Hall | onshore | 0.014 | GW | 2005-08-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3480 | Whitemill Wind Farm | onshore | 0.014 | GW | 2012-05-02 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3487 | Green Knowes | onshore | 0.027 | GW | 2008-09-29 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3489 | Whitelee | onshore | 0.322 | GW | 2007-12-14 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3491 | Great Orton | onshore | 0.004 | GW | 1999-12-21 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3492 | Winscales Phase I and II | onshore | 0.0088 | GW | 2004-12-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3494 | Holmside Hall | onshore | 0.0028 | GW | 2004-06-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3495 | High Volts Wind Farm | onshore | 0.0055 | GW | 2003-12-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3496 | Hare Hill | onshore | 0.0013 | GW | 2004-07-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3502 | Enoch Hill | onshore | 0.07 | GW | 2026-04-16 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3503 | Benbrack Wind Farm | onshore | 0.0671 | GW | 2025-10-01 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3504 | Great Eppleton Farm Repowering | onshore | 0.0082 | GW | 2010-03-01 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3507 | Haswell Moor | onshore | 0.01 | GW | 2010-12-12 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3510 | Worksop - B&Q | onshore | 0.002 | GW | 2009-01-21 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3511 | Cold Northcott | onshore | 0.0066 | GW | 2002-06-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3524 | Upper Ardgrain Wind Farm | onshore | 0.0024 | GW | 2010-10-01 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3529 | Rothiesholm | onshore | 0.0027 | GW | 2002-04-10 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3532 | Hill of Easterton | onshore | 0.0025 | GW | 2005-01-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3533 | Port of Liverpool - wind | onshore | 0.01 | GW | 2009-02-01 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3534 | Rothes Wind (Cairn Uish) | onshore | 0.0506 | GW | 2004-11-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3536 | Crystal Rig Extension II | onshore | 0.0207 | GW | 2010-10-25 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3538 | Glenkerie Wind Farm | onshore | 0.022 | GW | 2012-02-01 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3539 | Lissett Airfield Wind Farm | onshore | 0.03 | GW | 2009-02-20 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3548 | Methlick Farmers Wind Energy Project | onshore | 0.012 | GW | 2011-12-01 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3552 | Rheidol Wind Farm | onshore | 0.0024 | GW | 1997-02-06 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3554 | Deucheran Hill | onshore | 0.0158 | GW | 2001-11-30 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3556 | Bryn Du | onshore | 0.0164 | GW | 2005-04-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3570 | Dun Law | onshore | 0.0172 | GW | 2000-08-21 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3574 | Black Hill (Borders) | onshore | 0.0286 | GW | 2007-02-14 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3578 | Four Burrows Wind Farm | onshore | 0.0045 | GW | 1998-03-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3579 | Dun Law Extension | onshore | 0.0298 | GW | 2009-09-20 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3581 | Lochelbank Wind Farm II | onshore | 0.0096 | GW | 2011-05-25 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3585 | Cruach Mhor | onshore | 0.0333 | GW | 2004-01-31 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3592 | Wern Ddu Wind Farm | onshore | 0.0092 | GW | 2010-03-01 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3594 | Muirake | onshore | 0.0046 | GW | 2011-12-13 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3598 | Millennium Extension | onshore | 0.01 | GW | 2008-12-01 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3602 | Rusholme Wind Farm | onshore | 0.024 | GW | 2010-10-04 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3605 | Longpark | onshore | 0.038 | GW | 2009-09-01 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3606 | Walkway | onshore | 0.014 | GW | 2008-05-15 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3607 | Coldham | onshore | 0.016 | GW | 2005-11-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3608 | Red Tile | onshore | 0.024 | GW | 2006-12-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3609 | Deeping St Nicholas Wind Farm | onshore | 0.0164 | GW | 2006-08-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3611 | Lowca Wind Farm | onshore | 0.0047 | GW | 2000-04-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3613 | Fairfield Farm | onshore | 0.0065 | GW | 2011-03-02 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3614 | Haverigg Repowering (Haverigg II) | onshore | 0.0012 | GW | 2004-05-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3619 | Beinneun Windfarm Extension | onshore | 0.0238 | GW | 2017-02-16 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3627 | Ewe Hill (extension) | onshore | 0.0368 | GW | 2017-01-15 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3633 | Hazelside farm | onshore | 0.0016 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-3645 | Melton Common Wind Cluster | onshore | 0.005 | GW | 2017-03-01 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3647 | Moy Wind Farm (2nd Application) | onshore | 0.066 | GW | 2016-05-12 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3651 | Rosehill Wind Turbines | onshore | 0.0024 | GW | 2015-12-15 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3657 | Twin Rivers | onshore | 0.0287 | GW | 2016-08-03 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3659 | Blyth Harbour Wind Farm | onshore | 0.0027 | GW | 1992-12-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3660 | Penrhys Wind Farm/Ferndale Power Factory | onshore | 0.0064 | GW | 2011-06-08 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3662 | Gordonbush | onshore | 0.07 | GW | 2012-06-12 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3664 | Avonmouth Wind Power | onshore | 0.0082 | GW | 2014-02-06 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3666 | Gordonstown Hill Wind Farm | onshore | 0.0125 | GW | 2013-03-31 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3667 | The Rosti Factory | onshore | 0.0022 | GW | 2013-02-18 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3668 | Ben Aketil Extension | onshore | 0.0046 | GW | 2011-01-01 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3670 | Lochcarnan Community Windfarm | onshore | 0.0069 | GW | 2013-02-18 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3671 | The Grange Wind Farm | onshore | 0.014 | GW | 2013-03-01 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3672 | Humphrey Group | onshore | 0.005 | GW | 2013-02-25 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3673 | Rodbaston | onshore | 0.004 | GW | 2017-01-15 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3674 | Boundary Lane | onshore | 0.006 | GW | 2013-03-31 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3676 | Nutberry Wind Farm | onshore | 0.015 | GW | 2013-09-30 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3677 | Penny Hill Lane | onshore | 0.0198 | GW | 2013-03-31 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3681 | West Knock Wind Cluster | onshore | 0.0024 | GW | 2011-10-04 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3682 | Low Spinney Wind Farm | onshore | 0.008 | GW | 2011-09-29 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3684 | Westfield | onshore | 0.01 | GW | 2013-03-31 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3685 | Swinford Wind Farm | onshore | 0.022 | GW | 2012-11-21 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3686 | Burnt House Farm | onshore | 0.006 | GW | 2013-06-19 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3688 | Calder Water Community Wind Farm | onshore | 0.028 | GW | 2013-09-01 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3690 | Millour Hill Community Windfarm | onshore | 0.018 | GW | 2012-05-01 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3691 | Netherton of Windyhills | onshore | 0.0046 | GW | 2014-11-01 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3693 | Gallowhill | onshore | 0.0018 | GW | 2013-02-18 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3694 | Frodsham Marsh | onshore | 0.0504 | GW | 2016-11-15 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3695 | Brechfa Forest West | onshore | 0.0574 | GW | 2018-01-18 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3698 | Greenhill Croft | onshore | 0.0046 | GW | 2012-03-01 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3699 | Severn Trent STW | onshore | 0.0025 | GW | 2014-02-26 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3700 | Spaldington Airfield | onshore | 0.0125 | GW | 2016-05-11 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3701 | Hillhead of Auquhirie | onshore | 0.0069 | GW | 2013-01-16 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3702 | Middleton Wind Farm | onshore | 0.012 | GW | 2013-09-04 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3703 | Orchard End | onshore | 0.004 | GW | 2013-06-17 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3705 | Mynydd Bwllfa Wind Farm - Resubmission | onshore | 0.0225 | GW | 2015-05-08 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3707 | Tirgwynt | onshore | 0.0246 | GW | 2017-02-15 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3711 | Garreg Lwyd | onshore | 0.034 | GW | 2017-02-22 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3718 | Castle of Auchry Farm | onshore | 0.0024 | GW | 2013-11-01 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3722 | Little Byth | onshore | 0.0045 | GW | 2012-12-31 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3723 | Yonderton Farm | onshore | 0.001 | GW | 2014-12-01 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3726 | Oakdale Business Park | onshore | 0.004 | GW | 2013-12-24 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3732 | Boddington Reservoir | onshore | 0.0015 | GW | 2014-04-24 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3733 | HMP Standford Hill | onshore | 0.0046 | GW | 2013-02-08 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3734 | Sharpness Docks | onshore | 0.002 | GW | 2017-01-15 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3735 | Sancton Hill | onshore | 0.01 | GW | 2012-06-12 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3738 | Port of Sheerness Wind Farm (was Lappel Bank) | onshore | 0.0082 | GW | 2016-09-20 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3739 | Stonish Hill (Bilsthorpe) | onshore | 0.0103 | GW | 2013-03-31 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3741 | Stags Holt Extension | onshore | 0.002 | GW | 2010-12-31 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3745 | North Yell Wind Farm (Garth Community Wind Farm) | onshore | 0.0045 | GW | 2017-04-03 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3746 | Glenurquhart and Strathglass Wind Farm project | onshore | 0.01 | GW | 2013-04-19 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3747 | Damhead Farm | onshore | 0.0025 | GW | 2013-05-17 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3748 | Hyndburn Wind Farm | onshore | 0.024 | GW | 2012-10-19 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3749 | Tedder Hill Wind cluster | onshore | 0.0075 | GW | 2013-08-30 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3752 | Lynemouth Windfarm (Resubmission) | onshore | 0.026 | GW | 2012-04-12 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3754 | Wingates Wind Farm | onshore | 0.015 | GW | 2013-03-31 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3757 | Wathegar wind farm | onshore | 0.01 | GW | 2013-03-31 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3758 | Allt Dearg Wind Farmers LLP | onshore | 0.0108 | GW | 2012-09-25 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3761 | Hameldon Hill extension | onshore | 0.0075 | GW | 2013-04-25 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3764 | Dalby | onshore | 0.0072 | GW | 2016-03-15 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3765 | Glass moor Extension | onshore | 0.012 | GW | 2013-03-31 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3772 | Cour Wind Farm | onshore | 0.0205 | GW | 2016-12-01 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3776 | Upper Wheedlemont Farm | onshore | 0.0017 | GW | 2017-11-11 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3784 | Shielburn Farm | onshore | 0.0069 | GW | 2013-03-30 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3787 | Beinneun | onshore | 0.085 | GW | 2017-02-16 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3791 | Seamer Wind Farm - Hambleton | onshore | 0.004 | GW | 2012-11-01 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3792 | Fanny House Farm/Heysham Moss | onshore | 0.0015 | GW | 2015-02-01 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3793 | Newthorpe Wind Turbine | onshore | 0.0025 | GW | 2014-04-08 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3795 | Chelveston Renewable Energy Park Wind Farm (Bedford) | onshore | 0.01 | GW | 2014-02-15 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3799 | Torrance Farm | onshore | 0.009 | GW | 2013-12-30 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3802 | Land at Overside and Greenwellheads Farms | onshore | 0.0092 | GW | 2013-11-01 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3803 | Lancaster University (wind) | onshore | 0.002 | GW | 2013-02-18 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3804 | Myreton Crossroads | onshore | 0.0016 | GW | 2013-07-05 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3806 | Auchinderran Wind Farm | onshore | 0.0024 | GW | 2014-12-01 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3807 | The Limes Wind Turbines | onshore | 0.0017 | GW | 2015-01-15 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3809 | Milton of Fisherie Wind Cluster | onshore | 0.0046 | GW | 2016-02-01 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3810 | Blantyre Muir Wind Farm | onshore | 0.009 | GW | 2013-12-30 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3814 | Lilbourne Wind Farm | onshore | 0.01 | GW | 2014-12-15 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3818 | Tullo Wind Farm North Extension (Shiels Wind Farm) | onshore | 0.0075 | GW | 2014-04-01 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3819 | Easter Melrose Wind Energy Project | onshore | 0.0015 | GW | 2015-12-01 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3827 | Newton Marsh Wind Project | onshore | 0.0046 | GW | 2014-04-30 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3828 | North Pickenham Airfield | onshore | 0.004 | GW | 2014-04-01 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3832 | Wythegill Wind Turbine | onshore | 0.0023 | GW | 2015-06-15 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3835 | Roos Wind Farm (Resubmission) | onshore | 0.0171 | GW | 2013-04-02 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3836 | Backhill of Yonderton Wind Cluster | onshore | 0.0046 | GW | 2014-10-15 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3837 | Spurness Wind Farm Repowering | onshore | 0.01 | GW | 2012-12-01 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3840 | St Johns Wells Wind Cluster Extension | onshore | 0.0032 | GW | 2015-03-01 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3841 | GlaxoSmithKline Wind Project | onshore | 0.0075 | GW | 2013-06-30 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3842 | K L Technologies Wind Turbine | onshore | 0.0015 | GW | 2013-10-30 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3846 | Coire Na Cloiche Wind Farm | onshore | 0.0299 | GW | 2020-03-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3855 | Ardoch and Over Enoch Wind Farm (Over Enoch) | onshore | 0.0043 | GW | 2014-11-12 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3856 | Ystgellog Farm Wind Farm | onshore | 0.0046 | GW | 2013-04-30 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3857 | NEILSTON WIND FARM | onshore | 0.0092 | GW | 2013-05-13 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3859 | Greencroft Estate Turbines | onshore | 0.004 | GW | 2013-03-01 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3862 | Crossness Sewage Works Turbine | onshore | 0.0025 | GW | 2014-02-16 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3873 | Muirhall Extension | onshore | 0.0068 | GW | 2014-04-30 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3886 | Freasdail Wind Farm | onshore | 0.0225 | GW | 2017-02-08 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3887 | Nash Waste Water Treatment Works Turbine | onshore | 0.0025 | GW | 2017-03-15 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3890 | Marston Vale Country Park Wind Turbine | onshore | 0.0015 | GW | 2014-05-01 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3893 | Energy Works Hull - Wind Turbine | onshore | 0.003 | GW | 2018-03-01 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3896 | Mynydd Y Gwrhyd Windfarm | onshore | 0.0047 | GW | 2017-12-01 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3897 | Severn Trent Water - Stoke Bardolph Wind Turbine | onshore | 0.0015 | GW | 2015-12-15 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3902 | Barns of Ayre Wind Turbines (2) | onshore | 0.0018 | GW | 2013-07-01 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3904 | Newton Down | onshore | 0.005 | GW | 2016-09-29 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3905 | North Steads Wind Farm | onshore | 0.01845 | GW | 2016-07-04 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3911 | Hill of Tillymorgan (Kirkton Farm) Wind turbines | onshore | 0.0096 | GW | 2016-12-01 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3915 | LADEHEAD FARM - WIND TURBINES | onshore | 0.0024 | GW | 2016-09-15 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3917 | Garlenick Estate 2 - Wind Turbines | onshore | 0.004 | GW | 2015-06-18 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3918 | Goonabarn Farm Wind Turbines | onshore | 0.001 | GW | 2016-04-01 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3924 | Bloodhills - repowering | onshore | 0.001 | GW | 2015-06-15 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3925 | Ardoch and Over Enoch Wind Farm (Ardoch) | onshore | 0.0072 | GW | 2014-11-12 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3927 | Avonmouth Port II | onshore | 0.005 | GW | 2013-09-30 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3928 | Tween Bridge Windfarm | onshore | 0.044 | GW | 2012-02-27 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3931 | Mynydd Portref | onshore | 0.0094 | GW | 2012-03-26 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3932 | Fforch Nest Wind Farm pt2 | onshore | 0.0175 | GW | 2013-05-24 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3935 | Wadlow Wind Farm | onshore | 0.026 | GW | 2012-09-01 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3936 | Bradwell Wind Farm (Repower) | onshore | 0.02 | GW | 2013-09-30 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3937 | Hazlehead | onshore | 0.006 | GW | 2011-12-16 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3938 | Kiln Pit Hill Windfarm | onshore | 0.012 | GW | 2012-08-01 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3941 | Otterham Down Wind Farm | onshore | 0.0032 | GW | 2011-08-17 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3942 | Sixpenny Wood Windfarm | onshore | 0.033 | GW | 2013-07-15 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3943 | Earl's Hall | onshore | 0.0103 | GW | 2013-01-13 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3944 | Mawdesley Moss | onshore | 0.0023 | GW | 2012-08-01 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3946 | Chelveston Renewable Energy Park Wind Farm (East Northamptonshire) | onshore | 0.0125 | GW | 2014-02-15 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3947 | Bewick Drift | onshore | 0.0023 | GW | 2013-03-31 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3948 | Hall Farm Routh | onshore | 0.0246 | GW | 2013-05-28 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3951 | Rothes Wind Farm (Extension) (II) | onshore | 0.0414 | GW | 2013-04-15 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3956 | Fforch Nest Wind Farm pt1 | onshore | 0.01 | GW | 2013-05-24 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3957 | Hampole Wind Farm | onshore | 0.008 | GW | 2014-03-31 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3958 | Blackstone Edge | onshore | 0.0075 | GW | 2013-03-01 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3963 | Marr Windfarm | onshore | 0.008 | GW | 2012-01-18 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3964 | Nissan Motors Plant Extn | onshore | 0.002 | GW | 2008-04-01 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3968 | Hill of Fiddes | onshore | 0.0069 | GW | 2010-02-20 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3971 | Cotton Farm | onshore | 0.02 | GW | 2013-03-31 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3972 | Land at Flimby Hall Farm | onshore | 0.0062 | GW | 2013-06-14 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3976 | Carland Cross Wind Farm Repowering | onshore | 0.02 | GW | 2013-10-30 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3978 | Yelvertoft Wind Farm | onshore | 0.016 | GW | 2013-07-11 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3980 | Mains of Hatton | onshore | 0.0024 | GW | 2012-03-20 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3981 | Whitelee Windfarm Extension Phase 1 | onshore | 0.108 | GW | 2012-10-31 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3982 | Tilbury Docks | onshore | 0.012 | GW | 2013-03-25 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3984 | Seamer Windfarm - Stockton on Tees | onshore | 0.006 | GW | 2012-11-01 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3985 | South Sharpley Wind Farm (Revised) | onshore | 0.0075 | GW | 2013-01-23 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3986 | Armistead Wind Farm | onshore | 0.012 | GW | 2013-02-11 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3987 | Withernwick | onshore | 0.018 | GW | 2013-03-19 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3988 | Loch Sminig Wind Project | onshore | 0.0027 | GW | 2015-09-15 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-3992 | Burton Pidsea (Wadworth Hill) Wind Farm | onshore | 0.0102 | GW | 2014-01-10 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4006 | Camster | onshore | 0.05 | GW | 2013-02-09 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4008 | Bu Farm | onshore | 0.0027 | GW | 2002-05-10 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4009 | Drumderg | onshore | 0.0368 | GW | 2008-11-09 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4011 | Clyde Wind Farm | onshore | 0.35 | GW | 2012-10-01 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4013 | Novar Wind Farm (Extension) | onshore | 0.0368 | GW | 2012-09-17 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4014 | Hill of Towie (Drummuir) | onshore | 0.048 | GW | 2012-06-01 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4015 | Ewe Hill | onshore | 0.0138 | GW | 2016-05-30 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4019 | Middlemoor | onshore | 0.054 | GW | 2013-09-30 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4021 | Baillie Wind Farm | onshore | 0.0525 | GW | 2013-03-29 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4022 | Braich Ddu | onshore | 0.0039 | GW | 2007-08-31 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4023 | Drone Hill | onshore | 0.0286 | GW | 2012-09-01 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4024 | Tangy Wind Farm Extension/Tangy 2 | onshore | 0.006 | GW | 2011-06-17 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4026 | Ray Wind Farm | onshore | 0.0544 | GW | 2017-02-05 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4027 | Calliachar | onshore | 0.0322 | GW | 2013-09-30 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4028 | Griffin Wind farm | onshore | 0.156 | GW | 2012-02-28 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4029 | High Pow Farm | onshore | 0.0039 | GW | 2007-03-15 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4031 | St. Johns Hill | onshore | 0.00765 | GW | 2013-04-01 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4032 | Blackcraig | onshore | 0.0529 | GW | 2018-03-02 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4033 | Fullabrook Down Wind Farm | onshore | 0.066 | GW | 2012-01-24 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4034 | Little Raith Farm | onshore | 0.025 | GW | 2012-11-27 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4039 | Pant y wal | onshore | 0.025 | GW | 2013-06-01 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4044 | Green Rigg | onshore | 0.036 | GW | 2012-11-28 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4051 | Rosehall Hill Forest Windfarm | onshore | 0.0247 | GW | 2013-02-28 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4055 | Bankend Rig | onshore | 0.0143 | GW | 2013-03-27 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4056 | Hill of Easterton Extension | onshore | 0.002 | GW | 2007-07-31 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4057 | Batsworthy Cross | onshore | 0.018 | GW | 2016-04-07 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4059 | Fallago Rig | onshore | 0.144 | GW | 2013-03-31 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4060 | Cathkin Braes Wind Farm (Castlemilk) | onshore | 0.003 | GW | 2013-05-29 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4061 | Mynydd y Betws | onshore | 0.0345 | GW | 2013-04-01 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4062 | Ark Hill | onshore | 0.0064 | GW | 2013-03-29 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4063 | Pentland Road Wind Farm | onshore | 0.0138 | GW | 2013-03-28 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4067 | Turncole Wind Farm | onshore | 0.0175 | GW | 2016-12-22 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4068 | Derby Sewage Treatment Works | onshore | 0.005 | GW | 2014-05-15 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4069 | Grange | onshore | 0.0123 | GW | 2015-12-15 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4070 | Goole Fields ll Wind Farm | onshore | 0.0349 | GW | 2016-11-14 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4072 | Edintore Wind Farm | onshore | 0.018 | GW | 2016-10-31 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4073 | Tralorg Wind Farm | onshore | 0.02 | GW | 2020-06-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4075 | Gremista Wind Farm | onshore | 0.003 | GW | 2015-11-15 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4076 | Common Barn Wind Farm | onshore | 0.0062 | GW | 2019-05-09 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4078 | Clentrie Wind Farm (Gevens) | onshore | 0.0069 | GW | 2016-10-24 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4084 | Kelmarsh Wind Farm (Resubmission) | onshore | 0.0125 | GW | 2016-07-01 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4085 | Torrance Farm Wind Park Extension | onshore | 0.0057 | GW | 2015-06-18 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4088 | Goathill Quarry Turbine | onshore | 0.002 | GW | 2015-12-27 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4093 | Skeddoway Farm Wind Turbine | onshore | 0.0015 | GW | 2014-12-01 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4094 | Middle Balbeggie Wind Turbines | onshore | 0.0064 | GW | 2016-11-20 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4097 | Upper Holton Wind Farm | onshore | 0.0115 | GW | 2016-02-26 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4104 | Tallentire Hill | onshore | 0.012 | GW | 2013-07-09 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4109 | Meikle Carewe | onshore | 0.01 | GW | 2013-07-30 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4110 | Andershaw | onshore | 0.036 | GW | 2016-11-02 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4113 | East Midlands Airport | onshore | 0.001 | GW | 2011-05-10 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4114 | Kildrummy Windfarm | onshore | 0.0184 | GW | 2013-02-14 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4116 | Airfield Farm (Podington) | onshore | 0.0086 | GW | 2017-02-15 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4118 | Dunmaglass Wind Farm | onshore | 0.094 | GW | 2016-09-13 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4119 | Harestanes | onshore | 0.136 | GW | 2014-07-01 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4120 | Corriemoillie | onshore | 0.0544 | GW | 2017-04-26 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4121 | Hill of Stroupster Windfarm | onshore | 0.0299 | GW | 2015-12-03 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4122 | Burn of Whilk | onshore | 0.0225 | GW | 2015-08-07 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4123 | Lochluichart | onshore | 0.051 | GW | 2014-05-14 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4125 | Burnhead | onshore | 0.026 | GW | 2016-02-29 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4128 | Sneddon Law Community Wind Farm | onshore | 0.045 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-4133 | Easter Tolmauds | onshore | 0.0016 | GW | 2016-10-15 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4138 | Maerdy | onshore | 0.024 | GW | 2013-08-31 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4140 | Woodlands Barton Wind Project | onshore | 0.0046 | GW | 2014-09-01 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4141 | Westnewton | onshore | 0.0062 | GW | 2014-05-01 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4157 | Hare Hill Extension | onshore | 0.0298 | GW | 2016-09-15 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4159 | Avonmouth Port - extension | onshore | 0.009 | GW | 2014-04-01 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4163 | Barmoor South Wind Farm | onshore | 0.0138 | GW | 2015-01-19 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4164 | Winwick | onshore | 0.0123 | GW | 2016-06-30 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4167 | Sisters | onshore | 0.0082 | GW | 2016-07-30 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4168 | East Youlstone Wind Farm | onshore | 0.004 | GW | 2015-02-15 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4170 | Hill of Skilmafilly Cloffrickford (Denmore) Wind Farm | onshore | 0.0069 | GW | 2015-02-16 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4174 | Heysham South Wind Farm | onshore | 0.0075 | GW | 2015-04-24 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4175 | Woolley Hill Wind Farm | onshore | 0.01 | GW | 2014-04-30 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4177 | Furness Wind Farm/High Winds (Harlock Repowering) | onshore | 0.0115 | GW | 2016-11-17 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4178 | Clyde Wind Farm Extension (Clyde 2) | onshore | 0.1728 | GW | 2017-08-15 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4179 | Quixwood Moor | onshore | 0.0299 | GW | 2017-03-09 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4184 | Auchadaduie Wind Farm | onshore | 0.0069 | GW | 2018-11-21 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4189 | Dalquhandy Windfarm | onshore | 0.042 | GW | 2023-01-01 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4193 | Mynydd Brombil Wind Farm | onshore | 0.008 | GW | 2017-01-15 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4194 | Mynydd Portref Wind Farm extension | onshore | 0.012 | GW | 2017-03-01 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4196 | Longlands Lane | onshore | 0.0015 | GW | 2014-12-01 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4200 | Inverclyde Wind Farm (Corlic Hill) | onshore | 0.024 | GW | 2021-02-20 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4206 | Ryder Point Quarry Wind Turbines | onshore | 0.005 | GW | 2015-12-15 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4210 | Burton Wold Wind Farm - Northern Extension | onshore | 0.0144 | GW | 2014-08-01 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4211 | Pearie Law Wind Farm | onshore | 0.0192 | GW | 2016-12-01 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4213 | Greengairs East Wind Farm | onshore | 0.024 | GW | 2023-08-25 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4215 | Crystal Rig Wind Farm Phase III | onshore | 0.0138 | GW | 2016-12-22 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4218 | Drumduff | onshore | 0.0085 | GW | 2017-07-11 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4223 | Rhodders Wind Farm | onshore | 0.012 | GW | 2016-02-29 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4225 | Harburnhead Wind Farm | onshore | 0.0517 | GW | 2016-12-01 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4227 | Dunsland Cross Wind Farm | onshore | 0.0075 | GW | 2017-03-08 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4233 | Potato Pot Wind Farm | onshore | 0.006 | GW | 2016-09-15 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4235 | Millour Hill Community Windfarm (Extension) | onshore | 0.0064 | GW | 2016-03-31 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4240 | Blantyre Muir Wind Farm extension | onshore | 0.0075 | GW | 2014-01-15 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4244 | Dorenell Wind Farm (Previously Site A and B Scaut Hill) | onshore | 0.177 | GW | 2018-09-15 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4247 | Earlsburn North (Kingsburn) Wind Farm | onshore | 0.0225 | GW | 2016-05-30 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4248 | Wryde Croft | onshore | 0.026 | GW | 2016-02-20 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4250 | Wandylaw | onshore | 0.0205 | GW | 2013-07-30 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4253 | Black Law Extension - 1a | onshore | 0.0484 | GW | 2016-02-18 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4256 | Bishopthorpe | onshore | 0.0164 | GW | 2017-01-30 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4260 | Keadby Wind Farm | onshore | 0.068 | GW | 2015-02-26 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4261 | Berry Burn | onshore | 0.0667 | GW | 2014-05-30 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4262 | Afton Wind Farm | onshore | 0.05 | GW | 2018-02-15 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4263 | Tormywheel | onshore | 0.03075 | GW | 2017-03-17 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4266 | Den Brook | onshore | 0.018 | GW | 2016-11-17 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4269 | Dersalloch | onshore | 0.069 | GW | 2016-08-15 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4272 | Point Wind / Beinn Ghrideag Farm | onshore | 0.009 | GW | 2015-07-17 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4281 | Muirhall South | onshore | 0.0083 | GW | 2016-03-17 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4295 | Double Arches Quarry Wind Turbine | onshore | 0.0015 | GW | 2014-12-18 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4299 | Lochend Wind Farm | onshore | 0.0092 | GW | 2017-05-15 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4300 | Creag Riabhach Wind Farm | onshore | 0.0924 | GW | 2023-01-12 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4307 | West Benhar wind farm | onshore | 0.0272 | GW | 2023-01-01 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4315 | Sorbie Farm | onshore | 0.009 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-4316 | Hallburn Farm | onshore | 0.0132 | GW | 2018-02-15 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4321 | Coal Clough Wind Farm Repowering | onshore | 0.016 | GW | 2015-05-01 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4326 | Shepham Lane | onshore | 0.0075 | GW | 2017-01-12 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4327 | Sober Hill Wind Farm | onshore | 0.015 | GW | 2013-09-01 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4328 | Srondoire Community Wind Farm | onshore | 0.006 | GW | 2015-12-20 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4330 | Achlachan Wind Farm | onshore | 0.01 | GW | 2019-04-08 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4331 | A'Chruach (Phase 1) | onshore | 0.0483 | GW | 2016-06-29 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4332 | Aikengall II, Wester Dod Community Wind Farm | onshore | 0.0608 | GW | 2017-11-15 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4333 | Alaska Wind Farm | onshore | 0.0092 | GW | 2025-03-01 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4335 | Alveston Wind Park | onshore | 0.0069 | GW | 2017-12-07 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4337 | Auchrobert Wind Farm | onshore | 0.036 | GW | 2017-03-20 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4345 | Boardinghouse Wind Farm | onshore | 0.0103 | GW | 2015-10-01 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4346 | Bogenlea Farm | onshore | 0.0023 | GW | 2014-08-18 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4348 | BROWNIELEYS - 3 WIND TURBINES | onshore | 0.0075 | GW | 2017-02-28 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4350 | Cairnborrow | onshore | 0.01 | GW | 2017-02-09 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4351 | Camster II | onshore | 0.036 | GW | 2026-04-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4354 | Crook Hill (Calderdale MBC) 1 of 2 | onshore | 0.0136 | GW | 2015-12-01 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4360 | Deuchries | onshore | 0.0069 | GW | 2017-12-15 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4362 | Dungavel Hill | onshore | 0.0299 | GW | 2015-08-28 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4363 | Earlseat | onshore | 0.0184 | GW | 2014-07-30 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4365 | Easter Tulloch Wind Farm (Tullo Extension) | onshore | 0.025 | GW | 2014-06-30 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4368 | Galawhistle | onshore | 0.066 | GW | 2017-02-15 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4369 | Gayton Le Marsh Wind Farm | onshore | 0.0164 | GW | 2016-02-26 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4370 | GlaxoSmithKline Wind Project (Turbine 4) | onshore | 0.0025 | GW | 2014-06-01 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4371 | Glen Kyllachy Wind Farm | onshore | 0.0485 | GW | 2022-01-01 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4373 | Goole Fields | onshore | 0.0328 | GW | 2014-08-11 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4374 | Greenvale AP Wind Turbine | onshore | 0.0015 | GW | 2014-08-01 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4377 | Hendy Wind Farm | onshore | 0.0144 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-4381 | Hill of Glaschyle Wind Farm | onshore | 0.0276 | GW | 2016-12-01 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4385 | Kennoxhead Wind Farm | onshore | 0.062 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-4386 | Kilgallioch wind farm | onshore | 0.239 | GW | 2017-12-15 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4390 | Lambs Hill | onshore | 0.008 | GW | 2017-01-19 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4395 | Lochluichart (Extension) | onshore | 0.018 | GW | 2014-05-14 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4399 | M1 Wind Farm | onshore | 0.0072 | GW | 2014-06-30 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4403 | New Rides Wind Farm | onshore | 0.0088 | GW | 2018-12-01 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4404 | Noble Foods | onshore | 0.0015 | GW | 2014-12-01 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4408 | Ovenden Moor (Repower) | onshore | 0.018 | GW | 2017-01-24 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4409 | Pant y wal extension | onshore | 0.02 | GW | 2017-05-01 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4410 | Park Spring Wind Farm | onshore | 0.0086 | GW | 2015-11-20 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4411 | Brotherton (formerly Paul Matthew Hill wind turbines) | onshore | 0.0046 | GW | 2017-05-01 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4412 | Pen Bryn Oer Wind Farm | onshore | 0.004 | GW | 2018-01-15 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4414 | Ramsey Wind Farm Extension | onshore | 0.008 | GW | 2015-04-23 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4415 | Red Gap Moor Wind Farm | onshore | 0.0125 | GW | 2017-02-15 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4418 | Strathy South | onshore | 0.208 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-4419 | Todmorden Moor | onshore | 0.0123 | GW | 2014-09-10 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4420 | Tom Nan Clach | onshore | 0.039 | GW | 2019-03-01 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4422 | Tullo Wind Farm South (Ext.) | onshore | 0.01 | GW | 2014-07-01 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4424 | Watford Lodge | onshore | 0.0125 | GW | 2015-11-23 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4425 | Wathegar 2 Wind Farm | onshore | 0.0185 | GW | 2017-09-15 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4427 | West Browncastle | onshore | 0.03 | GW | 2014-06-30 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4431 | Brochloch Rig (formerly Windy Standard II) | onshore | 0.09 | GW | 2017-06-15 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4432 | Withernwick extension | onshore | 0.0082 | GW | 2019-08-01 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4434 | Pogbie Wind Farm 1 | onshore | 0.0051 | GW | 2019-03-29 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4435 | Barlockhart Moor | onshore | 0.0081 | GW | 2013-08-27 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4437 | Minnygap | onshore | 0.025 | GW | 2017-03-15 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4440 | Middle Muir Wind Farm | onshore | 0.051 | GW | 2019-05-16 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4441 | Sanquhar Community Windfarm | onshore | 0.0324 | GW | 2018-02-01 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4445 | Balmurrie Fell Wind Farm | onshore | 0.0091 | GW | 2012-09-01 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4449 | Solwaybank Wind Farm | onshore | 0.03 | GW | 2020-11-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4450 | Burnfoot Hill Extension | onshore | 0.004 | GW | 2014-09-09 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4462 | Airies Farm | onshore | 0.035 | GW | 2017-03-15 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4465 | Craig Wind Farm (Extension) | onshore | 0.0025 | GW | 2017-05-15 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4480 | Pencloe Wind Farm | onshore | 0.081 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-4483 | Lawrence Landfill | onshore | 0.0016 | GW | 2017-03-15 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4484 | Plascow wind cluster | onshore | 0.0024 | GW | 2015-07-15 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4485 | Maesgwyn Wind Farm - extension | onshore | 0.0025 | GW | 2016-03-29 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4493 | Halifax Farm | onshore | 0.0016 | GW | 2015-09-01 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4497 | Norton Fields Farm | onshore | 0.0013 | GW | 2015-09-15 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4501 | Carscreugh Renewable Energy Park | onshore | 0.0153 | GW | 2014-01-15 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4502 | Whiteside Hill | onshore | 0.0253 | GW | 2018-04-30 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4508 | North Rhins | onshore | 0.022 | GW | 2010-01-20 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4511 | Jacksbank Wind Farm (Glenbervie) | onshore | 0.0068 | GW | 2014-07-12 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4513 | New Albion Wind Farm | onshore | 0.0144 | GW | 2016-01-18 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4514 | Sunnyside wind cluster | onshore | 0.001 | GW | 2015-11-15 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4516 | Keith Hill | onshore | 0.0045 | GW | 2017-12-19 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4517 | Minsca | onshore | 0.0368 | GW | 2008-03-01 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4518 | Artfield Fell | onshore | 0.0195 | GW | 2005-06-23 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4519 | Wether Hill | onshore | 0.0182 | GW | 2007-05-01 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4520 | Dalswinton | onshore | 0.03 | GW | 2008-03-15 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4524 | Craig Wind Farm | onshore | 0.01 | GW | 2007-10-01 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4525 | Beinn an Tuirc Phase 2 | onshore | 0.0437 | GW | 2014-09-01 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4526 | Aikengall | onshore | 0.048 | GW | 2008-11-01 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4527 | Brochloch Rig 1 (formerly Windy Standard) | onshore | 0.0216 | GW | 1996-10-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4529 | Torrs Hill | onshore | 0.004 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-4532 | Hawton Wind Farm | onshore | 0.009 | GW | 2017-03-16 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4544 | Beck Burn | onshore | 0.031 | GW | 2017-04-26 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4552 | Clocaenog Forest Wind Farm | onshore | 0.096 | GW | 2019-10-01 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4575 | Hoprigshiels Community Wind Farm | onshore | 0.0069 | GW | 2017-03-31 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4580 | Black Law Extension - 1b | onshore | 0.015 | GW | 2016-02-18 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4584 | Strathy Wood | onshore | 0.0624 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-4586 | South Kyle Wind Farm | onshore | 0.24 | GW | 2023-06-01 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4591 | Aikengall IIa Community Wind Farm | onshore | 0.0817 | GW | 2021-11-01 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4593 | Glen App | onshore | 0.022 | GW | 2017-01-15 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4595 | Pen Y Cymoedd | onshore | 0.228 | GW | 2017-05-19 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4597 | Stronelairg Wind Farm | onshore | 0.2277 | GW | 2018-12-11 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4598 | M1 J18 Wind Turbines | onshore | 0.004 | GW | 2014-12-15 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4599 | Tullymurdoch Wind Farm | onshore | 0.0144 | GW | 2018-01-23 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4600 | Penmanshiel Wind Farm | onshore | 0.0287 | GW | 2016-07-01 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4601 | Kinegar Quarry | onshore | 0.005 | GW | 2017-03-15 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4604 | St. Breock Re-Power | onshore | 0.01 | GW | 2015-02-23 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4605 | Blary Hill Wind Farm | onshore | 0.035 | GW | 2022-01-01 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4615 | Windy Standard III Wind Farm (Brockloch Rig Phase 2) | onshore | 0.0876 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-4619 | Carraig Gheal | onshore | 0.046 | GW | 2013-10-28 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4620 | Langhope Rig | onshore | 0.016 | GW | 2015-03-26 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4623 | Clashindarroch | onshore | 0.037 | GW | 2015-06-26 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4624 | Galsworthy Wind Park | onshore | 0.0092 | GW | 2014-11-28 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4625 | Strathy North | onshore | 0.0677 | GW | 2015-12-01 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4627 | Mid Hill - Phase II | onshore | 0.0184 | GW | 2014-12-02 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4628 | Kype Muir Wind Farm Extension | onshore | 0.0672 | GW | 2024-10-01 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4629 | Monan Hill Wind Turbines | onshore | 0.0015 | GW | 2015-03-19 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4631 | Crystal Rig Wind Farm Phase IV | onshore | 0.048 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-4633 | Crossdykes | onshore | 0.048 | GW | 2021-06-01 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4636 | Halsary Wind Farm | onshore | 0.034 | GW | 2021-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4637 | French Farm | onshore | 0.004 | GW | 2016-11-24 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4638 | Glenchamber Wind Farm | onshore | 0.0275 | GW | 2016-06-01 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4640 | Bhlaraidh (previously Balmacaan) | onshore | 0.11 | GW | 2017-09-15 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4642 | Moor House Wind Farm | onshore | 0.012 | GW | 2017-12-15 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4643 | Kype Muir Wind Farm | onshore | 0.0884 | GW | 2019-09-15 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4644 | Llynfi Afan Renewable Energy Park | onshore | 0.006 | GW | 2017-09-14 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4645 | Assel Valley Wind Farm | onshore | 0.025 | GW | 2016-10-28 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4646 | Bad a Cheo Wind Farm | onshore | 0.0267 | GW | 2019-05-01 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4647 | Fraisthorpe Wind Farm | onshore | 0.0297 | GW | 2016-06-15 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4648 | Mynydd Y Gwair Wind Farm | onshore | 0.0328 | GW | 2019-04-24 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4649 | Jack's Lane Wind Farm | onshore | 0.0138 | GW | 2015-04-01 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4651 | Denzell Downs Wind Farm | onshore | 0.01 | GW | 2015-11-24 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4655 | Reaps Moss Wind Farm | onshore | 0.0102 | GW | 2015-03-31 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4656 | Llynfi Renewable Energy Park, Land at Mynydd Caerau | onshore | 0.024 | GW | 2017-09-14 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4657 | Chiplow | onshore | 0.0082 | GW | 2016-04-30 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4658 | Hook Moor | onshore | 0.0103 | GW | 2016-01-15 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4659 | Crook Hill (Rochdale MBC) 2 of 2 | onshore | 0.0238 | GW | 2015-12-01 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4660 | Far Marsh Farm | onshore | 0.0075 | GW | 2017-01-15 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4661 | Wear Point | onshore | 0.0082 | GW | 2014-07-07 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4662 | Middlewick wind farm | onshore | 0.0207 | GW | 2014-07-31 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4663 | Blyth Harbour Wind Farm (re-power) | onshore | 0.0034 | GW | 2012-09-01 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4664 | Corriegarth | onshore | 0.0695 | GW | 2016-09-30 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4665 | Carsington Pasture | onshore | 0.008 | GW | 2014-02-05 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4666 | Langford Wind Farm | onshore | 0.02 | GW | 2014-01-30 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4667 | Mid Hill I | onshore | 0.0575 | GW | 2013-12-01 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4668 | Ardrossan Extension | onshore | 0.006 | GW | 2008-11-01 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4669 | Beinn Tharsuinn Windfarm Project | onshore | 0.0298 | GW | 2005-12-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4670 | Blaengwen | onshore | 0.023 | GW | 2009-11-30 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4671 | Boyndie Airfield | onshore | 0.0167 | GW | 2006-02-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4672 | Burton Wold Windfarm | onshore | 0.02 | GW | 2006-04-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4674 | Edinbane Wind Farm | onshore | 0.0414 | GW | 2010-06-21 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4675 | Fairburn | onshore | 0.043 | GW | 2010-06-07 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4676 | Farr Wind Farm | onshore | 0.092 | GW | 2005-10-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4677 | Ffynnon Oer Wind Farm | onshore | 0.032 | GW | 2005-12-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4678 | Flotta | onshore | 0.0018 | GW | 2010-06-01 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4679 | Forss Wind Farm (Extension) | onshore | 0.0052 | GW | 2007-07-01 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4681 | Michelin Tyre Co Ltd - Dundee | onshore | 0.004 | GW | 2006-05-20 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4682 | Millennium Windfarm | onshore | 0.04 | GW | 2008-07-15 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4683 | Muirhall | onshore | 0.0123 | GW | 2011-01-01 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4684 | Mynydd Clogau Wind Farm | onshore | 0.0145 | GW | 2005-12-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4685 | New Barn Farm | onshore | 0.0045 | GW | 2007-02-01 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4686 | North Pickenham | onshore | 0.0144 | GW | 2006-10-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4687 | Paul's Hill and Extension | onshore | 0.065 | GW | 2006-04-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4689 | Tir Mostyn And Foel Goch Wind Farm | onshore | 0.0213 | GW | 2005-06-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4690 | Trimdon Grange | onshore | 0.0052 | GW | 2008-07-10 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4691 | Wardlaw Wood | onshore | 0.018 | GW | 2006-03-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4694 | East Midlands Distribution Centre | solar | 0.0061 | GW | 2015-03-02 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4701 | Land at High Point Farm | solar | 0.0045 | GW | 2017-03-31 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4703 | Land at Newlands Farm | solar | 0.005 | GW | 2016-02-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4705 | Eckland Lodge Farm | solar | 0.0029 | GW | 2016-12-23 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4706 | Caddington Solar Farm (Phase 2) | solar | 0.005 | GW | 2016-03-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4712 | Montys Farm | solar | 0.005 | GW | 2016-03-20 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4713 | Merston Solar Park | solar | 0.01 | GW | 2016-06-28 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4718 | Fambridge Road/Canewdon Road | solar | 0.005 | GW | 2015-11-23 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4721 | Roskrow Farm | solar | 0.0089 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4727 | Hale Farm | solar | 0.008 | GW | 2016-02-26 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4729 | Pylle Southern solar park (Lower Easton Farm) | solar | 0.005 | GW | 2015-12-20 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4734 | Land at Darran Farm | solar | 0.0026 | GW | 2017-03-30 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4736 | Wisbech Solar Farm | solar | 0.0035 | GW | 2015-12-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4738 | Rhug Estate | solar | 0.0012 | GW | 2016-03-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4739 | Snettisham Solar Farm | solar | 0.0027 | GW | 2017-03-28 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4740 | West Hill Farm | solar | 0.0024 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4745 | Cold Harbour Farm | solar | 0.005 | GW | 2015-12-18 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4747 | Southrigg | onshore | 0.0015 | GW | 2016-10-01 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4748 | Land at Whatton Road | solar | 0.0015 | GW | 2015-10-23 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4751 | Upper Wick Solar Farm | solar | 0.005 | GW | 2016-01-18 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4752 | Marshwood Farm | solar | 0.0018 | GW | 2015-06-26 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4753 | House O’Hill Solar Farm | solar | 0.0016 | GW | 2015-12-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4757 | Hawkers Farm | solar | 0.0095 | GW | 2015-03-23 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4761 | Woodtown Farm | solar | 0.0038 | GW | 2015-12-23 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4766 | Land at Tangmere Airfield | solar | 0.005 | GW | 2015-10-07 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4767 | Land at Coton Park Colliery | solar | 0.0025 | GW | 2015-12-21 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4769 | Chapel Farm | solar | 0.005 | GW | 2017-03-31 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4780 | Cairnmore Solar Park | solar | 0.0038 | GW | 2016-02-17 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4783 | Bake Farm Solar Farm | solar | 0.005 | GW | 2016-03-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4785 | Thompson House Equestrian farm | solar | 0.005 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4790 | Kingspan | onshore | 0.0018 | GW | 2019-01-11 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4792 | Red Hill Farm | solar | 0.0048 | GW | 2015-12-09 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4794 | Stoneshill Farm | solar | 0.005 | GW | 2017-03-17 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4804 | Carlam Hill Education CIC | solar | 0.005 | GW | 2016-06-24 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4817 | Binn Eco Park - Wind Farm | onshore | 0.01 | GW | 2020-01-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4825 | Caldecote Manor Farm | solar | 0.005 | GW | 2016-02-24 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4830 | Crundale / Fenton Home Farm (extension) | solar | 0.0059 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4833 | Fieldscale | solar | 0.0106 | GW | 2016-04-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4836 | Iwade Solar Farm | solar | 0.0017 | GW | 2015-03-19 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4838 | Kingsland Barton Solar Farm | solar | 0.005 | GW | 2014-02-22 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4839 | Lee Moor China Clay Works | solar | 0.0095 | GW | 2015-12-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4840 | Littleton | solar | 0.0121 | GW | 2015-03-23 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4841 | Lount solar farm | solar | 0.0028 | GW | 2015-11-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4844 | New Mains Of Guynd Farm | solar | 0.01 | GW | 2016-06-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4846 | Orchard Farm | solar | 0.01 | GW | 2016-02-02 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4850 | Salford Lodge | solar | 0.005 | GW | 2015-08-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4856 | The Grange | solar | 0.008 | GW | 2016-03-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4857 | Thorne Farm | solar | 0.005 | GW | 2015-12-18 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4858 | Tiddiecross Solar Farm | solar | 0.0105 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4859 | Tooleys Farm | solar | 0.0053 | GW | 2015-10-08 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4860 | Trickey Warren | solar | 0.0048 | GW | 2015-04-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4861 | Twemlows | solar | 0.01 | GW | 2015-11-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4862 | Tyddyn Cae (Nefyn) | solar | 0.0049 | GW | 2015-12-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4874 | Abbots Ann | solar | 0.007 | GW | 2015-03-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4878 | Margate Solar Farm | solar | 0.003 | GW | 2015-09-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4880 | Laceby Solar Farm | solar | 0.0271 | GW | 2016-06-22 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4885 | Land East of White Horse Lane | solar | 0.005 | GW | 2016-03-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4887 | Westfield Farm | solar | 0.005 | GW | 2016-01-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4889 | West Woodlands | solar | 0.005 | GW | 2016-03-23 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4891 | Mendennick Farm | solar | 0.0028 | GW | 2015-10-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4892 | Gawnsmoss Cluster | onshore | 0.0024 | GW | 2017-03-27 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4896 | Cockett Valley | solar | 0.004 | GW | 2017-03-29 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4897 | Rampisham North | solar | 0.005 | GW | 2017-03-01 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4899 | Severn Road Solar Park | solar | 0.0018 | GW | 2016-02-05 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4903 | Moorhouse Farm | solar | 0.005 | GW | 2016-11-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4908 | Quarrendon Fields | onshore | 0.0015 | GW | 2014-12-18 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4916 | Land at Sutor Farm | solar | 0.005 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4917 | Newstead and Annesley Wind Turbine | onshore | 0.0015 | GW | 2016-12-01 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4929 | Land North East Of Penrose Far | solar | 0.0015 | GW | 2015-09-25 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4931 | Land At Ferry Farm | solar | 0.01 | GW | 2015-12-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4933 | Land at Brookbarn Farm | solar | 0.003 | GW | 2015-10-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4935 | Field at School Aycliffe Lane | solar | 0.005 | GW | 2015-12-16 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4936 | Capel Grange Solar Park | solar | 0.0066 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4938 | Pentre farm | solar | 0.0055 | GW | 2014-09-25 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4939 | Land At Rymes Farm (Phase 1) | solar | 0.0069 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4940 | Llancadle Farm | solar | 0.005 | GW | 2015-12-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4943 | Land At Rymes Farm (Phase 2)/Grange Solar Farm | solar | 0.0068 | GW | 2015-11-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4948 | Trowle Common | solar | 0.005 | GW | 2016-02-02 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4951 | Canopus Farm | solar | 0.005 | GW | 2015-12-10 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4952 | Land At Guston Court Farm | solar | 0.005 | GW | 2015-12-20 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4969 | Pressock Farm | solar | 0.005 | GW | 2017-03-28 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4976 | Beckton Sewage Treatment Works | onshore | 0.0022 | GW | 2014-11-12 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4983 | Rufford Lane | solar | 0.0026 | GW | 2016-06-17 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4986 | Land to the north and south of Cakers Lane (Wilsom) | solar | 0.011 | GW | 2017-03-20 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4988 | Kirk Hill Wind Farm | onshore | 0.0188 | GW | 2024-05-01 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4990 | Collacott Farm | solar | 0.0045 | GW | 2016-03-22 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4994 | Tonedale Farm | solar | 0.005 | GW | 2015-12-10 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4995 | Melton Waste Park | onshore | 0.005 | GW | 2017-03-01 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4996 | Lindridge Farm | solar | 0.005 | GW | 2015-12-21 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-4997 | Abbots Ripton Solar Farm (ext.) | solar | 0.0039 | GW | 2015-12-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5001 | Fleetwood Water Treatment Works | solar | 0.0013 | GW | 2015-03-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5002 | Triangle Solar Farm Park | solar | 0.012 | GW | 2017-01-04 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5006 | Land at Lower House Farm | solar | 0.0081 | GW | 2016-03-21 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5012 | Aldi Distribution Centre | solar | 0.0013 | GW | 2015-10-22 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5014 | Bromfield Sand and Gravel | solar | 0.0005 | GW | 2017-08-25 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5015 | Land at Heywood Grange | solar | 0.0084 | GW | 2016-10-19 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5017 | Ravens Close | solar | 0.005 | GW | 2017-03-14 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5018 | Forest Farm | solar | 0.003 | GW | 2017-03-01 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5019 | Land West of Roberts Wall Far | solar | 0.0025 | GW | 2016-03-23 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5020 | Drayton Manor Farm | solar | 0.025 | GW | 2016-03-23 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5022 | Somersal Mill Farm | solar | 0.0026 | GW | 2016-03-23 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5026 | Land Opposite Tyn Y Pistyll | solar | 0.005 | GW | 2015-12-22 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5033 | Land South of Highfield House | solar | 0.005 | GW | 2016-03-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5053 | Rhewl Farm | solar | 0.006 | GW | 2016-06-26 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5063 | Land at Dayfields Farm | solar | 0.0047 | GW | 2016-12-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5071 | MMD Shipping Services | solar | 0.0012 | GW | 2015-03-09 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5079 | Newton Margate | solar | 0.0015 | GW | 2015-10-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5080 | Eveley Farm | solar | 0.049 | GW | 2016-03-17 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5084 | Court Farm | solar | 0.0085 | GW | 2017-03-30 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5089 | Green Farm | solar | 0.005 | GW | 2015-12-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5090 | Home Farm | solar | 0.0067 | GW | 2017-03-31 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5092 | Land at Thornborough Grounds | solar | 0.005 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5093 | Port of Barry - Site 1 | solar | 0.0045 | GW | 2015-08-18 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5096 | Southern Counties Shooting Ground Phase 1 | solar | 0.009 | GW | 2017-01-06 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5099 | Fanny House Farm | solar | 0.005 | GW | 2015-12-21 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5102 | Chard Solar Park | solar | 0.003 | GW | 2016-03-23 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5104 | Home Farm | solar | 0.003 | GW | 2017-04-15 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5117 | Marshborough Farm solar park | solar | 0.005 | GW | 2015-11-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5118 | Fiskerton Airfield (Phase 2) | solar | 0.022 | GW | 2015-03-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5119 | Langley Priory, Walnut Yard (Phase 2) | solar | 0.0062 | GW | 2016-06-01 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5125 | Bluegates Solar Park | solar | 0.0105 | GW | 2015-01-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5128 | Land To The East Of Back Lane | solar | 0.005 | GW | 2015-09-30 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5131 | Axe View Solar Farm | solar | 0.005 | GW | 2017-03-15 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5132 | Land at Fell View Farm (Phase 1) | solar | 0.0042 | GW | 2016-03-28 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5136 | South of Henley Hall | solar | 0.005 | GW | 2017-03-17 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5137 | Place Barton Farm | solar | 0.0049 | GW | 2017-03-31 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5139 | Lower Stanley Farm | solar | 0.004 | GW | 2016-03-23 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5140 | Land Parcel North of Goddards | solar | 0.005 | GW | 2016-03-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5142 | Ld At Lawrence End Park &, Dane Street | solar | 0.005 | GW | 2015-12-19 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5143 | Gravel Works, Wasing Estate | solar | 0.005 | GW | 2017-03-01 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5145 | Drakelow Solar Farm | solar | 0.005 | GW | 2016-03-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5146 | Land at Five Oaks Farm | solar | 0.005 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5147 | Knolton Farmhouse Cheese Solar Farm | solar | 0.001 | GW | 2016-03-01 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5148 | Blakenhall Park Solar Farm | solar | 0.0018 | GW | 2015-09-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5149 | Grantham Solar Farm | solar | 0.005 | GW | 2015-12-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5150 | Agricultural Land at Trecastle | solar | 0.004 | GW | 2015-12-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5152 | Sharland Solar Farm | solar | 0.0028 | GW | 2017-03-04 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5156 | Short Hazel Solar Farm | solar | 0.005 | GW | 2016-03-02 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5157 | Mill Hill Farm | solar | 0.005 | GW | 2015-12-17 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5158 | Little Irchester, Higham Road Solar Farm | solar | 0.0046 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5162 | Land North of Chiltern Greeen | solar | 0.005 | GW | 2016-03-10 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5163 | Bilsborrow Solar Farm | solar | 0.005 | GW | 2017-03-30 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5164 | Hill Farm | solar | 0.005 | GW | 2017-03-01 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5165 | Padleywood Farm | solar | 0.005 | GW | 2016-03-29 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5167 | Tiln Farm Retford (extension) | solar | 0.0017 | GW | 2015-04-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5168 | Tower Hayes Farm | solar | 0.005 | GW | 2016-05-17 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5169 | Sheriffhales Solar Farm | solar | 0.0082 | GW | 2015-12-16 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5182 | Land Adjacent Claypits Farm (a) | solar | 0.005 | GW | 2015-12-23 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5183 | Land Adjacent Claypits Farm (b) (Birch Estate) | solar | 0.0023 | GW | 2016-02-26 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5187 | Hill of Lybster (Wind Turbine - Extension) | onshore | 0.0015 | GW | 2021-04-12 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5190 | Fferm Bryn Bachau | solar | 0.0044 | GW | 2016-03-29 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5195 | Golticlay Wind Farm | onshore | 0.0726 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-5199 | Scottow Moor - RAF Coltishall Solar Farm (Phase 2) | solar | 0.0179 | GW | 2016-03-29 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5202 | West Carclaze Solar Farm | solar | 0.0065 | GW | 2017-03-29 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5204 | Flixborough Industrial Estate | solar | 0.005 | GW | 2017-03-01 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5207 | Land adjacent to Church Road | solar | 0.0035 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5212 | Lady Hole Farm | solar | 0.003 | GW | 2016-03-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5218 | Land at Christ’s Hospital School | solar | 0.0011 | GW | 2015-12-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5224 | Creswell Solar Park | solar | 0.005 | GW | 2016-03-23 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5225 | Pollington Solar Farm | solar | 0.005 | GW | 2017-03-23 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5226 | Land NW Of Pickhill Bridge Farm | solar | 0.0036 | GW | 2017-03-24 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5229 | Moneystone Quarry Solar Farm | solar | 0.005 | GW | 2016-11-21 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5230 | Pingry Farm - Phase 2 | solar | 0.0034 | GW | 2015-03-25 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5231 | Kenninghall Solar / Hazeldick Solar | solar | 0.008 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5232 | Wogaston Solar Farm | solar | 0.0053 | GW | 2015-03-17 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5233 | Crugmore Farm | solar | 0.0064 | GW | 2015-03-25 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5234 | Rydon Farm | solar | 0.012 | GW | 2015-03-31 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5241 | Solar farm at land at The Willows, Uttoxeter | solar | 0.0064 | GW | 2017-03-31 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5242 | Highwood Lane | solar | 0.005 | GW | 2016-08-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5243 | Yorkley Solar Park | solar | 0.005 | GW | 2015-12-18 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5244 | Solar Farm at Fields Farm (Phase 1) | solar | 0.005 | GW | 2016-03-23 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5253 | Land at Beech Farm | solar | 0.0046 | GW | 2016-02-17 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5255 | West Holcombe | solar | 0.0055 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-5256 | Aberporth Solar Farm | solar | 0.0015 | GW | 2015-03-24 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5257 | Hoplass Farm | solar | 0.01 | GW | 2015-03-13 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5258 | Chelveston Renewable Energy Park - Solar Extension | solar | 0.0195 | GW | 2015-03-20 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5259 | Grove Solar Park (Phase 1) | solar | 0.005 | GW | 2016-03-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5261 | Fell View Farm (Phase 2) | solar | 0.0029 | GW | 2016-03-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5263 | Land At Chiddinglye Farm | solar | 0.005 | GW | 2016-03-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5264 | Land of coal pit lane | solar | 0.005 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5265 | Huntingfield Solar Farm | solar | 0.0044 | GW | 2018-07-15 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5266 | Astley Solar Farm | solar | 0.005 | GW | 2016-03-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5267 | Majors Hill/Turners Hill Solar Farm | solar | 0.0011 | GW | 2016-03-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5271 | Land South Of Bryn Cyrnau Isaf | solar | 0.0059 | GW | 2017-03-31 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5273 | Ashby Solar Farm (a) | solar | 0.005 | GW | 2016-03-12 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5276 | Cirencester Solar Farm | solar | 0.023 | GW | 2022-10-13 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5277 | Burton Wold Wind Farm South | onshore | 0.0075 | GW | 2017-04-24 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5282 | Land South of Knock Lane | solar | 0.004 | GW | 2016-10-01 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5285 | Land south of Brick Kiln Road | solar | 0.005 | GW | 2016-03-17 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5287 | Averhill Farm | solar | 0.005 | GW | 2015-12-16 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5288 | Morton House (Marchington) | solar | 0.0062 | GW | 2016-03-24 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5289 | Biglis Farm | solar | 0.005 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5290 | Milborne Port Solar Farm | solar | 0.0042 | GW | 2018-06-25 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5292 | Land At Cwm Bargoed | solar | 0.005 | GW | 2016-01-20 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5293 | Land South Off Ollerton Road | solar | 0.0042 | GW | 2017-01-15 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5295 | Land At Swanland Road | solar | 0.005 | GW | 2017-03-23 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5296 | Rookery Business Park | solar | 0.005 | GW | 2016-02-11 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5297 | Land North of Sandhutton Lane | solar | 0.005 | GW | 2017-02-15 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5301 | Land West Of Hunger Hill Farm | solar | 0.005 | GW | 2017-02-15 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5302 | Land East Of Honeysome Road | solar | 0.0046 | GW | 2016-03-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5303 | Salford Road Solar Farm | solar | 0.0022 | GW | 2015-08-09 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5305 | Ld NW Of Ratcliffe House Farm | solar | 0.0035 | GW | 2015-12-21 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5309 | Land at Woodhouse Farm | solar | 0.005 | GW | 2016-03-24 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5310 | Parklands | solar | 0.0046 | GW | 2016-02-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5312 | Amcor Flexibles | solar | 0.0017 | GW | 2015-11-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5315 | Waterditch Solar Farm | solar | 0.018 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5316 | Land Off Ingarsby Lane | solar | 0.0021 | GW | 2016-06-05 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5320 | Nissan Test Track | solar | 0.0048 | GW | 2016-03-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5321 | Cooper House Farm | solar | 0.005 | GW | 2016-03-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5322 | Land at Pollington Airfield | solar | 0.005 | GW | 2015-12-21 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5324 | Land at Poles Hole Farm | solar | 0.0068 | GW | 2017-03-01 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5328 | Staining Wood Farm | solar | 0.0049 | GW | 2016-03-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5330 | Land between Orton Park Farm | solar | 0.0064 | GW | 2016-03-29 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5332 | Site To North East Of, Lochcraigs Farm | solar | 0.005 | GW | 2017-03-31 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5333 | West Mains of Kinblethmont | solar | 0.005 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5336 | Land West Side of Axe and Cleaver Lane | solar | 0.005 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5340 | Land To The North Of Moor Farm | solar | 0.0038 | GW | 2017-03-11 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5342 | Henley Solar Farm | solar | 0.0065 | GW | 2017-03-29 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5357 | Crown Farm | solar | 0.006 | GW | 2017-03-01 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5359 | Eaglescliffe Solar Farm | solar | 0.005 | GW | 2017-03-28 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5360 | Tyddyn Gwyn (Gelli Gron Farm) | solar | 0.0038 | GW | 2016-11-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5368 | Thornton Lane | solar | 0.0027 | GW | 2016-03-23 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5371 | Aborfield Solar Park | solar | 0.014 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-5376 | Penycae Solar Farm | solar | 0.005 | GW | 2016-03-28 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5377 | Land at Ingles Hill Farm | solar | 0.003 | GW | 2016-04-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5379 | Southbrook Solar Farm | solar | 0.005 | GW | 2016-05-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5380 | Green Croft Solar Farm | solar | 0.005 | GW | 2016-12-07 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5381 | Upper Pant-Ysgawen Farm/Crumlin | solar | 0.0049 | GW | 2016-12-07 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5383 | Land at Oxcroft Stocking Ground | solar | 0.004 | GW | 2016-03-25 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5384 | West Strathore Solar Limited | solar | 0.005 | GW | 2017-03-30 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5385 | Land at Meadow Farm | solar | 0.005 | GW | 2017-03-10 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5387 | Hungerford Farm | solar | 0.005 | GW | 2016-08-22 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5389 | Land at Morfa Camp | solar | 0.0028 | GW | 2016-03-20 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5391 | Land South of Pogmore Spinney | solar | 0.005 | GW | 2017-03-30 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5393 | Douglas West and Dalquhandy Renewable Energy Project | onshore | 0.045 | GW | 2023-01-01 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5394 | Abbey Fields Farm | solar | 0.0053 | GW | 2016-03-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5395 | Ernesettle Solar Farm | solar | 0.0041 | GW | 2016-03-23 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5396 | SPF Thirty Acres Farm | solar | 0.0038 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5398 | Killan Farm Solar Array Extens | solar | 0.001 | GW | 2017-05-20 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5400 | Land East of Appleton Farm | solar | 0.005 | GW | 2016-03-27 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5401 | Land At Debdale Lane | solar | 0.005 | GW | 2016-03-25 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5402 | Land at Ash Row Farm | solar | 0.005 | GW | 2015-12-21 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5403 | Land at Stripe Farm | solar | 0.005 | GW | 2016-03-28 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5404 | Land at Bolsover Moor Quarry | solar | 0.005 | GW | 2017-03-01 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5406 | Land To The North Of Dairy House Farm | solar | 0.0034 | GW | 2016-02-27 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5407 | Pennington Recycling Centre | solar | 0.0012 | GW | 2016-03-20 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5411 | Goosehall Solar Farm | solar | 0.0395 | GW | 2020-08-18 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5412 | Land west of Welton Road | solar | 0.0044 | GW | 2016-03-29 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5415 | Twin Yards Solar Farm | solar | 0.005 | GW | 2017-03-20 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5420 | Hull Solar Farm | solar | 0.0257 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-5424 | Land of Green Lane | solar | 0.0058 | GW | 2017-03-31 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5425 | Land At Actrees Farm | solar | 0.005 | GW | 2016-01-28 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5428 | Land at Bowden Lane | solar | 0.005 | GW | 2017-03-31 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5429 | Land at Stalbridge Park | solar | 0.005 | GW | 2017-03-31 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5430 | Frog's Loke Solar Farm | solar | 0.005 | GW | 2016-01-12 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5431 | Staughton Airfield Solar Farm | solar | 0.04 | GW | 2020-03-01 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5437 | Manmoel Road Solar Park | solar | 0.0041 | GW | 2017-03-30 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5440 | Huntspill Level Solar Park | solar | 0.0055 | GW | 2016-03-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5442 | Land at Box Road | solar | 0.0022 | GW | 2016-03-24 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5444 | Low Farm Solar Array | solar | 0.02 | GW | 2022-10-01 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5447 | Land south of Wood Lane (Safeguard Bradwell) | solar | 0.005 | GW | 2017-01-15 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5451 | Newton Downs Farm | solar | 0.005 | GW | 2017-02-15 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5453 | Bunn's Hill Solar Park | solar | 0.005 | GW | 2016-02-03 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5455 | Cumberhead Wind Farm | onshore | 0.048 | GW | 2023-09-11 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5465 | Rushmoor Lane Farm (Cheshire Coppice) | solar | 0.005 | GW | 2016-01-28 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5472 | Fullenton Solar Farm | solar | 0.0042 | GW | 2016-12-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5477 | Cwm Derwyn Farm | solar | 0.005 | GW | 2017-03-17 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5478 | Land to the west of Ashfordby Business Park | solar | 0.0035 | GW | 2016-04-26 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5480 | Glebe Farm Solar Farm | solar | 0.032 | GW | 2021-03-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5482 | York Solar Farm | solar | 0.0347 | GW | 2019-12-18 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5483 | Land Off Folly Lane | solar | 0.005 | GW | 2016-03-07 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5485 | Land At Bake Farm | solar | 0.005 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5486 | Land To The South Of Todderstaffe | solar | 0.0045 | GW | 2017-03-28 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5487 | Strettington Solar Farm | solar | 0.005 | GW | 2016-03-23 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5497 | Cressing Solar Farm (Phase 1) | solar | 0.005 | GW | 2016-03-16 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5498 | Land north of Ashton Road | solar | 0.004 | GW | 2017-03-24 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5499 | Parc Cynog | solar | 0.005 | GW | 2016-03-24 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5506 | Albrighton Solar farm | solar | 0.0158 | GW | 2017-02-28 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5508 | Clapton Farm Solar Park | solar | 0.005 | GW | 2017-03-31 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5512 | Galton Manor Solar Park | solar | 0.005 | GW | 2017-03-31 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5513 | Wormit Solar Farm | solar | 0.004 | GW | 2017-03-31 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5520 | The Breck | solar | 0.005 | GW | 2016-03-17 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5523 | North Tenement | solar | 0.005 | GW | 2017-03-28 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5524 | Cwrt Henllys Farm | solar | 0.005 | GW | 2016-12-29 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5525 | Land at Wreay | solar | 0.005 | GW | 2017-03-29 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5527 | Common Farm | solar | 0.0048 | GW | 2016-06-29 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5529 | Fields Farm (Agden) | solar | 0.005 | GW | 2017-02-09 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5530 | Land at Hill Farm | solar | 0.0012 | GW | 2016-11-01 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5531 | Land to North West of Lodge Farm (Park Farm) | solar | 0.004 | GW | 2017-03-03 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5532 | Seaton Road Solar Farm | solar | 0.004 | GW | 2017-03-31 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5534 | Land at Tip Field | solar | 0.005 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-5536 | Wick Lane Solar Ltd | solar | 0.0028 | GW | 2017-03-20 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5538 | Otherton Farm | solar | 0.004 | GW | 2017-03-21 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5540 | Nanthenfoel Farms | solar | 0.005 | GW | 2017-03-15 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5543 | New Road Solar Farm | solar | 0.005 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-5545 | Land at Green Farm | solar | 0.001 | GW | 2016-06-21 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5547 | West Venn Solar Farm | solar | 0.005 | GW | 2017-03-13 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5548 | Corntown Farm | solar | 0.0034 | GW | 2017-03-15 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5551 | Wally Corner Landfill Site | solar | 0.007 | GW | 2017-03-15 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5554 | Land North of the Wood at Averill Farm | solar | 0.005 | GW | 2016-03-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5555 | ANP Newport Wind Turbine | onshore | 0.0023 | GW | 2016-08-15 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5559 | Sudforth Lane (Kellingley Solar Farm) | solar | 0.005 | GW | 2017-03-30 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5560 | Berthlwyd Farm | solar | 0.005 | GW | 2017-02-15 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5562 | Pinguin Foods | solar | 0.0015 | GW | 2016-03-23 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5568 | Land East of Lawn Lane | solar | 0.005 | GW | 2016-03-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5572 | Land off Ford Lane | solar | 0.0047 | GW | 2016-11-17 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5577 | Woodhouse Fields Farm | solar | 0.005 | GW | 2017-02-10 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5578 | Land off Hooklands Lane | solar | 0.005 | GW | 2016-03-26 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5581 | High Dyke (Mill Farm) | solar | 0.005 | GW | 2016-03-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5582 | Land West of Parsonage Wood | solar | 0.0042 | GW | 2016-01-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5588 | Land at Oldstone Farm | solar | 0.005 | GW | 2017-03-31 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5590 | Shortheath Solar Park | solar | 0.005 | GW | 2017-03-31 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5591 | Land at Oxcroft Stocking Ground | solar | 0.003 | GW | 2016-03-20 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5592 | Holtwood Farm | solar | 0.005 | GW | 2016-03-10 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5593 | Carn Nicholas Farm | solar | 0.005 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-5596 | Nectar Way Regional Distribution Centre | solar | 0.001 | GW | 2015-06-12 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5598 | Brenig Wind Farm | onshore | 0.0376 | GW | 2018-10-15 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5599 | Gib Lane Solar farm (Extension) | solar | 0.005 | GW | 2016-03-22 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5600 | Land east of Littledown Business Park | solar | 0.0062 | GW | 2016-03-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5602 | Lyreco - Telford Distribution Centre | solar | 0.0038 | GW | 2016-01-26 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5603 | Long Lane Solar Farm / Nottingham Brick Works | solar | 0.017 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-5605 | Port of Barry - Site 2 | solar | 0.005 | GW | 2015-04-16 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5632 | Holly Farm Solar Park | solar | 0.005 | GW | 2017-03-31 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5633 | Worsted Farm | solar | 0.005 | GW | 2019-04-16 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5637 | Pogbie Wind Farm 2 | onshore | 0.0048 | GW | 2019-03-01 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5643 | Basin Bridge Farm | solar | 0.005 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5650 | Land at East Farm | solar | 0.005 | GW | 2017-03-31 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5653 | B&Q Swindon DC | solar | 0.0025 | GW | 2016-01-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5654 | Stragglethorpe Road farm | solar | 0.005 | GW | 2016-03-29 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5656 | Land at Bluehouse Farm | solar | 0.005 | GW | 2016-08-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5659 | Stokeford Farm | solar | 0.0285 | GW | 2024-07-31 | 2054-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5660 | Potters Bar Solar Farm | solar | 0.005 | GW | 2017-03-28 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5664 | Stob House Farm | solar | 0.0049 | GW | 2016-09-01 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5670 | Granville Road Solar Farm | solar | 0.005 | GW | 2016-10-24 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5683 | Mamhilad Solar Farm | solar | 0.005 | GW | 2020-02-12 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5685 | Hyde Farm | solar | 0.005 | GW | 2017-03-16 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5686 | Lower Venn Farm | solar | 0.005 | GW | 2016-03-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5687 | Littlewood Lane Solar | solar | 0.005 | GW | 2017-03-30 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5694 | Peterlee Solar Farm | solar | 0.005 | GW | 2016-03-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5712 | Land On The East Side Of Fosse Way | solar | 0.01 | GW | 2017-03-31 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5720 | Briar Solar Farm | solar | 0.0019 | GW | 2017-03-20 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5723 | Bent Spur Solar Farm | solar | 0.005 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5735 | Blaby Solar Farm | solar | 0.0035 | GW | 2016-03-29 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5742 | Bilsthorpe (Land off Forest Lane) | solar | 0.005 | GW | 2017-03-15 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5756 | Godley Water Treatment Works | solar | 0.003 | GW | 2016-04-22 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5786 | Park Farm | solar | 0.005 | GW | 2016-03-24 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5793 | Greaves Solar Farm | solar | 0.005 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5795 | Balhearty Solar | solar | 0.005 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5796 | Weddington Farm | solar | 0.0021 | GW | 2016-10-28 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5797 | Middle Balbeggie | solar | 0.005 | GW | 2017-01-27 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5824 | Widehurst Farm | solar | 0.005 | GW | 2017-03-15 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5828 | Screwfix Direct | solar | 0.0025 | GW | 2016-01-12 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5829 | Land at Biggin Lane | solar | 0.005 | GW | 2016-03-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5832 | Land at Barnham | solar | 0.001 | GW | 2017-02-20 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5834 | Ebnal Lodge | solar | 0.005 | GW | 2017-02-15 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5835 | Southill Solar | solar | 0.0045 | GW | 2016-11-14 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5838 | Carver Hay, moss lane | solar | 0.0025 | GW | 2017-03-20 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5844 | Hownsgill Industrial Park | solar | 0.005 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-5845 | Bruxiehall Farm | solar | 0.002 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-5848 | St Helen's Lane | solar | 0.005 | GW | 2017-03-28 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5864 | Avonmouth | solar | 0.0042 | GW | 2016-06-28 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5866 | Newport (Began Road) | solar | 0.0049 | GW | 2016-02-14 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5880 | Land to the south of Hill Farm | solar | 0.0068 | GW | 2017-03-31 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5883 | Woodington Solar Farm | solar | 0.046 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-5887 | Mill Farm | solar | 0.005 | GW | 2016-12-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5891 | Southern Counties Shooting Ground Phase 2 | solar | 0.005 | GW | 2017-02-02 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5914 | Parkhill Solar Farm | solar | 0.005 | GW | 2018-11-01 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5917 | Dura Park Bynea Industrial Site | solar | 0.0014 | GW | 2015-12-21 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5926 | Brook Hall Farm | solar | 0.0047 | GW | 2016-03-21 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5928 | Land off Moss Side Lane | solar | 0.005 | GW | 2017-03-31 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5938 | Jemmys Carr | solar | 0.005 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-5942 | Barvills Solar Farm | solar | 0.005 | GW | 2017-03-29 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5945 | Cairnmore Solar Park (extension) | solar | 0.0012 | GW | 2015-09-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5946 | London Southend Airport | solar | 0.0025 | GW | 2016-01-12 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-5985 | Thameside DC | solar | 0.001 | GW | 2016-01-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6005 | Limekiln Wind Farm | onshore | 0.0798 | GW | 2025-04-01 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6013 | Parc Stormy, Stormy Down | onshore | 0.0025 | GW | 2018-01-01 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Missing operational date estimated2018. | data/evidence/repd.csv
REPD-6019 | Moss Thorn Farm | solar | 0.0058 | GW | 2017-02-27 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6033 | Bodtegir | onshore | 0.0015 | GW | 2017-11-01 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6035 | Caergarw Farm | solar | 0.0038 | GW | 2017-03-20 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6042 | Rolls Royce Filton Campus Building 184 | solar | 0.0014 | GW | 2016-08-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6043 | Rolls Royce Filton Campus Building 185 | solar | 0.0018 | GW | 2016-08-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6055 | ParkerSteel Shoreham Plant | solar | 0.0018 | GW | 2015-09-02 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6062 | Bourne Farm | solar | 0.0024 | GW | 2015-03-15 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6069 | Barnfield Solar Park | solar | 0.0025 | GW | 2018-12-10 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6071 | Porth Wen | solar | 0.0499 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-6079 | West of Rhiwfelin Fach Farm | onshore | 0.0015 | GW | 2018-08-31 | 2043-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6106 | Marshill Farm | onshore | 0.0015 | GW | 2015-08-01 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6108 | Popehill Farm | solar | 0.005 | GW | 2017-03-29 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6114 | Waltham Point Distribution Centre | solar | 0.0018 | GW | 2016-02-05 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6120 | Checkley Wood Farm | onshore | 0.0041 | GW | 2024-01-20 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6129 | Knottingley B | solar | 0.0024 | GW | 2016-03-29 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6132 | Western International Market | solar | 0.0017 | GW | 2016-05-19 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6133 | Land East of Horton Road | solar | 0.0049 | GW | 2017-07-07 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6136 | Kincardine Offshore Windfarm | offshore | 0.0495 | GW | 2021-10-19 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6147 | Pines Burn Wind Farm | onshore | 0.0336 | GW | 2024-10-01 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6158 | Moray West Offshore Wind Farm Project | offshore | 0.882 | GW | 2025-04-01 | 2055-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6162 | Salford Road | solar | 0.0016 | GW | 2016-06-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6163 | Grove Solar Park (Phase 2) | solar | 0.011 | GW | 2016-03-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6172 | Williams Farm | solar | 0.005 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6173 | Woodlands Wind Farm | onshore | 0.0026 | GW | 2016-07-28 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6174 | Kirton Solar PV Farm | solar | 0.0032 | GW | 2016-03-30 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6180 | Bury Green Farm Solar | solar | 0.005 | GW | 2016-03-15 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6181 | Misson Solar Farm | solar | 0.005 | GW | 2016-03-24 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6189 | Lancaster Wastewater Treatment Works | solar | 0.0012 | GW | 2016-04-07 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6198 | Whitman Laboratories | solar | 0.001 | GW | 2017-10-18 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6205 | Binsted Farm | solar | 0.005 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6214 | Howpark Wind Farm | onshore | 0.016 | GW | 2024-01-01 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6230 | Oakfield Farm | solar | 0.005 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6231 | Oakfield Farm - extension | solar | 0.0017 | GW | 2016-03-31 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6244 | Former Westhampnett Landfill | solar | 0.0075 | GW | 2018-10-25 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6246 | Bentley Motors | solar | 0.0029 | GW | 2018-08-01 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6248 | Ingham North Solar | solar | 0.0142 | GW | 2021-03-23 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6264 | Dounreay Trì Floating Wind Demonstration | offshore | 0.01 | GW | 2030-01-01 | 2060-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2030-01-01. | data/evidence/repd.csv
REPD-6293 | Accolade Wines | onshore | 0.0025 | GW | 2019-06-15 | 2044-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6314 | DPD Distribution Centre | solar | 0.001 | GW | 2017-01-10 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6318 | Craigannet Farm Wind Turbine | onshore | 0.0015 | GW | 2017-03-31 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6320 | Bywaters’ Materials Recovery Facility Solar Array | solar | 0.001 | GW | 2017-01-24 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6321 | High Meadow Farm | solar | 0.004 | GW | 2016-10-18 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6324 | Burnfoot East Wind Farm (further extension) | onshore | 0.0108 | GW | 2020-07-01 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6327 | Longhill Burn Wind Farm | onshore | 0.0456 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-6328 | Deep Moor Landfill Site | solar | 0.002 | GW | 2018-04-20 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6329 | Testwood Water Supply Works | solar | 0.0019 | GW | 2017-08-24 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6363 | Priestgill Wind Farm | onshore | 0.0462 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-6369 | Rosedew Farm | solar | 0.005 | GW | 2016-03-29 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6376 | Dengemarsh Road | solar | 0.001 | GW | 2016-12-14 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6378 | Former Nant-y-Gwyddon Landfill Site | onshore | 0.0015 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-6388 | Ferneylea Farm | onshore | 0.0015 | GW | 2015-01-01 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6402 | Haigh Hall Solar Farm | solar | 0.005 | GW | 2017-02-01 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6403 | Next Distribution Centre Doncaster | solar | 0.0025 | GW | 2016-12-01 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6411 | Llanwern Solar Farm & Battery Storage | solar | 0.075 | GW | 2021-03-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6422 | Graig Fatha Farm | onshore | 0.0025 | GW | 2021-12-01 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6456 | Branston Solar Park (extension) | solar | 0.04 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-6458 | Sytchwythy Fields | solar | 0.0014 | GW | 2017-03-31 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6466 | Clifton Marsh Wastewater Treatment Works | solar | 0.0013 | GW | 2019-08-22 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6483 | The East Anglia Array - Norfolk Boreas | offshore | 1.4 | GW | 2030-01-01 | 2060-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2030-01-01. | data/evidence/repd.csv
REPD-6484 | Ling Hall | solar | 0.007 | GW | 2021-05-05 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6485 | Sherburn | solar | 0.005 | GW | 2016-01-20 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6486 | Aldi - Cardiff | solar | 0.0015 | GW | 2016-04-01 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6493 | Oak Grove Farm | solar | 0.0057 | GW | 2017-03-30 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6501 | Race Bank (Phase 2) | offshore | 0.2835 | GW | 2018-02-01 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6502 | Cleve Hill Solar Project | solar | 0.373 | GW | 2025-07-01 | 2055-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6509 | Longlands Farm, Rush Wall Lane | onshore | 0.0035 | GW | 2021-01-01 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6513 | Lathom (Pilkington Technical Centre) | solar | 0.0025 | GW | 2019-04-16 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6520 | Stormy Down Solar Farm | solar | 0.0038 | GW | 2017-03-27 | 2047-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6523 | Clifton Marsh Wastewater Treatment Works | solar | 0.0032 | GW | 2019-08-22 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6530 | White Cross Lane | solar | 0.025 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-6532 | Huntington Water Treatment Works | solar | 0.0072 | GW | 2019-07-24 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6556 | Sofia (Teesside B) | offshore | 1.4 | GW | 2030-01-01 | 2060-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2030-01-01. | data/evidence/repd.csv
REPD-6560 | Former St Michaels Golf Course | solar | 0.001 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-6590 | Twentyshilling Hill Wind Farm | onshore | 0.0378 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-6591 | Creacombe Solar Farm | solar | 0.0073 | GW | 2020-01-01 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6603 | Cranfield Airfield | solar | 0.001 | GW | 2018-09-01 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6607 | North Kyle Energy Project | onshore | 0.2058 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-6629 | Sanquhar 2 Community Wind Farm | onshore | 0.308 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-6636 | Forss Wind Farm | onshore | 0.0026 | GW | 2003-07-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6660 | Lamby Way Solar Farm | solar | 0.0089 | GW | 2020-05-01 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6683 | Chamber 16 (Cold Store) | solar | 0.0012 | GW | 2016-06-07 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6700 | Terriers Farm | solar | 0.044 | GW | 2022-02-01 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6701 | Gorse Lane | solar | 0.02 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-6703 | Sandy Knowe Wind Farm | onshore | 0.0816 | GW | 2023-02-18 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6708 | Broken Cross (Former Surface Mine) | onshore | 0.048 | GW | 2024-10-01 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6716 | Saputo Dairy UK | solar | 0.0042 | GW | 2022-03-31 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6720 | Swinford Wind Farm | solar | 0.02 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-6723 | Tilbury LCY2 | solar | 0.004 | GW | 2019-01-01 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6726 | Dunfermline EDI4 | solar | 0.0019 | GW | 2019-01-01 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6736 | Bilbo Solar Farm | solar | 0.0366 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-6742 | Building F, Renishaw Factory | solar | 0.0002 | GW | 2020-04-01 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6745 | Finmont Service Reservoir | solar | 0.0003 | GW | 2020-07-23 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6748 | Lower Farm | solar | 0.0005 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-6752 | Renishaw PLC Factory | solar | 0.0008 | GW | 2020-04-01 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6759 | Burneside Mill | solar | 0.0005 | GW | 2019-11-01 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6761 | Leeways | solar | 0.0005 | GW | 2019-07-01 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6762 | Field north of Water Treatment Works / Hoggs Drove | solar | 0.001 | GW | 2021-07-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6766 | Pretoria Road | solar | 0.0049 | GW | 2020-01-29 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6768 | Bolton Hill WTW | solar | 0.0005 | GW | 2020-07-01 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6798 | Arecleoch Wind Farm (extension) | onshore | 0.0728 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-6816 | Moog Controls Factory | solar | 0.00038 | GW | 2019-09-13 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6818 | Lower Tregeen, Davidstow - Wind Turbine | onshore | 0.0009 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-6826 | Douglas West Wind Farm (extension) | onshore | 0.078 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-6828 | Viking Wind Farm | onshore | 0.443 | GW | 2024-09-01 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6834 | Carn Nicholas Farm (Extension) | solar | 0.01 | GW | 2023-01-01 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6846 | EPSRC Willenhall | storage_power | 0.002 | GW | 2014-09-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6846-energy | EPSRC Willenhall | storage_energy | 0.0037238 | GWh | 2014-09-01 | 2031-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6852 | Isle of Eigg Electrification Project | storage_power | 0.0001 | GW | 2008-06-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6852-energy | Isle of Eigg Electrification Project | storage_energy | 0.00018619 | GWh | 2008-06-01 | 2031-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6855 | Northern Isles New Energy Solution (NINES) 1 | storage_power | 0.001 | GW | 2014-02-15 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6855-energy | Northern Isles New Energy Solution (NINES) 1 | storage_energy | 0.0018619 | GWh | 2014-02-15 | 2031-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6856 | Rise Carr, Darlington / CLNR EES3-1 | storage_power | 0.0025 | GW | 2014-06-05 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6856-energy | Rise Carr, Darlington / CLNR EES3-1 | storage_energy | 0.0046548 | GWh | 2014-06-05 | 2031-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6862 | Orkney Storage Park Project | storage_power | 0.002 | GW | 2013-06-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6862-energy | Orkney Storage Park Project | storage_energy | 0.0037238 | GWh | 2013-06-01 | 2031-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6864 | Falcon Project | storage_power | 0.0003 | GW | 2013-12-11 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6864-energy | Falcon Project | storage_energy | 0.00055857 | GWh | 2013-12-11 | 2031-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6866 | Slepe Farm | storage_power | 0.0003 | GW | 2014-10-10 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6866-energy | Slepe Farm | storage_energy | 0.00055857 | GWh | 2014-10-10 | 2031-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6869 | Willersey solar farm | storage_power | 0.001 | GW | 2019-02-01 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6869-energy | Willersey solar farm | storage_energy | 0.0018619 | GWh | 2019-02-01 | 2034-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6879 | Limberlost Solar Farm | storage_power | 0.0003 | GW | 2015-12-11 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6879-energy | Limberlost Solar Farm | storage_energy | 0.00055857 | GWh | 2015-12-11 | 2031-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6881 | Higher Hill Farm Energy Storage | storage_power | 0.0003 | GW | 2016-09-12 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6881-energy | Higher Hill Farm Energy Storage | storage_energy | 0.00055857 | GWh | 2016-09-12 | 2031-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6883 | The Everest System | storage_power | 0.0001 | GW | 2016-01-19 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6883-energy | The Everest System | storage_energy | 0.00018619 | GWh | 2016-01-19 | 2031-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6884 | Hywind 2 | storage_power | 0.001 | GW | 2018-11-20 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6884-energy | Hywind 2 | storage_energy | 0.0018619 | GWh | 2018-11-20 | 2033-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6885 | Oxcroft Solar Farm | storage_power | 0.001 | GW | 2017-12-01 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6885-energy | Oxcroft Solar Farm | storage_energy | 0.0018619 | GWh | 2017-12-01 | 2032-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6886 | Western International Market (WIM) Site | storage_power | 0.0002 | GW | 2016-05-24 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6886-energy | Western International Market (WIM) Site | storage_energy | 0.00037238 | GWh | 2016-05-24 | 2031-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6888 | Salcey Solar Farm | storage_power | 0.001 | GW | 2017-12-01 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6888-energy | Salcey Solar Farm | storage_energy | 0.0018619 | GWh | 2017-12-01 | 2032-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6892 | Cleveland Potash | storage_power | 0.006 | GW | 2017-10-01 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6892-energy | Cleveland Potash | storage_energy | 0.011171 | GWh | 2017-10-01 | 2032-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6897 | JB Wheaton | storage_power | 0.0088 | GW | 2016-08-08 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6897-energy | JB Wheaton | storage_energy | 0.016385 | GWh | 2016-08-08 | 2031-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6898 | Pelham | storage_power | 0.049 | GW | 2017-06-15 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6898-energy | Pelham | storage_energy | 0.091233 | GWh | 2017-06-15 | 2032-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6900 | Berry Court Solar Farm - energy storage | storage_power | 0.001 | GW | 2017-12-01 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6900-energy | Berry Court Solar Farm - energy storage | storage_energy | 0.0018619 | GWh | 2017-12-01 | 2032-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6906 | Blackburn Meadows | storage_power | 0.01 | GW | 2017-10-09 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6906-energy | Blackburn Meadows | storage_energy | 0.018619 | GWh | 2017-10-09 | 2032-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6909 | Dorking Battery Energy Storage System | storage_power | 0.006 | GW | 2020-07-31 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6909-energy | Dorking Battery Energy Storage System | storage_energy | 0.011171 | GWh | 2020-07-31 | 2035-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6910 | Broxburn | storage_power | 0.02 | GW | 2018-09-15 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6910-energy | Broxburn | storage_energy | 0.037238 | GWh | 2018-09-15 | 2033-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6911 | Land to the west of Clay Hill Pit / Larport Farm | storage_power | 0.02 | GW | 2020-01-01 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6911-energy | Land to the west of Clay Hill Pit / Larport Farm | storage_energy | 0.037238 | GWh | 2020-01-01 | 2035-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6912 | Roosecote | storage_power | 0.049 | GW | 2018-11-30 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6912-energy | Roosecote | storage_energy | 0.091233 | GWh | 2018-11-30 | 2033-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6913 | Bumpers Lane Solar Farm | storage_power | 0.0133 | GW | 2020-03-16 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6913-energy | Bumpers Lane Solar Farm | storage_energy | 0.024763 | GWh | 2020-03-16 | 2035-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6915 | Hill Farm - Energy Barn | storage_power | 0.01 | GW | 2017-03-31 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6915-energy | Hill Farm - Energy Barn | storage_energy | 0.018619 | GWh | 2017-03-31 | 2032-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6916 | Kings Barn Farm - Energy Barn | storage_power | 0.01 | GW | 2017-03-31 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6916-energy | Kings Barn Farm - Energy Barn | storage_energy | 0.018619 | GWh | 2017-03-31 | 2032-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6917 | Leverton Farm - Energy Barn | storage_power | 0.01 | GW | 2018-01-01 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6917-energy | Leverton Farm - Energy Barn | storage_energy | 0.018619 | GWh | 2018-01-01 | 2033-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Missing operational date estimated2018. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6918 | Noriker Power Staunch | storage_power | 0.02 | GW | 2017-03-15 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6918-energy | Noriker Power Staunch | storage_energy | 0.037238 | GWh | 2017-03-15 | 2032-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6920 | West Burton | storage_power | 0.049 | GW | 2018-06-25 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6920-energy | West Burton | storage_energy | 0.091233 | GWh | 2018-06-25 | 2033-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6925 | Tynemouth Energy Storage System (TESS) | storage_power | 0.025 | GW | 2018-05-25 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6925-energy | Tynemouth Energy Storage System (TESS) | storage_energy | 0.046548 | GWh | 2018-05-25 | 2033-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6926 | Nevendon | storage_power | 0.01 | GW | 2018-03-15 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6926-energy | Nevendon | storage_energy | 0.018619 | GWh | 2018-03-15 | 2033-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6927 | Pen y Cymoedd Energy Storage | storage_power | 0.022 | GW | 2018-05-01 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6927-energy | Pen y Cymoedd Energy Storage | storage_energy | 0.040962 | GWh | 2018-05-01 | 2033-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6929 | Traston Road | storage_power | 0.02 | GW | 2026-01-14 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6929-energy | Traston Road | storage_energy | 0.037238 | GWh | 2026-01-14 | 2041-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6932 | Asfordby Business Park (1) | storage_power | 0.0234 | GW | 2019-04-01 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6932-energy | Asfordby Business Park (1) | storage_energy | 0.043568 | GWh | 2019-04-01 | 2034-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6941 | Chelveston Renewable Energy Park | storage_power | 0.02 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-6941-energy | Chelveston Renewable Energy Park | storage_energy | 0.037238 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6943 | Ray Battery Storage Facility | storage_power | 0.02 | GW | 2022-10-01 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6943-energy | Ray Battery Storage Facility | storage_energy | 0.037238 | GWh | 2022-10-01 | 2037-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6945 | Claredown Farm | storage_power | 0.02 | GW | 2018-02-27 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6945-energy | Claredown Farm | storage_energy | 0.037238 | GWh | 2018-02-27 | 2033-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6953 | Melksham Substation East Storage | storage_power | 0.05 | GW | 2022-11-07 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6953-energy | Melksham Substation East Storage | storage_energy | 0.093095 | GWh | 2022-11-07 | 2037-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6961 | Lockleaze Energy Storage | storage_power | 0.015 | GW | 2017-12-01 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6961-energy | Lockleaze Energy Storage | storage_energy | 0.027929 | GWh | 2017-12-01 | 2032-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6969 | Thrybergh Hydroelectric Scheme | storage_power | 0.0003 | GW | 2015-10-01 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6969-energy | Thrybergh Hydroelectric Scheme | storage_energy | 0.00055857 | GWh | 2015-10-01 | 2031-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6976 | Port of Tyne | storage_power | 0.035 | GW | 2018-07-01 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6976-energy | Port of Tyne | storage_energy | 0.065167 | GWh | 2018-07-01 | 2033-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6992 | Burbo Bank Energy Storage | storage_power | 0.002 | GW | 2018-12-24 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6992-energy | Burbo Bank Energy Storage | storage_energy | 0.0037238 | GWh | 2018-12-24 | 2033-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6993 | Trent Basin Community Battery | storage_power | 0.0005 | GW | 2018-07-15 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6993-energy | Trent Basin Community Battery | storage_energy | 0.00093095 | GWh | 2018-07-15 | 2033-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-6995 | Land at and adjacent to Leicester Forest Services | storage_power | 0.0015 | GW | 2021-01-01 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-6995-energy | Land at and adjacent to Leicester Forest Services | storage_energy | 0.0027929 | GWh | 2021-01-01 | 2036-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7000 | Slamseys Energy Storage | storage_power | 0.01 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7000-energy | Slamseys Energy Storage | storage_energy | 0.018619 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7001 | Stony Energy Storage Facility | storage_power | 0.0799 | GW | 2023-07-31 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7001-energy | Stony Energy Storage Facility | storage_energy | 0.14877 | GWh | 2023-07-31 | 2038-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7003 | Land off Queenborough Road | storage_power | 0.04 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7003-energy | Land off Queenborough Road | storage_energy | 0.074476 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7005 | Pillswood Phase 1 | storage_power | 0.0495 | GW | 2022-11-01 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7005-energy | Pillswood Phase 1 | storage_energy | 0.092164 | GWh | 2022-11-01 | 2037-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7015 | Aikengall II Community Wind Farm Battery | storage_power | 0.08 | GW | 2021-06-01 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7015-energy | Aikengall II Community Wind Farm Battery | storage_energy | 0.14895 | GWh | 2021-06-01 | 2036-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7019 | Nether Moor Field | storage_power | 0.0499 | GW | 2020-09-01 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7019-energy | Nether Moor Field | storage_energy | 0.092909 | GWh | 2020-09-01 | 2035-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7020 | Bilbo Solar Farm Energy Storage | storage_power | 0.04 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7020-energy | Bilbo Solar Farm Energy Storage | storage_energy | 0.074476 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7024 | Mannington Battery Storage Plant | storage_power | 0.0499 | GW | 2021-10-01 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7024-energy | Mannington Battery Storage Plant | storage_energy | 0.092909 | GWh | 2021-10-01 | 2036-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7027 | London Distribution Park | storage_power | 0.0038 | GW | 2019-01-01 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7027-energy | London Distribution Park | storage_energy | 0.0070752 | GWh | 2019-01-01 | 2034-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7034 | Carland Cross Wind Farm - Storage | storage_power | 0.001 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7034-energy | Carland Cross Wind Farm - Storage | storage_energy | 0.0018619 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7037 | Lathom (Pilkington Technical Centre) Battery Storage | storage_power | 0.002 | GW | 2019-04-16 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7037-energy | Lathom (Pilkington Technical Centre) Battery Storage | storage_energy | 0.0037238 | GWh | 2019-04-16 | 2034-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7044 | Enderby Storage, Redcomb Farm | storage_power | 0.0499 | GW | 2022-01-01 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7044-energy | Enderby Storage, Redcomb Farm | storage_energy | 0.092909 | GWh | 2022-01-01 | 2037-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7058 | Chapel Farm | storage_power | 0.0495 | GW | 2023-05-01 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7058-energy | Chapel Farm | storage_energy | 0.092164 | GWh | 2023-05-01 | 2038-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7081 | Sundridge Hill | storage_power | 0.0495 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7081-energy | Sundridge Hill | storage_energy | 0.092164 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7085 | Severn Road | storage_power | 0.032 | GW | 2021-12-23 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7085-energy | Severn Road | storage_energy | 0.059581 | GWh | 2021-12-23 | 2036-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7088 | Dollymans Storage | storage_power | 0.09998 | GW | 2023-07-01 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7088-energy | Dollymans Storage | storage_energy | 0.18615 | GWh | 2023-07-01 | 2038-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7099 | Philip Dennis Food Service | storage_power | 0.0038 | GW | 2018-05-01 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7099-energy | Philip Dennis Food Service | storage_energy | 0.0070752 | GWh | 2018-05-01 | 2033-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7122 | Creyke Beck | storage_power | 0.0499 | GW | 2018-11-01 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7122-energy | Creyke Beck | storage_energy | 0.092909 | GWh | 2018-11-01 | 2033-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7129 | Huggin's Hall | storage_power | 0.04 | GW | 2018-02-13 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7129-energy | Huggin's Hall | storage_energy | 0.074476 | GWh | 2018-02-13 | 2033-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7134 | Land SW of Shilton Cottage | storage_power | 0.0299 | GW | 2022-01-01 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7134-energy | Land SW of Shilton Cottage | storage_energy | 0.055671 | GWh | 2022-01-01 | 2037-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7140 | Calow Green Farm | storage_power | 0.02 | GW | 2019-10-01 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7140-energy | Calow Green Farm | storage_energy | 0.037238 | GWh | 2019-10-01 | 2034-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7143 | Land Adj Harmer Warren Quarry | storage_power | 0.01 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7143-energy | Land Adj Harmer Warren Quarry | storage_energy | 0.018619 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7148 | Kirkhaw Lane | storage_power | 0.02 | GW | 2018-05-01 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7148-energy | Kirkhaw Lane | storage_energy | 0.037238 | GWh | 2018-05-01 | 2033-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7152 | Fideoak Mills | storage_power | 0.03 | GW | 2020-08-01 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7152-energy | Fideoak Mills | storage_energy | 0.055857 | GWh | 2020-08-01 | 2035-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7155 | Land at Carnegie Road | storage_power | 0.02 | GW | 2018-12-24 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7155-energy | Land at Carnegie Road | storage_energy | 0.037238 | GWh | 2018-12-24 | 2033-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7156 | Anchor Lane Energy Centre | storage_power | 0.004 | GW | 2020-10-01 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7156-energy | Anchor Lane Energy Centre | storage_energy | 0.0074476 | GWh | 2020-10-01 | 2035-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7163 | Arbroath Battery Storage | storage_power | 0.035 | GW | 2024-04-02 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7163-energy | Arbroath Battery Storage | storage_energy | 0.065167 | GWh | 2024-04-02 | 2039-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7168 | Halewick Lane, Sompting - Battery-based Energy Storage Facility | storage_power | 0.04999 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7168-energy | Halewick Lane, Sompting - Battery-based Energy Storage Facility | storage_energy | 0.093076 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7172 | Osbaldwick Substation | storage_power | 0.0499 | GW | 2024-01-01 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7172-energy | Osbaldwick Substation | storage_energy | 0.092909 | GWh | 2024-01-01 | 2039-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7174 | Whitelee Wind Farm Battery Storage Extension | storage_power | 0.05 | GW | 2021-10-01 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7174-energy | Whitelee Wind Farm Battery Storage Extension | storage_energy | 0.093095 | GWh | 2021-10-01 | 2036-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7177 | Cleator | storage_power | 0.01 | GW | 2018-01-08 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7177-energy | Cleator | storage_energy | 0.018619 | GWh | 2018-01-08 | 2033-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7184 | Minety South - Battery Storage | storage_power | 0.04999 | GW | 2022-10-01 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7184-energy | Minety South - Battery Storage | storage_energy | 0.093076 | GWh | 2022-10-01 | 2037-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7185 | West Didsbury Battery Storage | storage_power | 0.04999 | GW | 2023-11-21 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7185-energy | West Didsbury Battery Storage | storage_energy | 0.093076 | GWh | 2023-11-21 | 2038-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7210 | Unipres building | solar | 0.0049 | GW | 2020-07-31 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7222 | Easter Bush | solar | 0.003 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7223 | Inkersall Grange Farm | solar | 0.0499 | GW | 2025-05-01 | 2055-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7225 | Tesco Wombwell Lane | solar | 0.0002 | GW | 2020-04-01 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7229 | Tesco Superstore Shripney Road | solar | 0.0002 | GW | 2020-05-01 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7232 | Glaxosmithkline Shewalton Road | solar | 0.0199 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7235 | Tesco Lottbridge Drove | solar | 0.0002 | GW | 2019-11-15 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7238 | Tesco Super-Store (Bridge Road) | solar | 0.0004 | GW | 2020-01-24 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7242 | Meteor Business Park | storage_power | 0.0015 | GW | 2020-01-16 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7242-energy | Meteor Business Park | storage_energy | 0.0027929 | GWh | 2020-01-16 | 2035-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7244 | The Hazeley Academy | solar | 0.0002 | GW | 2019-10-16 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7247 | Tesco Extra Hazelmere | solar | 0.0004 | GW | 2019-10-04 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7248 | Amazon Omega Business Park | solar | 0.0015 | GW | 2020-01-01 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7249 | Iron Mountain Site | solar | 0.0003 | GW | 2020-01-01 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7251 | Tesco Crab Tree Lane | solar | 0.0005 | GW | 2020-03-27 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7252 | Building ONE | solar | 0.0012 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7256 | The Grange | solar | 0.0499 | GW | 2021-04-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7258 | Streetfield Farm | solar | 0.0183 | GW | 2022-12-01 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7259 | Iron Mountain Building | solar | 0.0003 | GW | 2020-03-01 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7267 | St Margarets Bay | solar | 0.0002 | GW | 2020-03-31 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7269 | Lamp Hill Wimpole Estate | solar | 0.0004 | GW | 2020-02-04 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7274 | Alness Academy | solar | 0.0005 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7279 | Ainsdale Wastewater Treatment Works | solar | 0.0003 | GW | 2019-09-06 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7281 | Lochaber High School (Resubmission) | solar | 0.0003 | GW | 2019-12-01 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7287 | Perth Wastewater Treatment Works | solar | 0.0004 | GW | 2021-07-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7288 | TF and JH Braime Holdings Factory | solar | 0.0002 | GW | 2020-10-01 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7290 | Computacenter Warehouse | solar | 0.002 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7292 | Tesco Super-Store (Garratt Way, Gorton) | solar | 0.0007 | GW | 2020-07-01 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7298 | Volmary Site | solar | 0.0002 | GW | 2019-07-31 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7304 | Deuchries Windfarm (extension) (Bradley 2) | onshore | 0.0047 | GW | 2024-08-01 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7306 | Stranoch 2 | storage_power | 0.02 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7306-energy | Stranoch 2 | storage_energy | 0.037238 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7307 | Silver Spinney Farm | storage_power | 0.005 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7307-energy | Silver Spinney Farm | storage_energy | 0.0093095 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7310 | Invergordon Academy | solar | 0.0002 | GW | 2019-11-01 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7312 | The Low Carbon Energy Generation Project at Keele University | onshore | 0.0019 | GW | 2021-09-01 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7320 | National Space Centre | solar | 0.0002 | GW | 2019-03-31 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7321 | Tesco Queensway Place | solar | 0.0003 | GW | 2019-12-20 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7330 | Meadow Lane Park and Ride | solar | 0.0009 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7332 | Boscar Grange Farm | storage_power | 0.027 | GW | 2019-12-18 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7332-energy | Boscar Grange Farm | storage_energy | 0.050271 | GWh | 2019-12-18 | 2034-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7334 | Clayhill | storage_power | 0.006 | GW | 2016-06-24 | 2031-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7334-energy | Clayhill | storage_energy | 0.011171 | GWh | 2016-06-24 | 2031-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7335 | Tollgate Farm Battery Storage | storage_power | 0.0495 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7335-energy | Tollgate Farm Battery Storage | storage_energy | 0.092164 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7340 | Kilgallioch Windfarm (Extension) | onshore | 0.0504 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-7347 | Aviva Headquarters | solar | 0.0018 | GW | 2020-11-01 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7360 | Pillswood Phase 2 | storage_power | 0.0495 | GW | 2022-11-01 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7360-energy | Pillswood Phase 2 | storage_energy | 0.092164 | GWh | 2022-11-01 | 2037-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7363 | Bracks Farm | solar | 0.028 | GW | 2023-10-04 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7368 | Kemsley Substation | storage_power | 0.0499 | GW | 2021-10-25 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7368-energy | Kemsley Substation | storage_energy | 0.092909 | GWh | 2021-10-25 | 2036-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7371 | Ferrymuir | storage_power | 0.0499 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7371-energy | Ferrymuir | storage_energy | 0.092909 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7374 | Flamingo House | solar | 0.001 | GW | 2020-12-01 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7375 | Kingmoor Park | solar | 0.005 | GW | 2020-08-01 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7376 | Shewalton Road | onshore | 0.003 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-7381 | The Oxfordshire Golf Club | solar | 0.0003 | GW | 2019-11-01 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7383 | Plot 2B EurolinkV | storage_power | 0.02 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7383-energy | Plot 2B EurolinkV | storage_energy | 0.037238 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7384 | Aurora Solar Farm | solar | 0.032 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7385 | Aurora Solar Farm | storage_power | 0.018 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7385-energy | Aurora Solar Farm | storage_energy | 0.033514 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7386 | Buckingham Tesco Superstore | solar | 0.0002 | GW | 2020-01-01 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7388 | Winkburn Estate Solar Farm | solar | 0.0499 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7391 | Henry Colbeck Office | solar | 0.0002 | GW | 2019-03-01 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7395 | Harestanes Windfarm | storage_power | 0.1 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7395-energy | Harestanes Windfarm | storage_energy | 0.18619 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7400 | Flint Landfill Site Castle Park | solar | 0.002 | GW | 2021-02-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7405 | East Codford Solar Farm Extension Phase 3 | solar | 0.018 | GW | 2022-09-01 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7409 | Keele University | solar | 0.0044 | GW | 2022-04-29 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7410 | Tesco Superstore Bicester | solar | 0.0006 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7423 | Lower Strensham, Bourne Road (Extension) | solar | 0.008 | GW | 2021-01-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7425 | Hatherden Farm | solar | 0.0499 | GW | 2025-10-01 | 2055-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7448 | Hewitts Avenue Tesco | solar | 0.0005 | GW | 2020-03-06 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7451 | Langford Solar Farm | solar | 0.035 | GW | 2025-07-02 | 2055-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7456 | Hagshaw Hill (Repowering) | onshore | 0.08 | GW | 2025-11-01 | 2050-01-01 | Operational | Rounded operator capacity: 80 MW, Scottish Power 2025 accounts p23; replaces REPD planned 84 MW | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Operator confirms the original 26 turbines were replaced. Capacity rounded to 80 MW in accounts; original 15.6 MW excluded. | https://www.scottishpower.com/documents/d/guest/SPUK_2025_Annual_Accounts
REPD-7464 | Lascar Works | storage_power | 0.02 | GW | 2019-06-26 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7464-energy | Lascar Works | storage_energy | 0.037238 | GWh | 2019-06-26 | 2034-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7478 | Pall Europe Building | solar | 0.00058 | GW | 2021-08-15 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7479 | Bramford Substation | storage_power | 0.057 | GW | 2025-04-01 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7479-energy | Bramford Substation | storage_energy | 0.10613 | GWh | 2025-04-01 | 2040-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7482 | North Angle Farm | solar | 0.0294 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7497 | Ray Valley Solar Farm | solar | 0.019 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7508 | A J Lowther and Son Premise | solar | 0.001 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7510 | Salisbury Substation | storage_power | 0.0495 | GW | 2024-04-01 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7510-energy | Salisbury Substation | storage_energy | 0.092164 | GWh | 2024-04-01 | 2039-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7519 | Corner Copse Solar Farm | solar | 0.0499 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7524 | Severn Road | onshore | 0.0042 | GW | 2023-10-09 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7526 | Iron Mountain Howe Moss Drive | solar | 0.0003 | GW | 2020-03-27 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7531 | Eden Campus | solar | 0.001 | GW | 2021-12-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7539 | Bowerhouse Farm (extension) | solar | 0.0198 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7541 | Queen Elizabeth The Queen Mothers Hospital | solar | 0.0004 | GW | 2020-07-01 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7542 | William Harvey Hospital | solar | 0.0004 | GW | 2018-01-01 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Missing operational date estimated2018. | data/evidence/repd.csv
REPD-7559 | South Shore Holiday Village | solar | 0.0004 | GW | 2021-05-18 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7561 | Tiln Farm Solar Farm | solar | 0.0499 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7562 | Windy Rig Wind Farm | onshore | 0.043 | GW | 2021-10-01 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7570 | Clayhill Farm - Battery Energy Storage | storage_power | 0.021 | GW | 2019-10-01 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7570-energy | Clayhill Farm - Battery Energy Storage | storage_energy | 0.0391 | GWh | 2019-10-01 | 2034-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7571 | Cowley electricity sub-station | storage_power | 0.0499 | GW | 2021-06-22 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7571-energy | Cowley electricity sub-station | storage_energy | 0.092909 | GWh | 2021-06-22 | 2036-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7577 | Bradford West Substation (Harrop Edge Farm) | storage_power | 0.0499 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7577-energy | Bradford West Substation (Harrop Edge Farm) | storage_energy | 0.092909 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7588 | Land near Ventonteague | onshore | 0.0023 | GW | 2020-07-22 | 2045-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7591 | Dunsinane Industrial Estate | storage_power | 0.0499 | GW | 2023-05-03 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7591-energy | Dunsinane Industrial Estate | storage_energy | 0.092909 | GWh | 2023-05-03 | 2038-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7595 | St Fergus Renewable Energy Park | onshore | 0.003 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-7596 | St Fergus Renewable Energy Park | solar | 0.005 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7599 | Duke Of Gloucester Barracks | solar | 0.0014 | GW | 2021-09-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7604 | Ely Road Waste Management Park | solar | 0.0011 | GW | 2022-01-01 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7614 | Lapwing Fen 2 - Battery Storage Plant | storage_power | 0.25 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7614-energy | Lapwing Fen 2 - Battery Storage Plant | storage_energy | 0.46548 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7630 | Burwell Solar Farm | solar | 0.0499 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7632 | Gipsy Lane | storage_power | 0.02 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7632-energy | Gipsy Lane | storage_energy | 0.037238 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7646 | Tesco Superstore Thetford Road | solar | 0.0002 | GW | 2021-10-09 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7656 | Double Arches Solar Array | solar | 0.0025 | GW | 2026-01-01 | 2056-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7663 | Feeder Road | storage_power | 0.02 | GW | 2023-05-01 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7663-energy | Feeder Road | storage_energy | 0.037238 | GWh | 2023-05-01 | 2038-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7666 | Pentlow Hill | solar | 0.024 | GW | 2024-06-10 | 2054-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7684 | Energy Centre Royal Mint | storage_power | 0.02 | GW | 2023-08-01 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7684-energy | Energy Centre Royal Mint | storage_energy | 0.037238 | GWh | 2023-08-01 | 2038-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7688 | Holes Bay | storage_power | 0.015 | GW | 2020-06-01 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7688-energy | Holes Bay | storage_energy | 0.027929 | GWh | 2020-06-01 | 2035-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7689 | Jaywick Water Recycling Centre | solar | 0.0009 | GW | 2019-12-16 | 2049-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7696 | Thurrock Flexible Generation Plant | storage_power | 0.15 | GW | 2018-01-01 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Missing operational date estimated2018. | data/evidence/repd.csv
REPD-7696-energy | Thurrock Flexible Generation Plant | storage_energy | 0.27929 | GWh | 2018-01-01 | 2033-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Missing operational date estimated2018. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7701 | Pancross & Oaklands Solar Farm | solar | 0.05 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7702 | Pancross & Oaklands Solar Farm | storage_power | 0.05 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7702-energy | Pancross & Oaklands Solar Farm | storage_energy | 0.093095 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7708 | Limekiln Wind Farm (Extension) | onshore | 0.021 | GW | 2025-04-01 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7714 | Rock Barracks Solar Farm | solar | 0.0015 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7735 | Elmsall Way Warehouse | solar | 0.0024 | GW | 2021-07-09 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7738 | Kenyon Way | solar | 0.0019 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7740 | Lister Drive | storage_power | 0.0499 | GW | 2018-01-01 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Missing operational date estimated2018. | data/evidence/repd.csv
REPD-7740-energy | Lister Drive | storage_energy | 0.092909 | GWh | 2018-01-01 | 2033-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Missing operational date estimated2018. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7741 | Land at Wrigley Head | solar | 0.0009 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7745 | Howden Farm | solar | 0.0002 | GW | 2021-01-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7758 | Hutchesons Grammar School | solar | 0.00018 | GW | 2021-01-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7763 | Claylands Road | solar | 0.0002 | GW | 2022-01-01 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7766 | Pattemores Transport (Crewkern) | solar | 0.0021 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7772 | Liverpool Energy Management Facility | storage_power | 0.0499 | GW | 2022-03-01 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7772-energy | Liverpool Energy Management Facility | storage_energy | 0.092909 | GWh | 2022-03-01 | 2037-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7773 | Stonehill Energy Storage / Lower Minety | storage_power | 0.05 | GW | 2022-12-15 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7773-energy | Stonehill Energy Storage / Lower Minety | storage_energy | 0.093095 | GWh | 2022-12-15 | 2037-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7781 | Two Post Lane | solar | 0.012 | GW | 2022-01-01 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7782 | ENWL Training Academy | solar | 0.0003 | GW | 2021-11-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7795 | Lag Farm | solar | 0.001 | GW | 2020-01-01 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7800 | Hawthorne Road | storage_power | 0.02 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7800-energy | Hawthorne Road | storage_energy | 0.037238 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7818 | Normandy Barracks | solar | 0.0023 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7819 | Harborough Road Store | solar | 0.0002 | GW | 2022-01-01 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7828 | Titchfield Lane | storage_power | 0.049 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7828-energy | Titchfield Lane | storage_energy | 0.091233 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7834 | Crumps Yard Solar Farm | solar | 0.0016 | GW | 2021-02-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7840 | Croome Airfield Solar Farm | solar | 0.0499 | GW | 2023-02-01 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7841 | Rassau Industrial Estate | storage_power | 0.006 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7841-energy | Rassau Industrial Estate | storage_energy | 0.011171 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7856 | Cleve Hill Solar Project | storage_power | 0.15 | GW | 2025-07-01 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7856-energy | Cleve Hill Solar Project | storage_energy | 0.27929 | GWh | 2025-07-01 | 2040-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7882 | Arecleoch Wind Farm (extension) | storage_power | 0.02 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7882-energy | Arecleoch Wind Farm (extension) | storage_energy | 0.037238 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7883 | Brinsbury Campus Stane | solar | 0.0002 | GW | 2021-12-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7885 | Coventry National Grid Substation | storage_power | 0.0499 | GW | 2023-12-01 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7885-energy | Coventry National Grid Substation | storage_energy | 0.092909 | GWh | 2023-12-01 | 2038-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7889 | Grimsby Solar Farm | solar | 0.0499 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7907 | Bustleholme Substation | storage_power | 0.0499 | GW | 2023-10-20 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7907-energy | Bustleholme Substation | storage_energy | 0.092909 | GWh | 2023-10-20 | 2038-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7911 | Chalk Pit Solar Farm | solar | 0.024 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7915 | Perth Wastewater Treatment Works (Extension) | solar | 0.0003 | GW | 2021-05-17 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7928 | H M Prison Bure | solar | 0.0002 | GW | 2021-03-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7929 | Clifton Farm | solar | 0.035 | GW | 2025-09-01 | 2055-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7943 | City of Edinburgh Council Buildings | solar | 0.0002 | GW | 2020-08-01 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7944 | Perrinpit Farm | solar | 0.0499 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7946 | Dundee Technology Park | storage_power | 0.0499 | GW | 2021-06-21 | 2036-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7946-energy | Dundee Technology Park | storage_energy | 0.092909 | GWh | 2021-06-21 | 2036-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7954 | Crick Road | solar | 0.0499 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7958 | Fox Covert Solar Farm | solar | 0.022 | GW | 2023-10-12 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7968 | Ricoh UK Products | solar | 0.0012 | GW | 2021-07-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7971 | Lower Fields Mushroom Farm | solar | 0.0003 | GW | 2021-08-26 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7972 | Fairview Farm | solar | 0.0002 | GW | 2021-09-22 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7976 | Brookhouse Mill | solar | 0.0003 | GW | 2020-10-21 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7985 | Unit 5 XL Business Park | storage_power | 0.0499 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-7985-energy | Unit 5 XL Business Park | storage_energy | 0.092909 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-7991 | Brownhill Farm | onshore | 0.0084 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-7994 | Clifton Marsh Waste Water Treatment Works | storage_power | 0.002 | GW | 2020-06-01 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-7994-energy | Clifton Marsh Waste Water Treatment Works | storage_energy | 0.0037238 | GWh | 2020-06-01 | 2035-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-8010 | Attleborough Road Solar Farm | solar | 0.03 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8011 | Three Maids Hill Solar Farm | solar | 0.025 | GW | 2023-01-01 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8013 | Elstow Landfill Site | solar | 0.0055 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8023 | Maldon Wycke Solar Farm | solar | 0.025 | GW | 2024-10-01 | 2054-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8026 | Bulphan Fen Solar Farm & Battery Storage | solar | 0.0499 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8029 | Tesco Extra Altrincham | solar | 0.0005 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8030 | The National Cycling Centre Velodrome | solar | 0.0007 | GW | 2023-07-01 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8031 | The Glowhouse | storage_power | 0.005 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8031-energy | The Glowhouse | storage_energy | 0.0093095 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-8037 | National Grid Enderby Substation | storage_power | 0.057 | GW | 2025-02-01 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8037-energy | National Grid Enderby Substation | storage_energy | 0.10613 | GWh | 2025-02-01 | 2040-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-8045 | Brindley Close (Extension) | storage_power | 0.006 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8045-energy | Brindley Close (Extension) | storage_energy | 0.011171 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-8046 | Lower Rumster wind turbine | onshore | 0.0002 | GW | 2021-06-26 | 2046-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8051 | Larks Green Solar Farm | solar | 0.07 | GW | 2023-05-02 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8052 | Larks Green Solar Farm | storage_power | 0.0495 | GW | 2024-11-12 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8052-energy | Larks Green Solar Farm | storage_energy | 0.092164 | GWh | 2024-11-12 | 2039-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-8053 | Low Farm Solar Farm | solar | 0.0499 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8062 | Wick Farm Melksham Substation | solar | 0.0499 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8067 | Swansea University Bay Campus | solar | 0.0002 | GW | 2023-03-01 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8069 | Blenheim Net Zero Estate | solar | 0.005 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8085 | Moston Vale | storage_power | 0.01 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8085-energy | Moston Vale | storage_energy | 0.018619 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-8094 | Hamer Warren Solar Farm | solar | 0.023 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8096 | Torrdhuin, Auchteraw Battery Storage Facility | storage_power | 0.0499 | GW | 2025-08-22 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8096-energy | Torrdhuin, Auchteraw Battery Storage Facility | storage_energy | 0.092909 | GWh | 2025-08-22 | 2040-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-8099 | Mill Lane, Nursling - Battery Storage Facility | storage_power | 0.02 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8099-energy | Mill Lane, Nursling - Battery Storage Facility | storage_energy | 0.037238 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-8101 | Litchardon Cross Solar Farm | solar | 0.0499 | GW | 2018-01-01 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Missing operational date estimated2018. | data/evidence/repd.csv
REPD-8131 | Darlington Road, Skeeby | solar | 0.055 | GW | 2024-10-24 | 2054-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8136 | Kemble Wick | solar | 0.0499 | GW | 2026-02-01 | 2056-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8141 | South Stilling Tanks Solar Farm | solar | 0.0005 | GW | 2021-12-16 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8146 | Bubney Farm | solar | 0.04 | GW | 2023-03-28 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8148 | Bracon Ash Solar | solar | 0.0285 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8149 | Bunkers Hill Farm - Solar farm & Battery stations | solar | 0.0499 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8160 | Bloxwich Battery | storage_power | 0.041 | GW | 2019-07-01 | 2034-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8160-energy | Bloxwich Battery | storage_energy | 0.076338 | GWh | 2019-07-01 | 2034-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-8165 | Sanko Gosei Solar Panels | solar | 0.0005 | GW | 2021-10-10 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8167 | Barnsdale Road Solar Park | solar | 0.04 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8178 | Heming Point Roof Mounted Solar Panels | solar | 0.0002 | GW | 2021-09-27 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8195 | Richborough Energy Park | storage_power | 0.0499 | GW | 2023-12-01 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8195-energy | Richborough Energy Park | storage_energy | 0.092909 | GWh | 2023-12-01 | 2038-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-8201 | Parkwood Road Rooftop Solar Array | solar | 0.00015 | GW | 2021-10-18 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8202 | Blyth Sewage Treatment Works | solar | 0.0023 | GW | 2021-09-14 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8203 | Stody Estate Solar Array | solar | 0.00049 | GW | 2021-10-06 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8204 | Albert Road Rooftop Solar Panels | solar | 0.00018 | GW | 2021-09-12 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8205 | Cupar Wastewater Treatment Works Solar Farm | solar | 0.00062 | GW | 2021-07-19 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8210 | Asksham Community Village Solar Farm | solar | 0.00015 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8212 | Kirby Road Solar Panels | solar | 0.00049 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8213 | Lower Dunton Road Battery Storage Facility | storage_power | 0.028 | GW | 2025-08-11 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8213-energy | Lower Dunton Road Battery Storage Facility | storage_energy | 0.052133 | GWh | 2025-08-11 | 2040-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-8222 | British Geological, Keywork Solar Panels | solar | 0.00062 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8223 | Four Elms Solar Array | solar | 0.00017 | GW | 2021-09-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8228 | Bishampton Solar Farm | solar | 0.03 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8233 | Stracathro Hospital Solar | solar | 0.00025 | GW | 2021-07-31 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8234 | Lockfield Avenue Solar | solar | 0.0002 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8251 | Layer Farm - Solar Farm | solar | 0.049 | GW | 2024-10-01 | 2054-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8257 | Siddington Solar Farm | solar | 0.01994 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8259 | Manor Farm Solar Panels | solar | 0.0003 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8261 | Riverside Resource Recovery Facility Battery Storage | storage_power | 0.0025 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8261-energy | Riverside Resource Recovery Facility Battery Storage | storage_energy | 0.0046548 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-8264 | Newlands Farm Battery Storage Facility Phase 2 | storage_power | 0.04 | GW | 2022-09-01 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8264-energy | Newlands Farm Battery Storage Facility Phase 2 | storage_energy | 0.074476 | GWh | 2022-09-01 | 2037-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-8272 | Littleyhey Prison Solar Farm | solar | 0.0005 | GW | 2021-11-22 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8283 | Native River | storage_power | 0.057 | GW | 2025-04-14 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8283-energy | Native River | storage_energy | 0.10613 | GWh | 2025-04-14 | 2040-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-8336 | Syston Road - Solar Farm | solar | 0.026 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8357 | Crouch Solar Farm | solar | 0.0499 | GW | 2024-10-30 | 2054-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8358 | Crouch Solar Farm | storage_power | 0.0499 | GW | 2024-10-30 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8358-energy | Crouch Solar Farm | storage_energy | 0.092909 | GWh | 2024-10-30 | 2039-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-8385 | Farburn Place - Battery Energy Storage Facility | storage_power | 0.03 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8385-energy | Farburn Place - Battery Energy Storage Facility | storage_energy | 0.055857 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-8405 | Oriel High School | solar | 0.00019 | GW | 2021-11-10 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8408 | Willow Farm | solar | 0.00115 | GW | 2022-08-15 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8411 | Fen Lane, Bulphan Solar Farm | solar | 0.0499 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8434 | Minchens Lane Battery Storage Facility | storage_power | 0.1 | GW | 2025-02-01 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8434-energy | Minchens Lane Battery Storage Facility | storage_energy | 0.18619 | GWh | 2025-02-01 | 2040-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-8440 | Burneside Mill, Burneside | solar | 0.001 | GW | 2021-06-15 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8448 | Nickle Farm | solar | 0.00035 | GW | 2021-08-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8452 | London Road, Holmes Chapel Photovoltaic Panels | solar | 0.00096 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8455 | Trondheim Way Battery energy storage | storage_power | 0.08 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8455-energy | Trondheim Way Battery energy storage | storage_energy | 0.14895 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-8457 | Churn Lane, Horsmonden Solar Panels | solar | 0.0005 | GW | 2021-09-08 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8468 | Garbet Windfarm - Wind Farm & Storage facility | onshore | 0.0462 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-8469 | Garbet Windfarm - Wind Farm & Storage facility | storage_power | 0.003 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8469-energy | Garbet Windfarm - Wind Farm & Storage facility | storage_energy | 0.0055857 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-8479 | Breach Farm - Solar farm | solar | 0.067 | GW | 2023-12-01 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8527 | Coylton Substation, Coylton - Battery Energy Storage | storage_power | 0.05 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8527-energy | Coylton Substation, Coylton - Battery Energy Storage | storage_energy | 0.093095 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-8528 | Doverdale - Solar Farm & Battery Storage | solar | 0.0499 | GW | 2025-12-01 | 2055-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8529 | Burtree Lane - Solar farm | solar | 0.0499 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8799 | Avon Road Car Park - Solar Photovoltaic Carport System | solar | 0.00162 | GW | 2022-07-26 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8802 | Derril Water Solar Farm - Solar Farm | solar | 0.042 | GW | 2025-09-10 | 2055-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8811 | Cranfield University - Solar Farm | solar | 0.00044 | GW | 2021-10-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8824 | Long Meadow Solar Farm | solar | 0.019 | GW | 2025-06-01 | 2055-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8830 | Neilston Greener Grid Park | storage_power | 0.05 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8830-energy | Neilston Greener Grid Park | storage_energy | 0.093095 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-8833 | Mannington Battery Energy Storage System | storage_power | 0.0499 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8833-energy | Mannington Battery Energy Storage System | storage_energy | 0.092909 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-8848 | Hirwaun Stor Generation - Battery Storage | storage_power | 0.02176 | GW | 2024-12-01 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8848-energy | Hirwaun Stor Generation - Battery Storage | storage_energy | 0.040515 | GWh | 2024-12-01 | 2039-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-8855 | Plant Produce - Solar PV panels | solar | 0.00015 | GW | 2021-10-06 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8856 | Hawthorn Farm - Solar photovoltaic panels | solar | 0.01 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8857 | Winterton Landfill Site - Ground Mounted Solar PV Arrays | solar | 0.005 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8858 | Dorset Green Solar Farm | solar | 0.005 | GW | 2023-04-05 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-8884 | Lairg 2 Wind Farm | onshore | 0.0499 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-8897 | Meadow Lane Solar Farm | solar | 0.0196 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8916 | Whitehills Energy Storage Facility | storage_power | 0.0499 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-8916-energy | Whitehills Energy Storage Facility | storage_energy | 0.092909 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-8928 | Burneside Mill Solar Array - Phase 3 | solar | 0.0003 | GW | 2021-05-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9002 | Offham Landfill Site - Solar PV Array | solar | 0.0102 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9010 | Standby Embedded Stor Power Plant - Battery storage | storage_power | 0.02 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9010-energy | Standby Embedded Stor Power Plant - Battery storage | storage_energy | 0.037238 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9013 | East Kilbride - Battery storage | storage_power | 0.0499 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9013-energy | East Kilbride - Battery storage | storage_energy | 0.092909 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9014 | Soay Solar Farm and Greener Grid Park | solar | 0.04999 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9038 | Littleton Solar Farm | solar | 0.03 | GW | 2026-03-27 | 2056-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9046 | Barton Hill Industrial Park - Battery Energy Storage Facility | storage_power | 0.0225 | GW | 2023-12-21 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9046-energy | Barton Hill Industrial Park - Battery Energy Storage Facility | storage_energy | 0.041893 | GWh | 2023-12-21 | 2038-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9051 | Fferm Penglais - Solar Farm | solar | 0.0025 | GW | 2022-07-31 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9058 | Breach Farm - Solar farm | storage_power | 0.00066 | GW | 2023-12-01 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9058-energy | Breach Farm - Solar farm | storage_energy | 0.0012289 | GWh | 2023-12-01 | 2038-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9063 | Minety South 2 - Battery Storage Facility | storage_power | 0.04999 | GW | 2022-11-07 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9063-energy | Minety South 2 - Battery Storage Facility | storage_energy | 0.093076 | GWh | 2022-11-07 | 2037-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9065 | Dragonhall Farm, Padanaram - Solar Photovoltaic Array | solar | 0.005 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9066 | Dragonhall Farm, Padanaram - Battery Storage | storage_power | 0.01 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9066-energy | Dragonhall Farm, Padanaram - Battery Storage | storage_energy | 0.018619 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9090 | Ducklington Solar Farm | solar | 0.036 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9096 | Gonerby Moor, Great Gonerby - Solar Farm | solar | 0.06 | GW | 2026-06-26 | 2056-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9110 | Westland Leisure Complex | solar | 0.00022 | GW | 2022-06-24 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9121 | Rusholme Grange | storage_power | 0.04 | GW | 2024-08-01 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9121-energy | Rusholme Grange | storage_energy | 0.074476 | GWh | 2024-08-01 | 2039-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9142 | Carland Cross - Solar Farm | solar | 0.01 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9150 | Outer Space Studios Solar Panels | solar | 0.0006 | GW | 2021-12-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9157 | Bumble Hole Lane, Dodford - Solar PV | solar | 0.00067 | GW | 2023-10-31 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9164 | Vale Of Mowbray Limited - Solar Photovoltaic System | solar | 0.001 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9173 | Eastfields Farm, Deppers Bridge - Solar Farm | solar | 0.0348 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9179 | Cottingham - Solar Farm | solar | 0.005 | GW | 2022-02-01 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9183 | Golds Hill - Battery Storage | storage_power | 0.057 | GW | 2024-01-01 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9183-energy | Golds Hill - Battery Storage | storage_energy | 0.10613 | GWh | 2024-01-01 | 2039-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9190 | Lidl Foodstore - Solar Panels | solar | 0.00018 | GW | 2022-01-01 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9193 | Boston Landfill, Wyberton - Solar PV Array | solar | 0.0097 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9198 | Continental Approach - Solar Panels | solar | 0.0002 | GW | 2021-08-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9224 | Balsillie Avenue - Roaring Hill Energy Storage Facility | storage_power | 0.0199 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9224-energy | Balsillie Avenue - Roaring Hill Energy Storage Facility | storage_energy | 0.037052 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9236 | Portsmouth International Port - Solar Panels | solar | 0.0012 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9237 | Leigh Delamere - Solar farm & Battery storage | solar | 0.0499 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9238 | Leigh Delamere - Solar farm & Battery storage | storage_power | 0.04 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9238-energy | Leigh Delamere - Solar farm & Battery storage | storage_energy | 0.074476 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9247 | Larport, Clay Hill Pit - Solar Photovoltaics & Battery storage | solar | 0.045 | GW | 2024-07-01 | 2054-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9248 | Devilla Energy Storage Facility | storage_power | 0.5 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9248-energy | Devilla Energy Storage Facility | storage_energy | 0.93095 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9253 | Harvie Card Way - Solar panels | solar | 0.00197 | GW | 2022-12-01 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9272 | Central Park - Solar photovaltics | solar | 0.00015 | GW | 2018-01-01 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Missing operational date estimated2018. | data/evidence/repd.csv
REPD-9273 | South Fambridge Hall - Solar farm & Battery storage | solar | 0.04999 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9274 | South Fambridge Hall - Solar farm & Battery storage | storage_power | 0.02 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9274-energy | South Fambridge Hall - Solar farm & Battery storage | storage_energy | 0.037238 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9282 | Periwinkle Hall - Links Solar photovoltaic farm & Battery storage | solar | 0.035 | GW | 2024-10-01 | 2054-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9315 | Sundon Substation | storage_power | 0.0499 | GW | 2025-12-01 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9315-energy | Sundon Substation | storage_energy | 0.092909 | GWh | 2025-12-01 | 2040-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9326 | Willow Road - Roof mounted solar panels | solar | 0.00035 | GW | 2021-11-15 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9340 | Widow Hill, Balderstone Lane - Battery Energy Storage System | storage_power | 0.07 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9340-energy | Widow Hill, Balderstone Lane - Battery Energy Storage System | storage_energy | 0.13033 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9351 | Bower Park Academy - Solar Photovoltaic Panels | solar | 0.00026 | GW | 2021-12-26 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9360 | South Farm Solar Park | solar | 0.04 | GW | 2022-12-16 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9361 | South Farm Solar Park | storage_power | 0.01 | GW | 2022-12-16 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9361-energy | South Farm Solar Park | storage_energy | 0.018619 | GWh | 2022-12-16 | 2037-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9367 | Jacksons Bakery - Solar Panels | solar | 0.00063 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9372 | Hazelrigg Lane, Scotforth - Solar Farm | solar | 0.0165 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9377 | Capenhurst Lane, Capenhurst - Battery storage | storage_power | 0.057 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9377-energy | Capenhurst Lane, Capenhurst - Battery storage | storage_energy | 0.10613 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9382 | St Peters Hall | solar | 0.0017 | GW | 2021-09-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9388 | Dyce Energy Storage, Raiths Industrial Estate - Battery Facility | storage_power | 0.05 | GW | 2023-09-01 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9388-energy | Dyce Energy Storage, Raiths Industrial Estate - Battery Facility | storage_energy | 0.093095 | GWh | 2023-09-01 | 2038-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9394 | Crimscote Solar Farm and Storage Project | solar | 0.04999 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9404 | Fiddlers Ferry Power Station - Battery storage | storage_power | 0.15 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9404-energy | Fiddlers Ferry Power Station - Battery storage | storage_energy | 0.27929 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9412 | Princess Yachts Limited - Solar PV system | solar | 0.0007 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9420 | Daresbury Science Park - Solar Array | solar | 0.00056 | GW | 2021-11-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9427 | Hams Hall - Battery Energy Storage System | storage_power | 0.4 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9427-energy | Hams Hall - Battery Energy Storage System | storage_energy | 0.74476 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9500 | Banbeath Industrial Estate Solar Array | solar | 0.00419 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9503 | Stanstead Solar Project | solar | 0.0143 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9522 | Wishaw Battery Storage Facility | storage_power | 0.04999 | GW | 2023-11-15 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9522-energy | Wishaw Battery Storage Facility | storage_energy | 0.093076 | GWh | 2023-11-15 | 2038-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9523 | Wastewater Treatment Works, Fraserburgh | solar | 0.00103 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9524 | Walpole Bank | solar | 0.04 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9527 | Bowmans Harbour Solar Farm | solar | 0.0069 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9541 | SAS International, Unit 1 - Solar PV Panels | solar | 0.0008 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9542 | Eastgate House Farm, Seamer - Solar Farm | solar | 0.032 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9570 | Royal Northern College Of Music, Oxford Road - Solar Photovoltaic panels | solar | 0.00017 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9578 | Chamber House | solar | 0.00399 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9584 | Astra Centre, Royal Barn Road - Energy Storage | storage_power | 0.04 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9584-energy | Astra Centre, Royal Barn Road - Energy Storage | storage_energy | 0.074476 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9610 | Tye Lane - Solar Farm | solar | 0.0499 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9626 | Richborough Energy Park - Phase 2 | storage_power | 0.0501 | GW | 2023-12-28 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9626-energy | Richborough Energy Park - Phase 2 | storage_energy | 0.093281 | GWh | 2023-12-28 | 2038-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9631 | Newbold Pacey Solar Farm | solar | 0.0287 | GW | 2024-11-01 | 2054-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9632 | Holly Street - Solar PV Panels | solar | 0.00016 | GW | 2021-12-31 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9653 | Bredbury Substation - Battery Storage Facility | storage_power | 0.0499 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9653-energy | Bredbury Substation - Battery Storage Facility | storage_energy | 0.092909 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9664 | Perrigo,Wrafton - Solar Photovoltaic System | solar | 0.00053 | GW | 2021-12-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9671 | Advent Way - Solar Panels | solar | 0.00018 | GW | 2021-12-01 | 2051-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9681 | Minster Abbey, Bedlam Court Lane - Solar PV panels | solar | 0.033 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9696 | Kilmarnock South Substation - Battery storage | storage_power | 0.3 | GW | 2026-01-21 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9696-energy | Kilmarnock South Substation - Battery storage | storage_energy | 0.55857 | GWh | 2026-01-21 | 2041-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9723 | Blackhillock Electricity Substation - Battery Energy Storage System | storage_power | 0.3 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9723-energy | Blackhillock Electricity Substation - Battery Energy Storage System | storage_energy | 0.55857 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9749 | Kingshill Solar Farm | solar | 0.003 | GW | 2024-07-16 | 2054-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9754 | Hornsea Project Three - Battery Storage | storage_power | 0.3 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9754-energy | Hornsea Project Three - Battery Storage | storage_energy | 0.55857 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9755 | Newcastle International Airport Phase 1 -Solar Farm | solar | 0.003 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9767 | Easlea Road - Solar Photovoltaic Panels | solar | 0.00062 | GW | 2022-01-01 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9785 | Gammaton Moor Solar farm | solar | 0.032 | GW | 2026-04-01 | 2056-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9802 | Great Wheatley Road - Solar Farm | solar | 0.03 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9815 | Gainsborough Road, Saundby - Solar Farm | solar | 0.078 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9816 | Gainsborough Road, Saundby - Battery Storage Facility | storage_power | 0.12 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9816-energy | Gainsborough Road, Saundby - Battery Storage Facility | storage_energy | 0.22343 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9826 | Squirrel Lane - Solar Photovoltaic Farm | solar | 0.012 | GW | 2026-05-01 | 2056-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9845 | IBL Cold Stores - Solar Photovoltaics Panels | solar | 0.0008 | GW | 2022-11-01 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9941 | Kiln Fields Solar Farm | solar | 0.01787 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9951 | Hurst Road - Walton Solar PV Farm | solar | 0.00055 | GW | 2022-04-01 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9957 | Douglas West Wind Farm (extension) | storage_power | 0.02 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9957-energy | Douglas West Wind Farm (extension) | storage_energy | 0.037238 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-9981 | Maes Mawr Solar | solar | 0.03 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-9997 | Pleasance Road - Battery Energy Facility | storage_power | 0.0499 | GW | 2023-06-01 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-9997-energy | Pleasance Road - Battery Energy Facility | storage_energy | 0.092909 | GWh | 2023-06-01 | 2038-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-10001 | Morrisons Witham - Solar Pv Panels | solar | 0.00019 | GW | 2022-10-01 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-10005 | Morrisons Store 148 Cheriton Road - Solar Array | solar | 0.00029 | GW | 2018-01-01 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Missing operational date estimated2018. | data/evidence/repd.csv
REPD-10016 | Banbury Road, Gaydon - Solar Array | solar | 0.018 | GW | 2025-08-01 | 2055-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-10022 | Kirkhaw Lane - Battery Storage Energy | storage_power | 0.15 | GW | 2026-03-23 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-10022-energy | Kirkhaw Lane - Battery Storage Energy | storage_energy | 0.27929 | GWh | 2026-03-23 | 2041-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-10035 | Penpergwm Solar Farm (Great House Farm) | solar | 0.032 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-10040 | Beavor - Photovoltaic Solar Arrays | solar | 0.0189 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-10088 | Horsey Levels - Solar Farm | solar | 0.024 | GW | 2018-01-01 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Missing operational date estimated2018. | data/evidence/repd.csv
REPD-10089 | Steeraway Farm - Solar Farm | solar | 0.03 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-10140 | Exeter Road, Braunton - Solar Panels | solar | 0.00075 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-10149 | Manners Avenue - Solar Panels | solar | 0.00062 | GW | 2022-05-01 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-10273 | Doverdale - Solar Farm & Battery Storage | storage_power | 0.0499 | GW | 2025-12-01 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-10273-energy | Doverdale - Solar Farm & Battery Storage | storage_energy | 0.092909 | GWh | 2025-12-01 | 2040-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-10296 | Station Road - Solar Array | solar | 0.00017 | GW | 2018-01-01 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Missing operational date estimated2018. | data/evidence/repd.csv
REPD-10303 | N H Case Limited - Solar Panels | solar | 0.00036 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-10304 | Dragon Energy Park - Wind Farm | onshore | 0.0144 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-10311 | Bullen Lane - Battery Storage | storage_power | 0.1 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-10311-energy | Bullen Lane - Battery Storage | storage_energy | 0.18619 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-10369 | Medebridge Road - Solar Farm | solar | 0.0499 | GW | 2025-09-01 | 2055-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-10412 | Chubb Road - Solar Photovoltaic | solar | 0.00015 | GW | 2022-05-01 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-10415 | Dragon Long Meadow - Solar farm | solar | 0.0099 | GW | 2023-03-13 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-10417 | Twitch Hill, Cheswell Grange Farm - Solar Farm & Battery Storage | solar | 0.025 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-10422 | Denton Hall Farm Road, Denton - Solar Photovoltaic System | solar | 0.00116 | GW | 2018-01-01 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Missing operational date estimated2018. | data/evidence/repd.csv
REPD-10443 | Morrisons, Bradford Road, Idle - Solar PV Panels | solar | 0.0008 | GW | 2022-04-01 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-10458 | Lumley Water Treatment Works - Solar Panels | solar | 0.0019 | GW | 2022-01-21 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-10469 | Hillhead Of Gask, Longhaven - Solar Array | solar | 0.0142 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-10471 | Kirkleatham Street - Solar Panel Array | solar | 0.00017 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-10477 | Highfields Farm, Clifton Lane - Solar Panels | solar | 0.0619 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-10497 | North Norfolk Business Centre Solar Park - Battery Energy Storage Scheme | storage_power | 0.006 | GW | 2018-01-01 | 2033-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Missing operational date estimated2018. | data/evidence/repd.csv
REPD-10497-energy | North Norfolk Business Centre Solar Park - Battery Energy Storage Scheme | storage_energy | 0.011171 | GWh | 2018-01-01 | 2033-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Missing operational date estimated2018. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-10549 | Glasgow Airport Solar Farm | solar | 0.0199 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-10577 | Maidstone Road, Horsmonden - Paddock Solar Farm | solar | 0.0499 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-10586 | Soay Solar Farm and Greener Grid Park | storage_power | 0.2 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-10586-energy | Soay Solar Farm and Greener Grid Park | storage_energy | 0.37238 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-10596 | Windyhill Battery Storage Facility | storage_power | 0.2 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-10596-energy | Windyhill Battery Storage Facility | storage_energy | 0.37238 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-10635 | Rock Farm - Solar Farm | solar | 0.04 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-10654 | Torbay Leisure Centre - Energy Project | solar | 0.00017 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-10690 | Whitegate Battery Storage | storage_power | 0.057 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-10690-energy | Whitegate Battery Storage | storage_energy | 0.10613 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-10692 | Altham Business Park - Solar Panels | solar | 0.00118 | GW | 2022-10-01 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-10716 | Waterswallows Road - Buxton Battery Storage Equipment | storage_power | 0.015 | GW | 2024-04-11 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-10716-energy | Waterswallows Road - Buxton Battery Storage Equipment | storage_energy | 0.027929 | GWh | 2024-04-11 | 2039-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-10755 | Arnolds Way, Yatton - Solar Panels | solar | 0.00084 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-10758 | Twin Tumps Way - Solar Panels | solar | 0.00062 | GW | 2022-05-28 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-10776 | Arthur Street - Solar Panels | solar | 0.00019 | GW | 2022-05-01 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-10778 | Crays Hall Farm - Solar Arrays | solar | 0.0256 | GW | 2026-05-14 | 2056-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-10780 | HMP Wayland - Solar Panels | solar | 0.00034 | GW | 2022-01-21 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-10790 | Royal Oak Way South - Solar Array | solar | 0.00166 | GW | 2023-10-01 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-10797 | Highleadon - Solar Arrays & Battery Storage | solar | 0.0499 | GW | 2025-12-01 | 2055-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-10800 | Tregonning Farm - Solar Farm & Battery Storage | solar | 0.068 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-10801 | Tregonning Farm - Solar Farm & Battery Storage | storage_power | 0.0475 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-10801-energy | Tregonning Farm - Solar Farm & Battery Storage | storage_energy | 0.08844 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-10809 | Barclays Bank Plc, Radbroke Solar Carport - Solar Panels | solar | 0.0025 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-10863 | Jamesfield Organic Centre - Battery Storage | storage_power | 0.049 | GW | 2024-02-01 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-10863-energy | Jamesfield Organic Centre - Battery Storage | storage_energy | 0.091233 | GWh | 2024-02-01 | 2039-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-10868 | Victoria Road - Solar Photovoltaic System | solar | 0.0007 | GW | 2022-06-01 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-10893 | Wormald Green - Battery Energy Storage System | storage_power | 0.033 | GW | 2024-09-11 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-10893-energy | Wormald Green - Battery Energy Storage System | storage_energy | 0.061443 | GWh | 2024-09-11 | 2039-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-10896 | Hawthorn Grid Site - Battery Storage | storage_power | 0.049 | GW | 2024-09-11 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-10896-energy | Hawthorn Grid Site - Battery Storage | storage_energy | 0.091233 | GWh | 2024-09-11 | 2039-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-10936 | Uskmouth Power Station - Battery Storage | storage_power | 0.23 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-10936-energy | Uskmouth Power Station - Battery Storage | storage_energy | 0.42824 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-10944 | Colton - Solar photovoltaic farm, Battery storage | solar | 0.03 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-10945 | Colton - Solar photovoltaic farm, Battery storage | storage_power | 0.03 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-10945-energy | Colton - Solar photovoltaic farm, Battery storage | storage_energy | 0.055857 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-10988 | B H K UK Davy Drive - Solar Panels | solar | 0.00134 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11017 | Pinnacle Storage Park, Dale Abbey - Solar PV Panels | solar | 0.001 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11034 | Coalburn Energy - Battery Storage | storage_power | 0.5 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11034-energy | Coalburn Energy - Battery Storage | storage_energy | 0.93095 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-11070 | Tudworth Field Road, Hatfield - Solar PV Panels | solar | 0.00027 | GW | 2023-01-01 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-11080 | The National Cycling Centre - Solar Photovoltaic Panels | solar | 0.00092 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11086 | Tudworth Field Road, Hatfield - Solar Panels | solar | 0.00018 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11101 | Faulds Park Road- Solar PV Panlels | solar | 0.00034 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11151 | Atherton - Battery energy storage | storage_power | 0.03 | GW | 2025-09-10 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-11151-energy | Atherton - Battery energy storage | storage_energy | 0.055857 | GWh | 2025-09-10 | 2040-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-11155 | Kirkcaldy W W T W, Nether Street- Solar Panels | solar | 0.00065 | GW | 2023-06-15 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-11160 | Chadderton - Battery energy storage facility | storage_power | 0.02 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11160-energy | Chadderton - Battery energy storage facility | storage_energy | 0.037238 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-11177 | Kincraig - Solar Farm and battery storage system | solar | 0.021 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11201 | Richborough Energy Park - Phase 3 (Sheaf) | storage_power | 0.249 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11201-energy | Richborough Energy Park - Phase 3 (Sheaf) | storage_energy | 0.46361 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-11259 | Mounteneys and Cherry Rock Wind Turbines | onshore | 0.001 | GW | 2017-03-01 | 2042-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-11263 | Dunfermline North - Solar Photovoltaic Array/Battery storage | solar | 0.0299 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11264 | Dunfermline North - Solar Photovoltaic Array/Battery storage | storage_power | 0.02 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11264-energy | Dunfermline North - Solar Photovoltaic Array/Battery storage | storage_energy | 0.037238 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-11271 | Kingsway - Solar Panels | solar | 0.00016 | GW | 2022-10-11 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-11291 | Audi Stockport, Brinksway, Edgeley - Solar Panels | solar | 0.00027 | GW | 2022-12-01 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-11302 | Parc Solar Caenewydd | solar | 0.042 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11303 | Parc Solar Caenewydd | storage_power | 0.046 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11303-energy | Parc Solar Caenewydd | storage_energy | 0.085647 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-11312 | Limekiln Wind Farm (Extension) - Battery | storage_power | 0.005 | GW | 2025-04-01 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-11312-energy | Limekiln Wind Farm (Extension) - Battery | storage_energy | 0.0093095 | GWh | 2025-04-01 | 2040-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-11321 | Staythorpe Road - Battery energy storage | storage_power | 0.36 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11321-energy | Staythorpe Road - Battery energy storage | storage_energy | 0.67028 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-11329 | Cutbush Farm, Belchamp St Paul - Solar Array | solar | 0.04999 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11330 | Cinch Stadium, Franklin’s Gardens - Solar | solar | 0.0088 | GW | 2022-05-20 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-11335 | Atherton Way - Solar Panels | solar | 0.00024 | GW | 2022-12-06 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-11359 | Elmsall Way, South Elmsall - Solar Panels | solar | 0.003 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11366 | Ford Oaks Solar & Green Infrastructure Facility | solar | 0.03 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11384 | Rhigos Road - Solar Farm | solar | 0.00988 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11410 | Arkwright Road, Groundwell Industrial Estate - Solar Panels | solar | 0.00091 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11419 | SC Johnson, Denby - Solar Panels | solar | 0.00062 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11423 | London Road, Irchester - Solar Farm | solar | 0.026 | GW | 2018-01-01 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Missing operational date estimated2018. | data/evidence/repd.csv
REPD-11449 | Harrington Franklin, Richborough Energy Park - Battery Storage | storage_power | 0.0499 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11449-energy | Harrington Franklin, Richborough Energy Park - Battery Storage | storage_energy | 0.092909 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-11486 | Ford Research And Engineering Centre, Dunton - Solar Farm | solar | 0.0052 | GW | 2025-01-31 | 2055-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-11491 | East Haddon - Solar Photovoltaic System | solar | 0.002 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11499 | Blanche Lane, South Mimms - Solar Panels | solar | 0.00061 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11509 | Bryngolwg Farm, Hirwaun - Solar farm | solar | 0.00894 | GW | 2018-01-01 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Missing operational date estimated2018. | data/evidence/repd.csv
REPD-11513 | Desford Brick Works, Bagworth - Solar Panels | solar | 0.0026 | GW | 2024-04-01 | 2054-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-11567 | Longlooms Road East - Solar panels | solar | 0.00022 | GW | 2023-01-01 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-11589 | Wooperton Station, Wooperton - Solar Farm | solar | 0.00556 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11590 | Overhill Farm, Rothienorman - Battery Energy Storage | storage_power | 0.0499 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11590-energy | Overhill Farm, Rothienorman - Battery Energy Storage | storage_energy | 0.092909 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-11646 | Plant 1, G-Tekt Europe Manufacturing Limited -Roof Mounted Solar Panels | solar | 0.001 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11656 | Little Beanit Farm, Balsall Common - Battery Storage | storage_power | 0.2 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11656-energy | Little Beanit Farm, Balsall Common - Battery Storage | storage_energy | 0.37238 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-11674 | Holmfield - Battery Energy Storage | storage_power | 0.00025 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11674-energy | Holmfield - Battery Energy Storage | storage_energy | 0.00046548 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-11679 | Holmston Road - Battery Storage Facility | storage_power | 0.0499 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11679-energy | Holmston Road - Battery Storage Facility | storage_energy | 0.092909 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-11706 | Arbikie, Inverkeilor - Green Hydrogen Project & Wind Turbine | onshore | 0.001 | GW | 2023-01-01 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-11711 | Ham Close - 452 Houses, Flats & Leisure Centre | solar | 0.00043 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11720 | Clay Tye Farm Phase 1 - Storage Facility | storage_power | 0.0495 | GW | 2024-03-22 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-11720-energy | Clay Tye Farm Phase 1 - Storage Facility | storage_energy | 0.092164 | GWh | 2024-03-22 | 2039-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-11721 | Clay Tye Farm Phase 2 - Storage Facility | storage_power | 0.0495 | GW | 2024-03-22 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-11721-energy | Clay Tye Farm Phase 2 - Storage Facility | storage_energy | 0.092164 | GWh | 2024-03-22 | 2039-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-11755 | Concorde Way, Segensworth - Solar Panels | solar | 0.00104 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11756 | Paytherden Solar Farm (Peradon) | solar | 0.049 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11799 | Pepperhill Solar Farm - Solar Farm & Battery Storage | solar | 0.023 | GW | 2018-01-01 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Missing operational date estimated2018. | data/evidence/repd.csv
REPD-11815 | Deyes Academy Redevelopment | solar | 0.00063 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11866 | Midsomer Norton - Battery Energy Storage System | storage_power | 0.006 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11866-energy | Midsomer Norton - Battery Energy Storage System | storage_energy | 0.011171 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-11867 | Eccles Battery Energy Storage System | storage_power | 0.4 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11867-energy | Eccles Battery Energy Storage System | storage_energy | 0.74476 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-11885 | Lychgate Lane, Aston Flamville - Solar Farm | solar | 0.02 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11975 | Apac Packaging, Loughborough Road - Solar Panels | solar | 0.0009 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11995 | Braintree Road, Cressing - Battery Storage | storage_power | 0.057 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-11995-energy | Braintree Road, Cressing - Battery Storage | storage_energy | 0.10613 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-12050 | Midland Lead, Kiln Way - Solar Photovoltaic Panels | solar | 0.00024 | GW | 2022-11-01 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-12054 | Regent Street, Sheepscar - Solar Panels | solar | 0.00022 | GW | 2023-06-01 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-12078 | Caldecote Farm - Storage & Distribution Unit | solar | 0.00026 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12101 | Birch Solar Farm & Battery Storage | solar | 0.04 | GW | 2018-01-01 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Missing operational date estimated2018. | data/evidence/repd.csv
REPD-12117 | Cowbridge Road, Bicker Fen - Solar Array | solar | 0.075 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12118 | Cowbridge Road, Bicker Fen - Battery Storage | storage_power | 0.05 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12118-energy | Cowbridge Road, Bicker Fen - Battery Storage | storage_energy | 0.093095 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-12137 | Feldon Vale Solar Farm | solar | 0.0499 | GW | 2018-01-01 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Missing operational date estimated2018. | data/evidence/repd.csv
REPD-12206 | Coalburn II Energy Storage Facility - Battery Storage Facility | storage_power | 1 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12206-energy | Coalburn II Energy Storage Facility - Battery Storage Facility | storage_energy | 1.8619 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-12271 | Tennant Avenue College, East Kilbride - Solar Panels | solar | 0.00094 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12273 | Loch Fergus Farm - Solar Farm | solar | 0.04 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12274 | Loch Fergus Farm - Energy Storage System | storage_power | 0.045 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12274-energy | Loch Fergus Farm - Energy Storage System | storage_energy | 0.083786 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-12275 | Mill Rig Wind Farm | onshore | 0.036 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-12293 | Hawkers Hill Energy Park | storage_power | 0.02 | GW | 2022-10-03 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-12293-energy | Hawkers Hill Energy Park | storage_energy | 0.037238 | GWh | 2022-10-03 | 2037-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-12300 | Inkersall Road, Staveley - Solar Photovoltaic Farm And Battery Storage | solar | 0.031 | GW | 2018-01-01 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Missing operational date estimated2018. | data/evidence/repd.csv
REPD-12314 | Bells Of Lazonby, Edenholme Bakery - Solar Panels | solar | 0.00063 | GW | 2023-03-01 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-12327 | Horiba Mira, Mira Drive - Solar Array | solar | 0.007 | GW | 2025-09-01 | 2055-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-12335 | Tout Lane, Charlton Adam - Solar Photovoltaic System | solar | 0.0003 | GW | 2020-01-01 | 2050-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-12393 | Brickfields Business Park, Unit 35 - Solar Panels | solar | 0.00033 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12397 | Brickfields Business Park, Unit 16 - Solar Panels | solar | 0.00017 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12398 | Brickfields Business Park, Unit 24 - Solar panels | solar | 0.00016 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12399 | Brickfields Business Park, Unit 17 - Solar panels | solar | 0.00062 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12439 | Cranswick Country Foods, Seafox Court - Solar Panels | solar | 0.00065 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12450 | West Suffolk College, Out Risbygate Street - Solar Panels | solar | 0.00055 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12507 | Croft Farm, Askern Road - Solar Array & Hydrogen Plant | solar | 0.0025 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12529 | Norwich Road Industrial Estate | storage_power | 0.05 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12529-energy | Norwich Road Industrial Estate | storage_energy | 0.093095 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-12597 | Tolldish Hall Farm, Parrotts Grove - Solar Photovoltaic Panels | solar | 0.025 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12623 | Trinity Hall Solar Farm | solar | 0.015 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12663 | Donaldsons Nursery, Marsh Farm - Solar Panels | solar | 0.00019 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12682 | Rookwood Way - Solar Farm | solar | 0.00204 | GW | 2024-05-01 | 2054-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-12694 | Freshfields, Fairy Lane - Battery Storage | storage_power | 0.0999 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12694-energy | Freshfields, Fairy Lane - Battery Storage | storage_energy | 0.186 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-12720 | Marsh Lane - Solar PV Panels | solar | 0.00089 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12725 | National Grid Electricity Substation, Capenhurst Lane - Battery Storage | storage_power | 0.1 | GW | 2023-02-11 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-12725-energy | National Grid Electricity Substation, Capenhurst Lane - Battery Storage | storage_energy | 0.18619 | GWh | 2023-02-11 | 2038-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-12728 | Eastbourne District General Hospital - Energy Management | solar | 0.0011 | GW | 2023-10-31 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-12758 | Total Food Services, North Road - Solar Panels | solar | 0.00022 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12764 | Kneller Hall School | solar | 0.00025 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12791 | Cirencester Solar Farm | storage_power | 0.01 | GW | 2022-10-13 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-12791-energy | Cirencester Solar Farm | storage_energy | 0.018619 | GWh | 2022-10-13 | 2037-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-12802 | University Way, Cranfield - Solar Array | solar | 0.00088 | GW | 2023-07-13 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-12803 | Derehams Farm, Derehams Lane - Battery Storage | storage_power | 0.04 | GW | 2025-08-06 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-12803-energy | Derehams Farm, Derehams Lane - Battery Storage | storage_energy | 0.074476 | GWh | 2025-08-06 | 2040-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-12856 | Shetland Battery Energy Storage System | storage_power | 0.07 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12856-energy | Shetland Battery Energy Storage System | storage_energy | 0.13033 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-12920 | J3 Business Park - Battery Energy Storage Facility | storage_power | 0.01 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12920-energy | J3 Business Park - Battery Energy Storage Facility | storage_energy | 0.018619 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-12922 | Sewage Treatment Works, Rosehall Road - Solar PV Panels | solar | 0.00023 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12927 | United Anodisers, Red Doles Lane - Solar Panels | solar | 0.00031 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12934 | County Hall, Loansdean - Solar Array | solar | 0.0008 | GW | 2023-08-18 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-12935 | County Hall, Loansdean - Battery Storage | storage_power | 0.0004 | GW | 2023-08-18 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-12935-energy | County Hall, Loansdean - Battery Storage | storage_energy | 0.00074476 | GWh | 2023-08-18 | 2038-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-12947 | Lilford Hall, Lilford - Solar Panels | solar | 0.001 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12972 | Limebury Farm, Horns Cross - Solar Farm | solar | 0.0065 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12982 | Welkin Mill, Welkin Road - Battery Storage | storage_power | 0.0499 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-12982-energy | Welkin Mill, Welkin Road - Battery Storage | storage_energy | 0.092909 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-13003 | Eccles Substation, Eccles - Battery Energy Storage System | storage_power | 0.05 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-13003-energy | Eccles Substation, Eccles - Battery Energy Storage System | storage_energy | 0.093095 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-13011 | Mount Pleasant Farm, Green Lane - Battery Storage | storage_power | 0.045 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-13011-energy | Mount Pleasant Farm, Green Lane - Battery Storage | storage_energy | 0.083786 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-13014 | Little Toms - Solar Farm | solar | 0.005 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-13025 | Wilkin And Sons, Factory Hill - Solar Farm | solar | 0.00615 | GW | 2023-01-01 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-13030 | Nethermains - Solar Farm | solar | 0.0075 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-13054 | Moorhouse Farm, Moorhouse Lane - Solar Park | solar | 0.00381 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-13104 | Chertsey Water Treatment Works | solar | 0.0013 | GW | 2022-04-01 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-13131 | M Sport, Dovenby Hall Estate - Solar Panels | solar | 0.0008 | GW | 2023-10-01 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-13162 | Wieland Nemco, Pennard Close - Solar panels | solar | 0.00015 | GW | 2023-06-01 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-13197 | Nevendon Battery Storage Extension | storage_power | 0.005 | GW | 2024-10-23 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-13197-energy | Nevendon Battery Storage Extension | storage_energy | 0.0093095 | GWh | 2024-10-23 | 2039-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-13225 | Merchiston Industrial Estate, Smith Street - Battery Storage | storage_power | 0.043 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-13225-energy | Merchiston Industrial Estate, Smith Street - Battery Storage | storage_energy | 0.080062 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-13250 | Shewalton Landfill Solar Farm | solar | 0.005 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-13251 | Northfield House Solar Farm | solar | 0.026 | GW | 2023-02-15 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-13362 | Carrington Power Station, Manchester Road - Battery Storage | storage_power | 0.68 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-13362-energy | Carrington Power Station, Manchester Road - Battery Storage | storage_energy | 1.2661 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-13370 | Grimsby West, Birchin Way - Solar Array | solar | 0.00112 | GW | 2024-01-01 | 2054-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-13381 | HSH Coldstores, Estate Road - Solar Panels | solar | 0.00108 | GW | 2024-01-10 | 2054-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-13443 | Souber Dairy, Bank Newton - Solar Panels | solar | 0.00019 | GW | 2022-10-31 | 2052-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-13475 | Eastcroft Municipal Depot | solar | 0.00018 | GW | 2023-03-20 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-13476 | Eastcroft Municipal Depot | storage_power | 0.0006 | GW | 2023-03-20 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-13476-energy | Eastcroft Municipal Depot | storage_energy | 0.0011171 | GWh | 2023-03-20 | 2038-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-13519 | Top Farm, Short Ferry Road - Solar PV Arrays | solar | 0.00086 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-13636 | Rolleston Park Farm, Lodge Hill - Solar Farm | solar | 0.012 | GW | 2026-06-01 | 2056-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-13697 | Hoods Close - Solar Panels | solar | 0.0017 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-13740 | Welkin Road, Bredbury - Battery Storage System | storage_power | 0.02 | GW | 2026-01-05 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-13740-energy | Welkin Road, Bredbury - Battery Storage System | storage_energy | 0.037238 | GWh | 2026-01-05 | 2041-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-13791 | Coed Ely - Solar Farm | solar | 0.006 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-13882 | King Edwards School, North Road - Solar Panels | solar | 0.00022 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-13904 | University Of East London - 650 Student accommodation & Teaching and learning | solar | 0.00018 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-13932 | New England Industrial Estate Development | solar | 0.00022 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-13973 | Turnpike Depot - Solar Panels | solar | 0.00048 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-14058 | Eccles II Substation - Battery Energy Storage System | storage_power | 0.5 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-14058-energy | Eccles II Substation - Battery Energy Storage System | storage_energy | 0.93095 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-14068 | Kerry Ingredients & Flavours - Solar Panels | solar | 0.0003 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-14202 | Blair Castle Caravan Park, Blair Atholl - Solar Farm | solar | 0.00016 | GW | 2023-05-01 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-14205 | Darlington Road, Skeeby - Battery Energy Storage | storage_power | 0.035 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-14205-energy | Darlington Road, Skeeby - Battery Energy Storage | storage_energy | 0.065167 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-14217 | Buchanan Gate, Stepps - Solar Panels | solar | 0.00086 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-14233 | Dounreay, Thurso - Battery Energy Storage | storage_power | 0.034 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-14233-energy | Dounreay, Thurso - Battery Energy Storage | storage_energy | 0.063305 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-14237 | Weeton Barracks, Grantham Road - Solar Panels | solar | 0.0007 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-14267 | Carrochan Road, Balloch - Solar Panels | solar | 0.00018 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-14275 | Iomart, Clivemont Road - Solar Panels | solar | 0.00029 | GW | 2024-08-09 | 2054-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-14356 | Whitehall Farm, Llanharry Road - Solar PV Panels | solar | 0.0013 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-14415 | Smart Systems Limited, Arnolds Way - Solar Panels | solar | 0.00293 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-14438 | Excelsior Academy, Denton Road - Solar Panels | solar | 0.00053 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-14707 | LVF Packaging - Solar Panel | solar | 0.0003 | GW | 2023-08-24 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-14748 | Wellington Sports Centre, Corams Lane - Solar Panels | solar | 0.00017 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-14754 | Farnborough Airport - Solar Panels | solar | 0.0017 | GW | 2024-11-12 | 2054-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-14774 | Elstree Film And TV Studios, Shenley Road - Solar Panels | solar | 0.003 | GW | 2023-09-05 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-14798 | Burges Lane, Stoke St Michael - Solar Array Panels | solar | 0.00178 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-14810 | F Lloyd Penley - Solar Panels | solar | 0.00041 | GW | 2023-08-01 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-14930 | Dunmow Solar Farm, Chelmsford Road - Solar Farm | solar | 0.00989 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-14982 | Fairham Business Park, Foresters Avenue - Roof Mounted Solar Panels | solar | 0.00036 | GW | 2023-09-07 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-15002 | Roskilly's - Solar Farm | solar | 0.00021 | GW | 2023-10-04 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-15003 | Lakeside Business Park | solar | 0.0045 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-15004 | Lakeside Business Park | storage_power | 0.002 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-15004-energy | Lakeside Business Park | storage_energy | 0.0037238 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-15049 | Leyes Road - New SEN School | solar | 0.00024 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-15091 | Heck Food, Lime Lane - Solar Panels | solar | 0.00024 | GW | 2024-06-07 | 2054-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-15144 | Watsonhead Wind Farm | onshore | 0.0084 | GW | 2023-10-01 | 2048-01-01 | Operational | Physical project Operational | Retirement estimated at 25 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-15164 | Monk Fryston Battery Storage | storage_power | 0.32 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-15164-energy | Monk Fryston Battery Storage | storage_energy | 0.59581 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-15248 | Rock Farm - Solar Farm | storage_power | 0.012 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-15248-energy | Rock Farm - Solar Farm | storage_energy | 0.022343 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-15263 | Uskmouth Power Station, West Nash Road - Battery Storage Facility | storage_power | 0.12 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-15263-energy | Uskmouth Power Station, West Nash Road - Battery Storage Facility | storage_energy | 0.22343 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-15275 | Goonamarth Farm - Wind Turbine | onshore | 0.0043 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-15340 | Epic Long Ashton, Phase 1 - 3 Office Buildings | solar | 0.00105 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-15343 | Cumberhead West Wind Farm | storage_power | 0.04 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-15343-energy | Cumberhead West Wind Farm | storage_energy | 0.074476 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-15379 | Fleet Hill Solar Farm | solar | 0.0475 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-15451 | Biggin Hill Airport, Main Road - Solar PV Array | solar | 0.012 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-15481 | Cnocbreac Inver Estate - Solar Generation | solar | 0.0021 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-15581 | Farnborough International Exhibition Centre, Etps Road - Solar Panels | solar | 0.00115 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-15591 | Belton Farm, Belton - Solar Pv System | solar | 0.00218 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-15617 | West Farm, Cosheston - Solar Farm | solar | 0.009 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-15732 | Hare Brewery - Solar Panels | solar | 0.00025 | GW | 2024-01-30 | 2054-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-15743 | Pepsico International Limited, Leycroft Road - Solar Panels | solar | 0.00325 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-15874 | HydroGlen Project - Glensaugh Farm | onshore | 0.001 | GW | 2029-01-01 | 2054-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 25 years, with a 2031 floor for listed live assets. Construction completion estimated 2029-01-01. | data/evidence/repd.csv
REPD-15915 | Jones Food Company - Solar Farm | solar | 0.00071 | GW | 2024-02-22 | 2054-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-15973 | Allers Wastewater Treatment Works, Barrie Road - Solar Pv Array | solar | 0.00024 | GW | 2025-01-01 | 2055-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-15994 | Burwell - Battery Storage | storage_power | 0.05 | GW | 2022-02-17 | 2037-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-15994-energy | Burwell - Battery Storage | storage_energy | 0.093095 | GWh | 2022-02-17 | 2037-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-16008 | Sutton Bridge Solar Farm | solar | 0.0499 | GW | 2024-04-01 | 2054-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-16075 | Camilla Battery Storage | storage_power | 0.04999 | GW | 2024-03-20 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-16075-energy | Camilla Battery Storage | storage_energy | 0.093076 | GWh | 2024-03-20 | 2039-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-16119 | City Football Academy, Ashton New Road - Solar panels | solar | 0.00338 | GW | 2026-04-01 | 2056-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-16120 | Mugdock Water Treatment Works - Solar panels | solar | 0.00075 | GW | 2025-06-01 | 2055-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-16366 | Panasonic Manufacturing, Pentwyn - BESS | storage_power | 0.00108 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-16366-energy | Panasonic Manufacturing, Pentwyn - BESS | storage_energy | 0.0020109 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-16367 | Premier Foods Bakery, Fish Dam Lane - Solar Farm | solar | 0.002 | GW | 2025-12-01 | 2055-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-16393 | Cowley Complex, Stockton on Tees | solar | 0.12 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-16426 | Derwentside Environmental Testing Servs Limited - Solar pv panels | solar | 0.00038 | GW | 2023-08-19 | 2053-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-16739 | Rednock School - Solar Panels | solar | 0.00021 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-16871 | Great Western Air Ambulance Charity - Solar Panels | solar | 0.00025 | GW | 2024-08-01 | 2054-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-16962 | Fordham Grange - Solar Panels | solar | 0.00193 | GW | 2026-05-01 | 2056-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-17406 | Stafford Leisure Centre, Lammascote Road - Solar Panels | solar | 0.00026 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-17782 | Woodside Leisure Centre - Solar PV Panels | solar | 0.00029 | GW | 2025-03-01 | 2055-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-18208 | Arclid Sand Quarry - Solar Array | solar | 0.0004 | GW | 2026-06-04 | 2056-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-18382 | Hall Farm, West End Northwold - Solar Farm | solar | 0.01 | GW | 2025-02-28 | 2055-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-18383 | Hall Farm, West End Northwold - Solar Farm | storage_power | 0.0075 | GW | 2025-02-28 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-18383-energy | Hall Farm, West End Northwold - Solar Farm | storage_energy | 0.013964 | GWh | 2025-02-28 | 2040-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-19113 | Cobham Motorway Service Area - Solar Photovoltaics | solar | 0.00045 | GW | 2025-10-01 | 2055-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-19164 | Langford Solar Farm | storage_power | 0.035 | GW | 2025-08-02 | 2040-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-19164-energy | Langford Solar Farm | storage_energy | 0.065167 | GWh | 2025-08-02 | 2040-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-19593 | Monk Fryston Battery Storage | storage_power | 0.057 | GW | 2028-01-01 | 2043-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-19593-energy | Monk Fryston Battery Storage | storage_energy | 0.10613 | GWh | 2028-01-01 | 2043-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-19627 | Alton Sport Centre - Solar Panels | solar | 0.00037 | GW | 2025-03-31 | 2055-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-20319 | Sedbergh Sports and Leisure Centre - Solar PV Installation | solar | 0.0002 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-20326 | Red Bull Racing, Bradbourne Drive - Solar Panels | solar | 0.00056 | GW | 2026-06-01 | 2056-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-20327 | Littlebrook Battery Storage | storage_power | 0.0075 | GW | 2017-12-01 | 2032-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-20327-energy | Littlebrook Battery Storage | storage_energy | 0.013964 | GWh | 2017-12-01 | 2032-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-20328 | Broadditch Battery Energy | storage_power | 0.011 | GW | 2023-03-01 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-20328-energy | Broadditch Battery Energy | storage_energy | 0.020481 | GWh | 2023-03-01 | 2038-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-20381 | Waterswallows Road - Buxton Battery Storage Equipment | storage_power | 0.015 | GW | 2024-04-11 | 2039-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-20381-energy | Waterswallows Road - Buxton Battery Storage Equipment | storage_energy | 0.027929 | GWh | 2024-04-11 | 2039-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-20393 | Charnock Richard - Battery Storage | storage_power | 0.03 | GW | 2026-02-03 | 2041-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-20393-energy | Charnock Richard - Battery Storage | storage_energy | 0.055857 | GWh | 2026-02-03 | 2041-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-20396 | Hutton Battery Storage (Lower Road) | storage_power | 0.01 | GW | 2020-04-01 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-20396-energy | Hutton Battery Storage (Lower Road) | storage_energy | 0.018619 | GWh | 2020-04-01 | 2035-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-20397 | Barnsley Battery Energy Storage | storage_power | 0.04 | GW | 2023-01-01 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-20397-energy | Barnsley Battery Energy Storage | storage_energy | 0.074476 | GWh | 2023-01-01 | 2038-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-20398 | Aylesford BESS | storage_power | 0.029 | GW | 2020-06-01 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-20398-energy | Aylesford BESS | storage_energy | 0.053995 | GWh | 2020-06-01 | 2035-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-20399 | Stonehill Energy Storage / Upper Minety | storage_power | 0.05 | GW | 2020-12-01 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-20399-energy | Stonehill Energy Storage / Upper Minety | storage_energy | 0.093095 | GWh | 2020-12-01 | 2035-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-20400 | Stonehill Energy Storage / Upper Minety | storage_power | 0.05 | GW | 2020-12-01 | 2035-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-20400-energy | Stonehill Energy Storage / Upper Minety | storage_energy | 0.093095 | GWh | 2020-12-01 | 2035-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-20401 | Winchester Battery Storage | storage_power | 0.019 | GW | 2023-05-01 | 2038-01-01 | Operational | Physical project Operational | Retirement estimated at 15 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-20401-energy | Winchester Battery Storage | storage_energy | 0.035376 | GWh | 2023-05-01 | 2038-01-01 | Aggregate/named cohort | Energy estimated from common outlook battery duration | Retirement estimated at 15 years, with a 2031 floor for listed live assets. Each project uses 1.861901h; project-specific energy not established. | data/evidence/tyo2026_es1.csv; data/evidence/repd.csv
REPD-20992 | Wren Kitchens & Bedrooms, Parrott Street - Solar Array | solar | 0.0066 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-21089 | Red Bull Ford Powertrains, Rindt Building, Bradbourne Drive – Solar Panels | solar | 0.00033 | GW | 2024-01-01 | 2054-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
REPD-21090 | Red Bull Racing Wind Tunnel, Sherbourne Drive – Solar Panels | solar | 0.00029 | GW | 2028-01-01 | 2058-01-01 | Under Construction | Physical project Under Construction | Retirement estimated at 30 years, with a 2031 floor for listed live assets. Construction completion estimated 2028-01-01. | data/evidence/repd.csv
REPD-21096 | Principality Stadium, Westgate Street - Solar panels | solar | 0.00149 | GW | 2026-06-12 | 2056-01-01 | Operational | Physical project Operational | Retirement estimated at 30 years, with a 2031 floor for listed live assets. | data/evidence/repd.csv
forecast-storage_power-residual | Unidentified / small-scale storage_power outlook residual | storage_power | 9.9915 | GW | 2030-01-01 | 2045-01-01 | Aggregate/named cohort | Outlook forecast less eligible physical cohorts | Includes unlisted small-scale assets and assumed future completion. Not all contracted. Assumed commissioned2030 for retirement; capital before opening excluded. | data/evidence/tyo2026_es1.csv
forecast-storage-energy-residual | Unidentified battery energy | storage_energy | 18.6032 | GWh | 2030-01-01 | 2045-01-01 | Aggregate/named cohort | Forecast battery energy matched by common duration | Same project assumptions as residual battery power. | data/evidence/tyo2026_es1.csv
opening-pumped-storage_power | Pumped hydro aggregate | storage_power | 2.744 | GW | 2029-01-01 | 2080-01-01 | Aggregate/named cohort | 2030 outlook pumped hydro | Online date is a bookkeeping placeholder for existing assets, not commissioning. Retention to2080 assumed with maintenance; separate cost assumptions. | data/evidence/tyo2026_es1.csv
opening-pumped-storage_energy | Pumped hydro aggregate | storage_energy | 28.004 | GWh | 2029-01-01 | 2080-01-01 | Aggregate/named cohort | 2030 outlook pumped hydro | Online date is a bookkeeping placeholder for existing assets, not commissioning. Retention to2080 assumed with maintenance; separate cost assumptions. | data/evidence/tyo2026_es1.csv
forecast-solar-unlisted-2010 | Unlisted existing solar: estimated 2010 vintage | solar | 0.077332 | GW | 2010-01-01 | 2040-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 30-year life with 2031 retention floor. No automatic repowering. | audit/sources/solar_deployment.xlsx Table_1_by_Capacity GB
forecast-solar-unlisted-2011 | Unlisted existing solar: estimated 2011 vintage | solar | 0.76554 | GW | 2011-01-01 | 2041-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 30-year life with 2031 retention floor. No automatic repowering. | audit/sources/solar_deployment.xlsx Table_1_by_Capacity GB
forecast-solar-unlisted-2012 | Unlisted existing solar: estimated 2012 vintage | solar | 0.65685 | GW | 2012-01-01 | 2042-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 30-year life with 2031 retention floor. No automatic repowering. | audit/sources/solar_deployment.xlsx Table_1_by_Capacity GB
forecast-solar-unlisted-2013 | Unlisted existing solar: estimated 2013 vintage | solar | 0.50376 | GW | 2013-01-01 | 2043-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 30-year life with 2031 retention floor. No automatic repowering. | audit/sources/solar_deployment.xlsx Table_1_by_Capacity GB
forecast-solar-unlisted-2014 | Unlisted existing solar: estimated 2014 vintage | solar | 0.85065 | GW | 2014-01-01 | 2044-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 30-year life with 2031 retention floor. No automatic repowering. | audit/sources/solar_deployment.xlsx Table_1_by_Capacity GB
forecast-solar-unlisted-2015 | Unlisted existing solar: estimated 2015 vintage | solar | 1.3605 | GW | 2015-01-01 | 2045-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 30-year life with 2031 retention floor. No automatic repowering. | audit/sources/solar_deployment.xlsx Table_1_by_Capacity GB
forecast-solar-unlisted-2016 | Unlisted existing solar: estimated 2016 vintage | solar | 0.13239 | GW | 2016-01-01 | 2046-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 30-year life with 2031 retention floor. No automatic repowering. | audit/sources/solar_deployment.xlsx Table_1_by_Capacity GB
forecast-solar-unlisted-2017 | Unlisted existing solar: estimated 2017 vintage | solar | 0.093911 | GW | 2017-01-01 | 2047-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 30-year life with 2031 retention floor. No automatic repowering. | audit/sources/solar_deployment.xlsx Table_1_by_Capacity GB
forecast-solar-unlisted-2019 | Unlisted existing solar: estimated 2019 vintage | solar | 0.24559 | GW | 2019-01-01 | 2049-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 30-year life with 2031 retention floor. No automatic repowering. | audit/sources/solar_deployment.xlsx Table_1_by_Capacity GB
forecast-solar-unlisted-2020 | Unlisted existing solar: estimated 2020 vintage | solar | 0.1817 | GW | 2020-01-01 | 2050-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 30-year life with 2031 retention floor. No automatic repowering. | audit/sources/solar_deployment.xlsx Table_1_by_Capacity GB
forecast-solar-unlisted-2021 | Unlisted existing solar: estimated 2021 vintage | solar | 0.24102 | GW | 2021-01-01 | 2051-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 30-year life with 2031 retention floor. No automatic repowering. | audit/sources/solar_deployment.xlsx Table_1_by_Capacity GB
forecast-solar-unlisted-2022 | Unlisted existing solar: estimated 2022 vintage | solar | 0.63646 | GW | 2022-01-01 | 2052-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 30-year life with 2031 retention floor. No automatic repowering. | audit/sources/solar_deployment.xlsx Table_1_by_Capacity GB
forecast-solar-unlisted-2023 | Unlisted existing solar: estimated 2023 vintage | solar | 1.9771 | GW | 2023-01-01 | 2053-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 30-year life with 2031 retention floor. No automatic repowering. | audit/sources/solar_deployment.xlsx Table_1_by_Capacity GB
forecast-solar-unlisted-2024 | Unlisted existing solar: estimated 2024 vintage | solar | 1.4339 | GW | 2024-01-01 | 2054-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 30-year life with 2031 retention floor. No automatic repowering. | audit/sources/solar_deployment.xlsx Table_1_by_Capacity GB
forecast-solar-unlisted-2025 | Unlisted existing solar: estimated 2025 vintage | solar | 1.8273 | GW | 2025-01-01 | 2055-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 30-year life with 2031 retention floor. No automatic repowering. | audit/sources/solar_deployment.xlsx Table_1_by_Capacity GB
forecast-solar-unlisted-2026 | Unlisted existing solar: estimated 2026 vintage | solar | 0.64658 | GW | 2026-01-01 | 2056-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 30-year life with 2031 retention floor. No automatic repowering. | audit/sources/solar_deployment.xlsx Table_1_by_Capacity GB
forecast-solar-future-2027 | Unidentified future solar: assumed completion 2027 | solar | 4.5104 | GW | 2027-01-01 | 2057-01-01 | Future completion estimate | Outlook forecast less eligible physical cohorts | Remaining 2030 outlook residual after observed unlisted GB stock; equal completion tranches 2027–2030 are an explicit estimate, not contracted projects. 30-year life. | data/evidence/tyo2026_es1.csv
forecast-solar-future-2028 | Unidentified future solar: assumed completion 2028 | solar | 4.5104 | GW | 2028-01-01 | 2058-01-01 | Future completion estimate | Outlook forecast less eligible physical cohorts | Remaining 2030 outlook residual after observed unlisted GB stock; equal completion tranches 2027–2030 are an explicit estimate, not contracted projects. 30-year life. | data/evidence/tyo2026_es1.csv
forecast-solar-future-2029 | Unidentified future solar: assumed completion 2029 | solar | 4.5104 | GW | 2029-01-01 | 2059-01-01 | Future completion estimate | Outlook forecast less eligible physical cohorts | Remaining 2030 outlook residual after observed unlisted GB stock; equal completion tranches 2027–2030 are an explicit estimate, not contracted projects. 30-year life. | data/evidence/tyo2026_es1.csv
forecast-solar-future-2030 | Unidentified future solar: assumed completion 2030 | solar | 4.5104 | GW | 2030-01-01 | 2060-01-01 | Future completion estimate | Outlook forecast less eligible physical cohorts | Remaining 2030 outlook residual after observed unlisted GB stock; equal completion tranches 2027–2030 are an explicit estimate, not contracted projects. 30-year life. | data/evidence/tyo2026_es1.csv
forecast-onshore-unlisted-2010 | Unlisted existing onshore: estimated 2010 vintage | onshore | 0.088665 | GW | 2010-01-01 | 2035-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 25-year life with 2031 retention floor. No automatic repowering. | audit/sources/et61.xlsx GB country quarterly capacity tables
forecast-onshore-unlisted-2011 | Unlisted existing onshore: estimated 2011 vintage | onshore | 0.14108 | GW | 2011-01-01 | 2036-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 25-year life with 2031 retention floor. No automatic repowering. | audit/sources/et61.xlsx GB country quarterly capacity tables
forecast-onshore-unlisted-2013 | Unlisted existing onshore: estimated 2013 vintage | onshore | 0.015184 | GW | 2013-01-01 | 2038-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 25-year life with 2031 retention floor. No automatic repowering. | audit/sources/et61.xlsx GB country quarterly capacity tables
forecast-onshore-unlisted-2014 | Unlisted existing onshore: estimated 2014 vintage | onshore | 0.068998 | GW | 2014-01-01 | 2039-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 25-year life with 2031 retention floor. No automatic repowering. | audit/sources/et61.xlsx GB country quarterly capacity tables
forecast-onshore-unlisted-2015 | Unlisted existing onshore: estimated 2015 vintage | onshore | 0.029414 | GW | 2015-01-01 | 2040-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 25-year life with 2031 retention floor. No automatic repowering. | audit/sources/et61.xlsx GB country quarterly capacity tables
forecast-onshore-unlisted-2016 | Unlisted existing onshore: estimated 2016 vintage | onshore | 0.14963 | GW | 2016-01-01 | 2041-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 25-year life with 2031 retention floor. No automatic repowering. | audit/sources/et61.xlsx GB country quarterly capacity tables
forecast-onshore-unlisted-2019 | Unlisted existing onshore: estimated 2019 vintage | onshore | 0.1166 | GW | 2019-01-01 | 2044-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 25-year life with 2031 retention floor. No automatic repowering. | audit/sources/et61.xlsx GB country quarterly capacity tables
forecast-onshore-unlisted-2021 | Unlisted existing onshore: estimated 2021 vintage | onshore | 0.035885 | GW | 2021-01-01 | 2046-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 25-year life with 2031 retention floor. No automatic repowering. | audit/sources/et61.xlsx GB country quarterly capacity tables
forecast-onshore-unlisted-2022 | Unlisted existing onshore: estimated 2022 vintage | onshore | 0.17227 | GW | 2022-01-01 | 2047-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 25-year life with 2031 retention floor. No automatic repowering. | audit/sources/et61.xlsx GB country quarterly capacity tables
forecast-onshore-unlisted-2023 | Unlisted existing onshore: estimated 2023 vintage | onshore | 0.038512 | GW | 2023-01-01 | 2048-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 25-year life with 2031 retention floor. No automatic repowering. | audit/sources/et61.xlsx GB country quarterly capacity tables
forecast-onshore-unlisted-2024 | Unlisted existing onshore: estimated 2024 vintage | onshore | 0.0067847 | GW | 2024-01-01 | 2049-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 25-year life with 2031 retention floor. No automatic repowering. | audit/sources/et61.xlsx GB country quarterly capacity tables
forecast-onshore-unlisted-2026 | Unlisted existing onshore: estimated 2026 vintage | onshore | 0.19372 | GW | 2026-01-01 | 2051-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 25-year life with 2031 retention floor. No automatic repowering. | audit/sources/et61.xlsx GB country quarterly capacity tables
forecast-onshore-future-2027 | Unidentified future onshore: assumed completion 2027 | onshore | 1.3288 | GW | 2027-01-01 | 2052-01-01 | Future completion estimate | Outlook forecast less eligible physical cohorts | Remaining 2030 outlook residual after observed unlisted GB stock; equal completion tranches 2027–2030 are an explicit estimate, not contracted projects. 25-year life. | data/evidence/tyo2026_es1.csv
forecast-onshore-future-2028 | Unidentified future onshore: assumed completion 2028 | onshore | 1.3288 | GW | 2028-01-01 | 2053-01-01 | Future completion estimate | Outlook forecast less eligible physical cohorts | Remaining 2030 outlook residual after observed unlisted GB stock; equal completion tranches 2027–2030 are an explicit estimate, not contracted projects. 25-year life. | data/evidence/tyo2026_es1.csv
forecast-onshore-future-2029 | Unidentified future onshore: assumed completion 2029 | onshore | 1.3288 | GW | 2029-01-01 | 2054-01-01 | Future completion estimate | Outlook forecast less eligible physical cohorts | Remaining 2030 outlook residual after observed unlisted GB stock; equal completion tranches 2027–2030 are an explicit estimate, not contracted projects. 25-year life. | data/evidence/tyo2026_es1.csv
forecast-onshore-future-2030 | Unidentified future onshore: assumed completion 2030 | onshore | 1.3288 | GW | 2030-01-01 | 2055-01-01 | Future completion estimate | Outlook forecast less eligible physical cohorts | Remaining 2030 outlook residual after observed unlisted GB stock; equal completion tranches 2027–2030 are an explicit estimate, not contracted projects. 25-year life. | data/evidence/tyo2026_es1.csv
forecast-offshore-unlisted-2010 | Unlisted existing offshore: estimated 2010 vintage | offshore | 0.0027432 | GW | 2010-01-01 | 2040-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 30-year life with 2031 retention floor. No automatic repowering. | audit/sources/et61.xlsx GB country quarterly capacity tables
forecast-offshore-unlisted-2011 | Unlisted existing offshore: estimated 2011 vintage | offshore | 0.083822 | GW | 2011-01-01 | 2041-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 30-year life with 2031 retention floor. No automatic repowering. | audit/sources/et61.xlsx GB country quarterly capacity tables
forecast-offshore-unlisted-2012 | Unlisted existing offshore: estimated 2012 vintage | offshore | 0.00069584 | GW | 2012-01-01 | 2042-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 30-year life with 2031 retention floor. No automatic repowering. | audit/sources/et61.xlsx GB country quarterly capacity tables
forecast-offshore-unlisted-2014 | Unlisted existing offshore: estimated 2014 vintage | offshore | 0.10958 | GW | 2014-01-01 | 2044-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 30-year life with 2031 retention floor. No automatic repowering. | audit/sources/et61.xlsx GB country quarterly capacity tables
forecast-offshore-unlisted-2016 | Unlisted existing offshore: estimated 2016 vintage | offshore | 0.053499 | GW | 2016-01-01 | 2046-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 30-year life with 2031 retention floor. No automatic repowering. | audit/sources/et61.xlsx GB country quarterly capacity tables
forecast-offshore-unlisted-2017 | Unlisted existing offshore: estimated 2017 vintage | offshore | 0.073103 | GW | 2017-01-01 | 2047-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 30-year life with 2031 retention floor. No automatic repowering. | audit/sources/et61.xlsx GB country quarterly capacity tables
forecast-offshore-unlisted-2024 | Unlisted existing offshore: estimated 2024 vintage | offshore | 0.37602 | GW | 2024-01-01 | 2054-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 30-year life with 2031 retention floor. No automatic repowering. | audit/sources/et61.xlsx GB country quarterly capacity tables
forecast-offshore-unlisted-2026 | Unlisted existing offshore: estimated 2026 vintage | offshore | 0.022213 | GW | 2026-01-01 | 2056-01-01 | Observed aggregate residual; estimated vintage | GB aggregate at June 2026 less selected REPD operational MW; age allocated from positive annual aggregate additions less listed additions, rescaled to residual total | Estimated vintage, not a named project. Net additions proxy gross commissioning; negative increments clipped and weights rescaled. Earliest bin includes earlier stock. 30-year life with 2031 retention floor. No automatic repowering. | audit/sources/et61.xlsx GB country quarterly capacity tables
forecast-offshore-future-2027 | Unidentified future offshore: assumed completion 2027 | offshore | 1.2618 | GW | 2027-01-01 | 2057-01-01 | Future completion estimate | Outlook forecast less eligible physical cohorts | Remaining 2030 outlook residual after observed unlisted GB stock; equal completion tranches 2027–2030 are an explicit estimate, not contracted projects. 30-year life. | data/evidence/tyo2026_es1.csv
forecast-offshore-future-2028 | Unidentified future offshore: assumed completion 2028 | offshore | 1.2618 | GW | 2028-01-01 | 2058-01-01 | Future completion estimate | Outlook forecast less eligible physical cohorts | Remaining 2030 outlook residual after observed unlisted GB stock; equal completion tranches 2027–2030 are an explicit estimate, not contracted projects. 30-year life. | data/evidence/tyo2026_es1.csv
forecast-offshore-future-2029 | Unidentified future offshore: assumed completion 2029 | offshore | 1.2618 | GW | 2029-01-01 | 2059-01-01 | Future completion estimate | Outlook forecast less eligible physical cohorts | Remaining 2030 outlook residual after observed unlisted GB stock; equal completion tranches 2027–2030 are an explicit estimate, not contracted projects. 30-year life. | data/evidence/tyo2026_es1.csv
forecast-offshore-future-2030 | Unidentified future offshore: assumed completion 2030 | offshore | 1.2618 | GW | 2030-01-01 | 2060-01-01 | Future completion estimate | Outlook forecast less eligible physical cohorts | Remaining 2030 outlook residual after observed unlisted GB stock; equal completion tranches 2027–2030 are an explicit estimate, not contracted projects. 30-year life. | data/evidence/tyo2026_es1.csv

## Build orders
The six saved construction schedules
Six mixed-gas programmes and three unchanged clean-target plans. CCGT 920 MW units, OCGT 300 MW units and 100 MW engine sites (five 20 MW engines). Four-year CCGT, three-year OCGT and two-year engine leads; no discretionary orders before 2029. Supplier capacity is unconfirmed. Wylfa is inherited: unit delivery in 2035 for all three units is assumed, not a published annual commissioning sequence. Repeat SMR orders follow a conditional 2034 gate. Target cases remove only additional adequacy gas orders; retained gas capacity has an annual output quota. New gas orders start in 2029 or later. Separate planning/connection allowances are excluded unless entered.
Programme | Demand | ID | Technology | Units | Unit GW | Unit GWh | Start | Online | Retire | Recovery | Planning bn | Connection bn | Status | Source
ours | low | offshore-2030-0 | offshore | 13 | 1 | 0 | 2026 | 2030 | 2060 | 30 |  |  | Retained dated assumption | demand_plans/ours_low.plan.json
ours | low | offshore-2031-8 | offshore | 7 | 1 | 0 | 2027 | 2031 | 2061 | 30 |  |  | Retained dated assumption | demand_plans/ours_low.plan.json
ours | low | battery-2030-3 | battery | 1 | 1 | 4 | 2028 | 2030 | 2045 | 15 |  |  | Retained dated assumption | demand_plans/ours_low.plan.json
ours | low | offshore-2032-12 | offshore | 7 | 1 | 0 | 2028 | 2032 | 2062 | 30 |  |  | Retained dated assumption | demand_plans/ours_low.plan.json
ours | low | onshore-2030-1 | onshore | 54 | 0.1 | 0 | 2028 | 2030 | 2055 | 25 |  |  | Retained dated assumption | demand_plans/ours_low.plan.json
ours | low | solar-2030-2 | solar | 117 | 0.1 | 0 | 2028 | 2030 | 2060 | 30 |  |  | Retained dated assumption | demand_plans/ours_low.plan.json
ours | low | coal-2035 | coal | 1 | 2 | 0 | 2029 | 2035 | 2085 | 50 |  |  | M49 additional coal | demand_plans/ours_low.plan.json
ours | low | mixed-gas-2033 | gas | 4 | 0.92 | 0 | 2029 | 2033 | 2068 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_low.plan.json
ours | low | mixed-gas_engine-2031 | gas_engine | 40 | 0.1 | 0 | 2029 | 2031 | 2061 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_low.plan.json
ours | low | large-nuclear-2037 | nuclear | 1 | 1.7 | 0 | 2029 | 2037 | 2097 | 60 |  |  | Retained dated assumption | demand_plans/ours_low.plan.json
ours | low | coal-2036 | coal | 1 | 2 | 0 | 2030 | 2036 | 2086 | 50 |  |  | M49 additional coal | demand_plans/ours_low.plan.json
ours | low | mixed-gas-2034 | gas | 4 | 0.92 | 0 | 2030 | 2034 | 2069 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_low.plan.json
ours | low | mixed-gas_engine-2032 | gas_engine | 40 | 0.1 | 0 | 2030 | 2032 | 2062 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_low.plan.json
ours | low | pilot-nuclear-2035-5 | nuclear | 1 | 0.47 | 0 | 2030 | 2035 | 2095 | 60 |  |  | Retained dated assumption | demand_plans/ours_low.plan.json
ours | low | pilot-nuclear-2036-6 | nuclear | 1 | 0.47 | 0 | 2030 | 2035 | 2095 | 60 |  |  | Retained dated assumption | demand_plans/ours_low.plan.json
ours | low | pilot-nuclear-2037-7 | nuclear | 1 | 0.47 | 0 | 2030 | 2035 | 2095 | 60 |  |  | Retained dated assumption | demand_plans/ours_low.plan.json
ours | low | coal-2037 | coal | 1 | 2 | 0 | 2031 | 2037 | 2087 | 50 |  |  | M49 additional coal | demand_plans/ours_low.plan.json
ours | low | mixed-gas-2035 | gas | 4 | 0.92 | 0 | 2031 | 2035 | 2070 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_low.plan.json
ours | low | mixed-gas_engine-2033 | gas_engine | 36 | 0.1 | 0 | 2031 | 2033 | 2063 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_low.plan.json
ours | low | coal-2038 | coal | 1 | 2 | 0 | 2032 | 2038 | 2088 | 50 |  |  | M49 additional coal | demand_plans/ours_low.plan.json
ours | low | mixed-gas-2036 | gas | 4 | 0.92 | 0 | 2032 | 2036 | 2071 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_low.plan.json
ours | low | mixed-gas_engine-2034 | gas_engine | 36 | 0.1 | 0 | 2032 | 2034 | 2064 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_low.plan.json
ours | low | mixed-gas-2037 | gas | 4 | 0.92 | 0 | 2033 | 2037 | 2072 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_low.plan.json
ours | low | mixed-gas_engine-2035 | gas_engine | 36 | 0.1 | 0 | 2033 | 2035 | 2065 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_low.plan.json
ours | low | mixed-gas-2038 | gas | 2 | 0.92 | 0 | 2034 | 2038 | 2073 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_low.plan.json
ours | low | mixed-gas_engine-2036 | gas_engine | 9 | 0.1 | 0 | 2034 | 2036 | 2066 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_low.plan.json
ours | low | repeat-smr-2039 | nuclear | 2 | 0.47 | 0 | 2034 | 2039 | 2099 | 60 |  |  | Retained dated assumption | demand_plans/ours_low.plan.json
ours | low | mixed-gas-2039 | gas | 1 | 0.92 | 0 | 2035 | 2039 | 2074 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_low.plan.json
ours | low | repeat-smr-2040 | nuclear | 4 | 0.47 | 0 | 2035 | 2040 | 2100 | 60 |  |  | Retained dated assumption | demand_plans/ours_low.plan.json
ours | low | mixed-gas-2040 | gas | 2 | 0.92 | 0 | 2036 | 2040 | 2075 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_low.plan.json
ours | low | repeat-smr-2041 | nuclear | 6 | 0.47 | 0 | 2036 | 2041 | 2101 | 60 |  |  | Retained dated assumption | demand_plans/ours_low.plan.json
ours | low | mixed-gas-2041 | gas | 1 | 0.92 | 0 | 2037 | 2041 | 2076 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_low.plan.json
ours | low | repeat-smr-2042 | nuclear | 8 | 0.47 | 0 | 2037 | 2042 | 2102 | 60 |  |  | Retained dated assumption | demand_plans/ours_low.plan.json
ours | low | repeat-smr-2043 | nuclear | 8 | 0.47 | 0 | 2038 | 2043 | 2103 | 60 |  |  | Retained dated assumption | demand_plans/ours_low.plan.json
ours | low | mixed-gas-2043 | gas | 1 | 0.92 | 0 | 2039 | 2043 | 2078 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_low.plan.json
ours | low | repeat-smr-2044 | nuclear | 8 | 0.47 | 0 | 2039 | 2044 | 2104 | 60 |  |  | Retained dated assumption | demand_plans/ours_low.plan.json
ours | low | mixed-gas-2044 | gas | 1 | 0.92 | 0 | 2040 | 2044 | 2079 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_low.plan.json
ours | low | mixed-gas_engine-2042 | gas_engine | 8 | 0.1 | 0 | 2040 | 2042 | 2072 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_low.plan.json
ours | low | repeat-smr-2045 | nuclear | 8 | 0.47 | 0 | 2040 | 2045 | 2105 | 60 |  |  | Retained dated assumption | demand_plans/ours_low.plan.json
ours | low | mixed-gas-2045 | gas | 3 | 0.92 | 0 | 2041 | 2045 | 2080 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_low.plan.json
ours | low | repeat-smr-2046 | nuclear | 8 | 0.47 | 0 | 2041 | 2046 | 2106 | 60 |  |  | Retained dated assumption | demand_plans/ours_low.plan.json
ours | low | repeat-smr-2047 | nuclear | 8 | 0.47 | 0 | 2042 | 2047 | 2107 | 60 |  |  | Retained dated assumption | demand_plans/ours_low.plan.json
ours | low | mixed-gas_engine-2045 | gas_engine | 23 | 0.1 | 0 | 2043 | 2045 | 2075 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_low.plan.json
ours | low | repeat-smr-2048 | nuclear | 5 | 0.47 | 0 | 2043 | 2048 | 2108 | 60 |  |  | Retained dated assumption | demand_plans/ours_low.plan.json
ours | low | repeat-smr-2049 | nuclear | 1 | 0.47 | 0 | 2044 | 2049 | 2109 | 60 |  |  | Retained dated assumption | demand_plans/ours_low.plan.json
ours | low | repeat-smr-2050 | nuclear | 2 | 0.47 | 0 | 2045 | 2050 | 2110 | 60 |  |  | Retained dated assumption | demand_plans/ours_low.plan.json
ours | low | mixed-gas-2050 | gas | 2 | 0.92 | 0 | 2046 | 2050 | 2085 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_low.plan.json
ours | low | mixed-gas_engine-2050 | gas_engine | 19 | 0.1 | 0 | 2048 | 2050 | 2080 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_low.plan.json
ours | central | offshore-2030-0 | offshore | 13 | 1 | 0 | 2026 | 2030 | 2060 | 30 |  |  | Retained dated assumption | demand_plans/ours_central.plan.json
ours | central | offshore-2031-8 | offshore | 7 | 1 | 0 | 2027 | 2031 | 2061 | 30 |  |  | Retained dated assumption | demand_plans/ours_central.plan.json
ours | central | battery-2030-3 | battery | 1 | 1 | 4 | 2028 | 2030 | 2045 | 15 |  |  | Retained dated assumption | demand_plans/ours_central.plan.json
ours | central | offshore-2032-12 | offshore | 7 | 1 | 0 | 2028 | 2032 | 2062 | 30 |  |  | Retained dated assumption | demand_plans/ours_central.plan.json
ours | central | onshore-2030-1 | onshore | 54 | 0.1 | 0 | 2028 | 2030 | 2055 | 25 |  |  | Retained dated assumption | demand_plans/ours_central.plan.json
ours | central | solar-2030-2 | solar | 117 | 0.1 | 0 | 2028 | 2030 | 2060 | 30 |  |  | Retained dated assumption | demand_plans/ours_central.plan.json
ours | central | coal-2035 | coal | 1 | 2 | 0 | 2029 | 2035 | 2085 | 50 |  |  | M49 additional coal | demand_plans/ours_central.plan.json
ours | central | mixed-gas-2033 | gas | 4 | 0.92 | 0 | 2029 | 2033 | 2068 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_central.plan.json
ours | central | mixed-gas_engine-2031 | gas_engine | 40 | 0.1 | 0 | 2029 | 2031 | 2061 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_central.plan.json
ours | central | large-nuclear-2037 | nuclear | 1 | 1.7 | 0 | 2029 | 2037 | 2097 | 60 |  |  | Retained dated assumption | demand_plans/ours_central.plan.json
ours | central | coal-2036 | coal | 1 | 2 | 0 | 2030 | 2036 | 2086 | 50 |  |  | M49 additional coal | demand_plans/ours_central.plan.json
ours | central | mixed-gas-2034 | gas | 4 | 0.92 | 0 | 2030 | 2034 | 2069 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_central.plan.json
ours | central | mixed-gas_engine-2032 | gas_engine | 40 | 0.1 | 0 | 2030 | 2032 | 2062 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_central.plan.json
ours | central | pilot-nuclear-2035-5 | nuclear | 1 | 0.47 | 0 | 2030 | 2035 | 2095 | 60 |  |  | Retained dated assumption | demand_plans/ours_central.plan.json
ours | central | pilot-nuclear-2036-6 | nuclear | 1 | 0.47 | 0 | 2030 | 2035 | 2095 | 60 |  |  | Retained dated assumption | demand_plans/ours_central.plan.json
ours | central | pilot-nuclear-2037-7 | nuclear | 1 | 0.47 | 0 | 2030 | 2035 | 2095 | 60 |  |  | Retained dated assumption | demand_plans/ours_central.plan.json
ours | central | coal-2037 | coal | 1 | 2 | 0 | 2031 | 2037 | 2087 | 50 |  |  | M49 additional coal | demand_plans/ours_central.plan.json
ours | central | mixed-gas-2035 | gas | 4 | 0.92 | 0 | 2031 | 2035 | 2070 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_central.plan.json
ours | central | mixed-gas_engine-2033 | gas_engine | 36 | 0.1 | 0 | 2031 | 2033 | 2063 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_central.plan.json
ours | central | coal-2038 | coal | 1 | 2 | 0 | 2032 | 2038 | 2088 | 50 |  |  | M49 additional coal | demand_plans/ours_central.plan.json
ours | central | mixed-gas-2036 | gas | 4 | 0.92 | 0 | 2032 | 2036 | 2071 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_central.plan.json
ours | central | mixed-gas_engine-2034 | gas_engine | 36 | 0.1 | 0 | 2032 | 2034 | 2064 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_central.plan.json
ours | central | mixed-gas-2037 | gas | 4 | 0.92 | 0 | 2033 | 2037 | 2072 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_central.plan.json
ours | central | mixed-gas_engine-2035 | gas_engine | 36 | 0.1 | 0 | 2033 | 2035 | 2065 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_central.plan.json
ours | central | mixed-gas-2038 | gas | 4 | 0.92 | 0 | 2034 | 2038 | 2073 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_central.plan.json
ours | central | mixed-gas_engine-2036 | gas_engine | 36 | 0.1 | 0 | 2034 | 2036 | 2066 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_central.plan.json
ours | central | repeat-smr-2039 | nuclear | 2 | 0.47 | 0 | 2034 | 2039 | 2099 | 60 |  |  | Retained dated assumption | demand_plans/ours_central.plan.json
ours | central | mixed-gas-2039 | gas | 4 | 0.92 | 0 | 2035 | 2039 | 2074 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_central.plan.json
ours | central | mixed-gas_engine-2037 | gas_engine | 36 | 0.1 | 0 | 2035 | 2037 | 2067 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_central.plan.json
ours | central | repeat-smr-2040 | nuclear | 4 | 0.47 | 0 | 2035 | 2040 | 2100 | 60 |  |  | Retained dated assumption | demand_plans/ours_central.plan.json
ours | central | mixed-gas-2040 | gas | 4 | 0.92 | 0 | 2036 | 2040 | 2075 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_central.plan.json
ours | central | mixed-gas_engine-2038 | gas_engine | 21 | 0.1 | 0 | 2036 | 2038 | 2068 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_central.plan.json
ours | central | repeat-smr-2041 | nuclear | 6 | 0.47 | 0 | 2036 | 2041 | 2101 | 60 |  |  | Retained dated assumption | demand_plans/ours_central.plan.json
ours | central | mixed-gas-2041 | gas | 4 | 0.92 | 0 | 2037 | 2041 | 2076 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_central.plan.json
ours | central | mixed-gas_engine-2039 | gas_engine | 3 | 0.1 | 0 | 2037 | 2039 | 2069 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_central.plan.json
ours | central | repeat-smr-2042 | nuclear | 8 | 0.47 | 0 | 2037 | 2042 | 2102 | 60 |  |  | Retained dated assumption | demand_plans/ours_central.plan.json
ours | central | mixed-gas_engine-2040 | gas_engine | 27 | 0.1 | 0 | 2038 | 2040 | 2070 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_central.plan.json
ours | central | repeat-smr-2043 | nuclear | 8 | 0.47 | 0 | 2038 | 2043 | 2103 | 60 |  |  | Retained dated assumption | demand_plans/ours_central.plan.json
ours | central | mixed-gas-2043 | gas | 1 | 0.92 | 0 | 2039 | 2043 | 2078 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_central.plan.json
ours | central | repeat-smr-2044 | nuclear | 8 | 0.47 | 0 | 2039 | 2044 | 2104 | 60 |  |  | Retained dated assumption | demand_plans/ours_central.plan.json
ours | central | mixed-gas-2044 | gas | 1 | 0.92 | 0 | 2040 | 2044 | 2079 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_central.plan.json
ours | central | repeat-smr-2045 | nuclear | 8 | 0.47 | 0 | 2040 | 2045 | 2105 | 60 |  |  | Retained dated assumption | demand_plans/ours_central.plan.json
ours | central | mixed-gas-2045 | gas | 2 | 0.92 | 0 | 2041 | 2045 | 2080 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_central.plan.json
ours | central | repeat-smr-2046 | nuclear | 8 | 0.47 | 0 | 2041 | 2046 | 2106 | 60 |  |  | Retained dated assumption | demand_plans/ours_central.plan.json
ours | central | repeat-smr-2047 | nuclear | 8 | 0.47 | 0 | 2042 | 2047 | 2107 | 60 |  |  | Retained dated assumption | demand_plans/ours_central.plan.json
ours | central | mixed-gas_engine-2045 | gas_engine | 10 | 0.1 | 0 | 2043 | 2045 | 2075 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_central.plan.json
ours | central | repeat-smr-2048 | nuclear | 8 | 0.47 | 0 | 2043 | 2048 | 2108 | 60 |  |  | Retained dated assumption | demand_plans/ours_central.plan.json
ours | central | repeat-smr-2049 | nuclear | 8 | 0.47 | 0 | 2044 | 2049 | 2109 | 60 |  |  | Retained dated assumption | demand_plans/ours_central.plan.json
ours | central | repeat-smr-2050 | nuclear | 8 | 0.47 | 0 | 2045 | 2050 | 2110 | 60 |  |  | Retained dated assumption | demand_plans/ours_central.plan.json
ours | high | offshore-2030-0 | offshore | 13 | 1 | 0 | 2026 | 2030 | 2060 | 30 |  |  | Retained dated assumption | demand_plans/ours_high.plan.json
ours | high | offshore-2031-8 | offshore | 7 | 1 | 0 | 2027 | 2031 | 2061 | 30 |  |  | Retained dated assumption | demand_plans/ours_high.plan.json
ours | high | battery-2030-3 | battery | 1 | 1 | 4 | 2028 | 2030 | 2045 | 15 |  |  | Retained dated assumption | demand_plans/ours_high.plan.json
ours | high | offshore-2032-12 | offshore | 7 | 1 | 0 | 2028 | 2032 | 2062 | 30 |  |  | Retained dated assumption | demand_plans/ours_high.plan.json
ours | high | onshore-2030-1 | onshore | 54 | 0.1 | 0 | 2028 | 2030 | 2055 | 25 |  |  | Retained dated assumption | demand_plans/ours_high.plan.json
ours | high | solar-2030-2 | solar | 117 | 0.1 | 0 | 2028 | 2030 | 2060 | 30 |  |  | Retained dated assumption | demand_plans/ours_high.plan.json
ours | high | coal-2035 | coal | 1 | 2 | 0 | 2029 | 2035 | 2085 | 50 |  |  | M49 additional coal | demand_plans/ours_high.plan.json
ours | high | mixed-gas-2033 | gas | 4 | 0.92 | 0 | 2029 | 2033 | 2068 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
ours | high | mixed-gas_engine-2031 | gas_engine | 40 | 0.1 | 0 | 2029 | 2031 | 2061 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
ours | high | large-nuclear-2037 | nuclear | 1 | 1.7 | 0 | 2029 | 2037 | 2097 | 60 |  |  | Retained dated assumption | demand_plans/ours_high.plan.json
ours | high | coal-2036 | coal | 1 | 2 | 0 | 2030 | 2036 | 2086 | 50 |  |  | M49 additional coal | demand_plans/ours_high.plan.json
ours | high | mixed-gas-2034 | gas | 4 | 0.92 | 0 | 2030 | 2034 | 2069 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
ours | high | mixed-gas_engine-2032 | gas_engine | 40 | 0.1 | 0 | 2030 | 2032 | 2062 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
ours | high | pilot-nuclear-2035-5 | nuclear | 1 | 0.47 | 0 | 2030 | 2035 | 2095 | 60 |  |  | Retained dated assumption | demand_plans/ours_high.plan.json
ours | high | pilot-nuclear-2036-6 | nuclear | 1 | 0.47 | 0 | 2030 | 2035 | 2095 | 60 |  |  | Retained dated assumption | demand_plans/ours_high.plan.json
ours | high | pilot-nuclear-2037-7 | nuclear | 1 | 0.47 | 0 | 2030 | 2035 | 2095 | 60 |  |  | Retained dated assumption | demand_plans/ours_high.plan.json
ours | high | coal-2037 | coal | 1 | 2 | 0 | 2031 | 2037 | 2087 | 50 |  |  | M49 additional coal | demand_plans/ours_high.plan.json
ours | high | mixed-gas-2035 | gas | 4 | 0.92 | 0 | 2031 | 2035 | 2070 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
ours | high | mixed-gas_engine-2033 | gas_engine | 36 | 0.1 | 0 | 2031 | 2033 | 2063 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
ours | high | coal-2038 | coal | 1 | 2 | 0 | 2032 | 2038 | 2088 | 50 |  |  | M49 additional coal | demand_plans/ours_high.plan.json
ours | high | mixed-gas-2036 | gas | 4 | 0.92 | 0 | 2032 | 2036 | 2071 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
ours | high | mixed-gas_engine-2034 | gas_engine | 36 | 0.1 | 0 | 2032 | 2034 | 2064 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
ours | high | mixed-gas-2037 | gas | 4 | 0.92 | 0 | 2033 | 2037 | 2072 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
ours | high | mixed-gas_engine-2035 | gas_engine | 36 | 0.1 | 0 | 2033 | 2035 | 2065 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
ours | high | mixed-gas-2038 | gas | 4 | 0.92 | 0 | 2034 | 2038 | 2073 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
ours | high | mixed-gas_engine-2036 | gas_engine | 36 | 0.1 | 0 | 2034 | 2036 | 2066 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
ours | high | repeat-smr-2039 | nuclear | 2 | 0.47 | 0 | 2034 | 2039 | 2099 | 60 |  |  | Retained dated assumption | demand_plans/ours_high.plan.json
ours | high | mixed-gas-2039 | gas | 4 | 0.92 | 0 | 2035 | 2039 | 2074 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
ours | high | mixed-gas_engine-2037 | gas_engine | 36 | 0.1 | 0 | 2035 | 2037 | 2067 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
ours | high | repeat-smr-2040 | nuclear | 4 | 0.47 | 0 | 2035 | 2040 | 2100 | 60 |  |  | Retained dated assumption | demand_plans/ours_high.plan.json
ours | high | mixed-gas-2040 | gas | 4 | 0.92 | 0 | 2036 | 2040 | 2075 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
ours | high | mixed-gas_engine-2038 | gas_engine | 36 | 0.1 | 0 | 2036 | 2038 | 2068 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
ours | high | repeat-smr-2041 | nuclear | 6 | 0.47 | 0 | 2036 | 2041 | 2101 | 60 |  |  | Retained dated assumption | demand_plans/ours_high.plan.json
ours | high | mixed-gas-2041 | gas | 4 | 0.92 | 0 | 2037 | 2041 | 2076 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
ours | high | mixed-gas_engine-2039 | gas_engine | 36 | 0.1 | 0 | 2037 | 2039 | 2069 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
ours | high | repeat-smr-2042 | nuclear | 8 | 0.47 | 0 | 2037 | 2042 | 2102 | 60 |  |  | Retained dated assumption | demand_plans/ours_high.plan.json
ours | high | mixed-gas-2042 | gas | 4 | 0.92 | 0 | 2038 | 2042 | 2077 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
ours | high | mixed-gas_engine-2040 | gas_engine | 36 | 0.1 | 0 | 2038 | 2040 | 2070 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
ours | high | repeat-smr-2043 | nuclear | 8 | 0.47 | 0 | 2038 | 2043 | 2103 | 60 |  |  | Retained dated assumption | demand_plans/ours_high.plan.json
ours | high | mixed-gas-2043 | gas | 4 | 0.92 | 0 | 2039 | 2043 | 2078 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
ours | high | mixed-gas_engine-2041 | gas_engine | 36 | 0.1 | 0 | 2039 | 2041 | 2071 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
ours | high | repeat-smr-2044 | nuclear | 8 | 0.47 | 0 | 2039 | 2044 | 2104 | 60 |  |  | Retained dated assumption | demand_plans/ours_high.plan.json
ours | high | mixed-gas-2044 | gas | 4 | 0.92 | 0 | 2040 | 2044 | 2079 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
ours | high | mixed-gas_engine-2042 | gas_engine | 36 | 0.1 | 0 | 2040 | 2042 | 2072 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
ours | high | repeat-smr-2045 | nuclear | 8 | 0.47 | 0 | 2040 | 2045 | 2105 | 60 |  |  | Retained dated assumption | demand_plans/ours_high.plan.json
ours | high | mixed-gas-2045 | gas | 4 | 0.92 | 0 | 2041 | 2045 | 2080 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
ours | high | mixed-gas_engine-2043 | gas_engine | 36 | 0.1 | 0 | 2041 | 2043 | 2073 | 30 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
ours | high | repeat-smr-2046 | nuclear | 8 | 0.47 | 0 | 2041 | 2046 | 2106 | 60 |  |  | Retained dated assumption | demand_plans/ours_high.plan.json
ours | high | mixed-gas-2046 | gas | 1 | 0.92 | 0 | 2042 | 2046 | 2081 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
ours | high | repeat-smr-2047 | nuclear | 8 | 0.47 | 0 | 2042 | 2047 | 2107 | 60 |  |  | Retained dated assumption | demand_plans/ours_high.plan.json
ours | high | repeat-smr-2048 | nuclear | 8 | 0.47 | 0 | 2043 | 2048 | 2108 | 60 |  |  | Retained dated assumption | demand_plans/ours_high.plan.json
ours | high | repeat-smr-2049 | nuclear | 8 | 0.47 | 0 | 2044 | 2049 | 2109 | 60 |  |  | Retained dated assumption | demand_plans/ours_high.plan.json
ours | high | repeat-smr-2050 | nuclear | 8 | 0.47 | 0 | 2045 | 2050 | 2110 | 60 |  |  | Retained dated assumption | demand_plans/ours_high.plan.json
ours | high | mixed-gas-2050 | gas | 1 | 0.92 | 0 | 2046 | 2050 | 2085 | 35 |  |  | M48 mixed-gas candidate | demand_plans/ours_high.plan.json
government | low | offshore-2030-0 | offshore | 13 | 1 | 0 | 2026 | 2030 | 2060 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | offshore-2031-8 | offshore | 7 | 1 | 0 | 2027 | 2031 | 2061 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | battery-2030-3 | battery | 1 | 1 | 4 | 2028 | 2030 | 2045 | 15 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | offshore-2032-12 | offshore | 7 | 1 | 0 | 2028 | 2032 | 2062 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | onshore-2030-1 | onshore | 54 | 0.1 | 0 | 2028 | 2030 | 2055 | 25 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | solar-2030-2 | solar | 117 | 0.1 | 0 | 2028 | 2030 | 2060 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | mixed-gas-2033 | gas | 4 | 0.92 | 0 | 2029 | 2033 | 2068 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_low.plan.json
government | low | mixed-gas_engine-2031 | gas_engine | 40 | 0.1 | 0 | 2029 | 2031 | 2061 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_low.plan.json
government | low | adaptive-onshore-2031 | onshore | 14 | 0.1 | 0 | 2029 | 2031 | 2056 | 25 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | mixed-gas-2034 | gas | 4 | 0.92 | 0 | 2030 | 2034 | 2069 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_low.plan.json
government | low | mixed-gas_engine-2032 | gas_engine | 40 | 0.1 | 0 | 2030 | 2032 | 2062 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_low.plan.json
government | low | nuclear-2035-5 | nuclear | 1 | 0.47 | 0 | 2030 | 2035 | 2095 | 60 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | nuclear-2036-6 | nuclear | 1 | 0.47 | 0 | 2030 | 2035 | 2095 | 60 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | nuclear-2037-7 | nuclear | 1 | 0.47 | 0 | 2030 | 2035 | 2095 | 60 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-offshore-2034 | offshore | 6 | 1 | 0 | 2030 | 2034 | 2064 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-onshore-2032 | onshore | 14 | 0.1 | 0 | 2030 | 2032 | 2057 | 25 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | mixed-gas-2035 | gas | 4 | 0.92 | 0 | 2031 | 2035 | 2070 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_low.plan.json
government | low | mixed-gas_engine-2033 | gas_engine | 36 | 0.1 | 0 | 2031 | 2033 | 2063 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_low.plan.json
government | low | adaptive-offshore-2035 | offshore | 4 | 1 | 0 | 2031 | 2035 | 2065 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-onshore-2033 | onshore | 14 | 0.1 | 0 | 2031 | 2033 | 2058 | 25 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-solar-2033 | solar | 2 | 0.1 | 0 | 2031 | 2033 | 2063 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | gas-2030-4 | gas | 1 | 0.92 | 0 | 2032 | 2036 | 2071 | 35 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | mixed-gas-2036 | gas | 2 | 0.92 | 0 | 2032 | 2036 | 2071 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_low.plan.json
government | low | mixed-gas_engine-2034 | gas_engine | 21 | 0.1 | 0 | 2032 | 2034 | 2064 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_low.plan.json
government | low | adaptive-offshore-2036 | offshore | 2 | 1 | 0 | 2032 | 2036 | 2066 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-onshore-2034 | onshore | 12 | 0.1 | 0 | 2032 | 2034 | 2059 | 25 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-solar-2034 | solar | 10 | 0.1 | 0 | 2032 | 2034 | 2064 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | gas-2031-11 | gas | 1 | 0.92 | 0 | 2033 | 2037 | 2072 | 35 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | gas-2032-16 | gas | 1 | 0.92 | 0 | 2033 | 2037 | 2072 | 35 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | mixed-gas-2037 | gas | 1 | 0.92 | 0 | 2033 | 2037 | 2072 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_low.plan.json
government | low | adaptive-offshore-2037 | offshore | 2 | 1 | 0 | 2033 | 2037 | 2067 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-onshore-2035 | onshore | 12 | 0.1 | 0 | 2033 | 2035 | 2060 | 25 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-solar-2035 | solar | 6 | 0.1 | 0 | 2033 | 2035 | 2065 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-battery-2036 | battery | 1 | 1 | 4 | 2034 | 2036 | 2051 | 15 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-gas-2038 | gas | 2 | 0.92 | 0 | 2034 | 2038 | 2073 | 35 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | mixed-gas-2038 | gas | 1 | 0.92 | 0 | 2034 | 2038 | 2073 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_low.plan.json
government | low | adaptive-offshore-2038 | offshore | 3 | 1 | 0 | 2034 | 2038 | 2068 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-onshore-2036 | onshore | 14 | 0.1 | 0 | 2034 | 2036 | 2061 | 25 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-solar-2036 | solar | 17 | 0.1 | 0 | 2034 | 2036 | 2066 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-battery-2037 | battery | 1 | 1 | 4 | 2035 | 2037 | 2052 | 15 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-gas-2039 | gas | 2 | 0.92 | 0 | 2035 | 2039 | 2074 | 35 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-offshore-2039 | offshore | 2 | 1 | 0 | 2035 | 2039 | 2069 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-onshore-2037 | onshore | 23 | 0.1 | 0 | 2035 | 2037 | 2062 | 25 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-solar-2037 | solar | 18 | 0.1 | 0 | 2035 | 2037 | 2067 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-battery-2038 | battery | 1 | 1 | 4 | 2036 | 2038 | 2053 | 15 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-gas-2040 | gas | 2 | 0.92 | 0 | 2036 | 2040 | 2075 | 35 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | mixed-gas-2040 | gas | 2 | 0.92 | 0 | 2036 | 2040 | 2075 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_low.plan.json
government | low | adaptive-offshore-2040 | offshore | 3 | 1 | 0 | 2036 | 2040 | 2070 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-onshore-2038 | onshore | 23 | 0.1 | 0 | 2036 | 2038 | 2063 | 25 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-solar-2038 | solar | 18 | 0.1 | 0 | 2036 | 2038 | 2068 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-battery-2039 | battery | 1 | 1 | 4 | 2037 | 2039 | 2054 | 15 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-gas-2041 | gas | 1 | 0.92 | 0 | 2037 | 2041 | 2076 | 35 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-offshore-2041 | offshore | 4 | 1 | 0 | 2037 | 2041 | 2071 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-onshore-2039 | onshore | 17 | 0.1 | 0 | 2037 | 2039 | 2064 | 25 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-solar-2039 | solar | 18 | 0.1 | 0 | 2037 | 2039 | 2069 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-battery-2040 | battery | 2 | 1 | 4 | 2038 | 2040 | 2055 | 15 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-gas-2042 | gas | 1 | 0.92 | 0 | 2038 | 2042 | 2077 | 35 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | mixed-gas-2042 | gas | 2 | 0.92 | 0 | 2038 | 2042 | 2077 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_low.plan.json
government | low | mixed-gas_engine-2040 | gas_engine | 11 | 0.1 | 0 | 2038 | 2040 | 2070 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_low.plan.json
government | low | adaptive-offshore-2042 | offshore | 3 | 1 | 0 | 2038 | 2042 | 2072 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-onshore-2040 | onshore | 18 | 0.1 | 0 | 2038 | 2040 | 2065 | 25 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-solar-2040 | solar | 22 | 0.1 | 0 | 2038 | 2040 | 2070 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-battery-2041 | battery | 1 | 1 | 4 | 2039 | 2041 | 2056 | 15 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | mixed-gas_engine-2041 | gas_engine | 25 | 0.1 | 0 | 2039 | 2041 | 2071 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_low.plan.json
government | low | adaptive-offshore-2043 | offshore | 4 | 1 | 0 | 2039 | 2043 | 2073 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-onshore-2041 | onshore | 26 | 0.1 | 0 | 2039 | 2041 | 2066 | 25 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-solar-2041 | solar | 26 | 0.1 | 0 | 2039 | 2041 | 2071 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-battery-2042 | battery | 2 | 1 | 4 | 2040 | 2042 | 2057 | 15 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-gas-2044 | gas | 1 | 0.92 | 0 | 2040 | 2044 | 2079 | 35 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | mixed-gas-2044 | gas | 2 | 0.92 | 0 | 2040 | 2044 | 2079 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_low.plan.json
government | low | mixed-gas_engine-2042 | gas_engine | 7 | 0.1 | 0 | 2040 | 2042 | 2072 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_low.plan.json
government | low | adaptive-offshore-2044 | offshore | 2 | 1 | 0 | 2040 | 2044 | 2074 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-onshore-2042 | onshore | 30 | 0.1 | 0 | 2040 | 2042 | 2067 | 25 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-solar-2042 | solar | 22 | 0.1 | 0 | 2040 | 2042 | 2072 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-battery-2043 | battery | 10 | 1 | 4 | 2041 | 2043 | 2058 | 15 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | mixed-gas_engine-2043 | gas_engine | 10 | 0.1 | 0 | 2041 | 2043 | 2073 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_low.plan.json
government | low | adaptive-offshore-2045 | offshore | 4 | 1 | 0 | 2041 | 2045 | 2075 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-onshore-2043 | onshore | 18 | 0.1 | 0 | 2041 | 2043 | 2068 | 25 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-solar-2043 | solar | 19 | 0.1 | 0 | 2041 | 2043 | 2073 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-battery-2044 | battery | 1 | 1 | 4 | 2042 | 2044 | 2059 | 15 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | mixed-gas-2046 | gas | 2 | 0.92 | 0 | 2042 | 2046 | 2081 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_low.plan.json
government | low | mixed-gas_engine-2044 | gas_engine | 11 | 0.1 | 0 | 2042 | 2044 | 2074 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_low.plan.json
government | low | adaptive-offshore-2046 | offshore | 2 | 1 | 0 | 2042 | 2046 | 2076 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-onshore-2044 | onshore | 15 | 0.1 | 0 | 2042 | 2044 | 2069 | 25 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-solar-2044 | solar | 20 | 0.1 | 0 | 2042 | 2044 | 2074 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-battery-2045 | battery | 12 | 1 | 4 | 2043 | 2045 | 2060 | 15 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | mixed-gas_engine-2045 | gas_engine | 8 | 0.1 | 0 | 2043 | 2045 | 2075 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_low.plan.json
government | low | adaptive-offshore-2047 | offshore | 4 | 1 | 0 | 2043 | 2047 | 2077 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-onshore-2045 | onshore | 13 | 0.1 | 0 | 2043 | 2045 | 2070 | 25 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-solar-2045 | solar | 21 | 0.1 | 0 | 2043 | 2045 | 2075 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | mixed-gas-2048 | gas | 2 | 0.92 | 0 | 2044 | 2048 | 2083 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_low.plan.json
government | low | mixed-gas_engine-2046 | gas_engine | 2 | 0.1 | 0 | 2044 | 2046 | 2076 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_low.plan.json
government | low | adaptive-offshore-2048 | offshore | 3 | 1 | 0 | 2044 | 2048 | 2078 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-onshore-2046 | onshore | 12 | 0.1 | 0 | 2044 | 2046 | 2071 | 25 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-solar-2046 | solar | 20 | 0.1 | 0 | 2044 | 2046 | 2076 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-battery-2047 | battery | 1 | 1 | 4 | 2045 | 2047 | 2062 | 15 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-gas-2049 | gas | 1 | 0.92 | 0 | 2045 | 2049 | 2084 | 35 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | mixed-gas_engine-2047 | gas_engine | 16 | 0.1 | 0 | 2045 | 2047 | 2077 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_low.plan.json
government | low | adaptive-offshore-2049 | offshore | 4 | 1 | 0 | 2045 | 2049 | 2079 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-onshore-2047 | onshore | 10 | 0.1 | 0 | 2045 | 2047 | 2072 | 25 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-solar-2047 | solar | 18 | 0.1 | 0 | 2045 | 2047 | 2077 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-battery-2048 | battery | 1 | 1 | 4 | 2046 | 2048 | 2063 | 15 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-gas-2050 | gas | 4 | 0.92 | 0 | 2046 | 2050 | 2085 | 35 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-offshore-2050 | offshore | 2 | 1 | 0 | 2046 | 2050 | 2080 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-onshore-2048 | onshore | 15 | 0.1 | 0 | 2046 | 2048 | 2073 | 25 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-solar-2048 | solar | 22 | 0.1 | 0 | 2046 | 2048 | 2078 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | mixed-gas_engine-2049 | gas_engine | 12 | 0.1 | 0 | 2047 | 2049 | 2079 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_low.plan.json
government | low | adaptive-onshore-2049 | onshore | 15 | 0.1 | 0 | 2047 | 2049 | 2074 | 25 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-solar-2049 | solar | 35 | 0.1 | 0 | 2047 | 2049 | 2079 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-battery-2050 | battery | 1 | 1 | 4 | 2048 | 2050 | 2065 | 15 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | mixed-gas_engine-2050 | gas_engine | 12 | 0.1 | 0 | 2048 | 2050 | 2080 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_low.plan.json
government | low | adaptive-onshore-2050 | onshore | 12 | 0.1 | 0 | 2048 | 2050 | 2075 | 25 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | low | adaptive-solar-2050 | solar | 45 | 0.1 | 0 | 2048 | 2050 | 2080 | 30 |  |  | Retained dated assumption | demand_plans/government_low.plan.json
government | central | offshore-2030-0 | offshore | 13 | 1 | 0 | 2026 | 2030 | 2060 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | offshore-2031-8 | offshore | 7 | 1 | 0 | 2027 | 2031 | 2061 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | battery-2030-3 | battery | 1 | 1 | 4 | 2028 | 2030 | 2045 | 15 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | offshore-2032-12 | offshore | 7 | 1 | 0 | 2028 | 2032 | 2062 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | onshore-2030-1 | onshore | 54 | 0.1 | 0 | 2028 | 2030 | 2055 | 25 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | solar-2030-2 | solar | 117 | 0.1 | 0 | 2028 | 2030 | 2060 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | gas-2033-21 | gas | 1 | 0.92 | 0 | 2029 | 2033 | 2068 | 35 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | mixed-gas-2033 | gas | 3 | 0.92 | 0 | 2029 | 2033 | 2068 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | mixed-gas_engine-2031 | gas_engine | 40 | 0.1 | 0 | 2029 | 2031 | 2061 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | offshore-2033-17 | offshore | 7 | 1 | 0 | 2029 | 2033 | 2063 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | onshore-2031-9 | onshore | 33 | 0.1 | 0 | 2029 | 2031 | 2056 | 25 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | solar-2031-10 | solar | 22 | 0.1 | 0 | 2029 | 2031 | 2061 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | battery-2032-15 | battery | 1 | 1 | 4 | 2030 | 2032 | 2047 | 15 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | mixed-gas-2034 | gas | 4 | 0.92 | 0 | 2030 | 2034 | 2069 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | mixed-gas_engine-2032 | gas_engine | 40 | 0.1 | 0 | 2030 | 2032 | 2062 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | nuclear-2035-5 | nuclear | 1 | 0.47 | 0 | 2030 | 2035 | 2095 | 60 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | nuclear-2036-6 | nuclear | 1 | 0.47 | 0 | 2030 | 2035 | 2095 | 60 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | nuclear-2037-7 | nuclear | 1 | 0.47 | 0 | 2030 | 2035 | 2095 | 60 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | offshore-2034-22 | offshore | 7 | 1 | 0 | 2030 | 2034 | 2064 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | onshore-2032-13 | onshore | 21 | 0.1 | 0 | 2030 | 2032 | 2057 | 25 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | solar-2032-14 | solar | 22 | 0.1 | 0 | 2030 | 2032 | 2062 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | battery-2033-20 | battery | 1 | 1 | 4 | 2031 | 2033 | 2048 | 15 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | gas-2035-29 | gas | 2 | 0.92 | 0 | 2031 | 2035 | 2070 | 35 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | mixed-gas-2035 | gas | 2 | 0.92 | 0 | 2031 | 2035 | 2070 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | mixed-gas_engine-2033 | gas_engine | 36 | 0.1 | 0 | 2031 | 2033 | 2063 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | offshore-2035-25 | offshore | 7 | 1 | 0 | 2031 | 2035 | 2065 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | onshore-2033-18 | onshore | 22 | 0.1 | 0 | 2031 | 2033 | 2058 | 25 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | solar-2033-19 | solar | 22 | 0.1 | 0 | 2031 | 2033 | 2063 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | gas-2036-34 | gas | 2 | 0.92 | 0 | 2032 | 2036 | 2071 | 35 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | mixed-gas-2036 | gas | 2 | 0.92 | 0 | 2032 | 2036 | 2071 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | mixed-gas_engine-2034 | gas_engine | 36 | 0.1 | 0 | 2032 | 2034 | 2064 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | offshore-2036-30 | offshore | 5 | 1 | 0 | 2032 | 2036 | 2066 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | onshore-2034-23 | onshore | 19 | 0.1 | 0 | 2032 | 2034 | 2059 | 25 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | solar-2034-24 | solar | 22 | 0.1 | 0 | 2032 | 2034 | 2064 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | battery-2035-28 | battery | 1 | 1 | 4 | 2033 | 2035 | 2050 | 15 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | gas-2037-39 | gas | 2 | 0.92 | 0 | 2033 | 2037 | 2072 | 35 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | mixed-gas-2037 | gas | 2 | 0.92 | 0 | 2033 | 2037 | 2072 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | mixed-gas_engine-2035 | gas_engine | 7 | 0.1 | 0 | 2033 | 2035 | 2065 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | offshore-2037-35 | offshore | 5 | 1 | 0 | 2033 | 2037 | 2067 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | onshore-2035-26 | onshore | 21 | 0.1 | 0 | 2033 | 2035 | 2060 | 25 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | solar-2035-27 | solar | 22 | 0.1 | 0 | 2033 | 2035 | 2065 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | battery-2036-33 | battery | 2 | 1 | 4 | 2034 | 2036 | 2051 | 15 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | gas-2038-44 | gas | 3 | 0.92 | 0 | 2034 | 2038 | 2073 | 35 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | mixed-gas-2038 | gas | 1 | 0.92 | 0 | 2034 | 2038 | 2073 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | mixed-gas_engine-2036 | gas_engine | 25 | 0.1 | 0 | 2034 | 2036 | 2066 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | offshore-2038-40 | offshore | 5 | 1 | 0 | 2034 | 2038 | 2068 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | onshore-2036-31 | onshore | 28 | 0.1 | 0 | 2034 | 2036 | 2061 | 25 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | solar-2036-32 | solar | 43 | 0.1 | 0 | 2034 | 2036 | 2066 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | battery-2037-38 | battery | 2 | 1 | 4 | 2035 | 2037 | 2052 | 15 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | gas-2030-4 | gas | 1 | 0.92 | 0 | 2035 | 2039 | 2074 | 35 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | gas-2039-49 | gas | 2 | 0.92 | 0 | 2035 | 2039 | 2074 | 35 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | mixed-gas-2039 | gas | 1 | 0.92 | 0 | 2035 | 2039 | 2074 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | mixed-gas_engine-2037 | gas_engine | 21 | 0.1 | 0 | 2035 | 2037 | 2067 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | offshore-2039-45 | offshore | 4 | 1 | 0 | 2035 | 2039 | 2069 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | onshore-2037-36 | onshore | 35 | 0.1 | 0 | 2035 | 2037 | 2062 | 25 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | solar-2037-37 | solar | 42 | 0.1 | 0 | 2035 | 2037 | 2067 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | battery-2038-43 | battery | 2 | 1 | 4 | 2036 | 2038 | 2053 | 15 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | gas-2040-54 | gas | 2 | 0.92 | 0 | 2036 | 2040 | 2075 | 35 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | mixed-gas-2040 | gas | 2 | 0.92 | 0 | 2036 | 2040 | 2075 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | mixed-gas_engine-2038 | gas_engine | 9 | 0.1 | 0 | 2036 | 2038 | 2068 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | offshore-2040-50 | offshore | 6 | 1 | 0 | 2036 | 2040 | 2070 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | onshore-2038-41 | onshore | 35 | 0.1 | 0 | 2036 | 2038 | 2063 | 25 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | solar-2038-42 | solar | 39 | 0.1 | 0 | 2036 | 2038 | 2068 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | battery-2039-48 | battery | 2 | 1 | 4 | 2037 | 2039 | 2054 | 15 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | gas-2031-11 | gas | 1 | 0.92 | 0 | 2037 | 2041 | 2076 | 35 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | gas-2032-16 | gas | 1 | 0.92 | 0 | 2037 | 2041 | 2076 | 35 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | gas-2041-59 | gas | 1 | 0.92 | 0 | 2037 | 2041 | 2076 | 35 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | mixed-gas-2041 | gas | 1 | 0.92 | 0 | 2037 | 2041 | 2076 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | offshore-2041-55 | offshore | 4 | 1 | 0 | 2037 | 2041 | 2071 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | onshore-2039-46 | onshore | 26 | 0.1 | 0 | 2037 | 2039 | 2064 | 25 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | solar-2039-47 | solar | 34 | 0.1 | 0 | 2037 | 2039 | 2069 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | battery-2040-53 | battery | 3 | 1 | 4 | 2038 | 2040 | 2055 | 15 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | gas-2042-64 | gas | 1 | 0.92 | 0 | 2038 | 2042 | 2077 | 35 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | mixed-gas-2042 | gas | 3 | 0.92 | 0 | 2038 | 2042 | 2077 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | mixed-gas_engine-2040 | gas_engine | 28 | 0.1 | 0 | 2038 | 2040 | 2070 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | offshore-2042-60 | offshore | 4 | 1 | 0 | 2038 | 2042 | 2072 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | onshore-2040-51 | onshore | 29 | 0.1 | 0 | 2038 | 2040 | 2065 | 25 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | solar-2040-52 | solar | 43 | 0.1 | 0 | 2038 | 2040 | 2070 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | battery-2041-58 | battery | 1 | 1 | 4 | 2039 | 2041 | 2056 | 15 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | mixed-gas-2043 | gas | 3 | 0.92 | 0 | 2039 | 2043 | 2078 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | offshore-2043-65 | offshore | 5 | 1 | 0 | 2039 | 2043 | 2073 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | onshore-2041-56 | onshore | 28 | 0.1 | 0 | 2039 | 2041 | 2066 | 25 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | solar-2041-57 | solar | 29 | 0.1 | 0 | 2039 | 2041 | 2071 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | battery-2042-63 | battery | 2 | 1 | 4 | 2040 | 2042 | 2057 | 15 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | gas-2044-73 | gas | 1 | 0.92 | 0 | 2040 | 2044 | 2079 | 35 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | mixed-gas-2044 | gas | 2 | 0.92 | 0 | 2040 | 2044 | 2079 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | offshore-2044-69 | offshore | 3 | 1 | 0 | 2040 | 2044 | 2074 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | onshore-2042-61 | onshore | 34 | 0.1 | 0 | 2040 | 2042 | 2067 | 25 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | solar-2042-62 | solar | 30 | 0.1 | 0 | 2040 | 2042 | 2072 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | battery-2043-68 | battery | 10 | 1 | 4 | 2041 | 2043 | 2058 | 15 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | offshore-2045-74 | offshore | 4 | 1 | 0 | 2041 | 2045 | 2075 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | onshore-2043-66 | onshore | 23 | 0.1 | 0 | 2041 | 2043 | 2068 | 25 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | solar-2043-67 | solar | 28 | 0.1 | 0 | 2041 | 2043 | 2073 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | battery-2044-72 | battery | 1 | 1 | 4 | 2042 | 2044 | 2059 | 15 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | mixed-gas-2046 | gas | 2 | 0.92 | 0 | 2042 | 2046 | 2081 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | offshore-2046-78 | offshore | 3 | 1 | 0 | 2042 | 2046 | 2076 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | onshore-2044-70 | onshore | 16 | 0.1 | 0 | 2042 | 2044 | 2069 | 25 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | solar-2044-71 | solar | 22 | 0.1 | 0 | 2042 | 2044 | 2074 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | battery-2045-77 | battery | 13 | 1 | 4 | 2043 | 2045 | 2060 | 15 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | mixed-gas_engine-2045 | gas_engine | 3 | 0.1 | 0 | 2043 | 2045 | 2075 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | offshore-2047-81 | offshore | 4 | 1 | 0 | 2043 | 2047 | 2077 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | onshore-2045-75 | onshore | 17 | 0.1 | 0 | 2043 | 2045 | 2070 | 25 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | solar-2045-76 | solar | 29 | 0.1 | 0 | 2043 | 2045 | 2075 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | mixed-gas-2048 | gas | 2 | 0.92 | 0 | 2044 | 2048 | 2083 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | mixed-gas_engine-2046 | gas_engine | 4 | 0.1 | 0 | 2044 | 2046 | 2076 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | offshore-2048-85 | offshore | 3 | 1 | 0 | 2044 | 2048 | 2078 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | onshore-2046-79 | onshore | 16 | 0.1 | 0 | 2044 | 2046 | 2071 | 25 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | solar-2046-80 | solar | 26 | 0.1 | 0 | 2044 | 2046 | 2076 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | battery-2047-84 | battery | 2 | 1 | 4 | 2045 | 2047 | 2062 | 15 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | gas-2049-92 | gas | 1 | 0.92 | 0 | 2045 | 2049 | 2084 | 35 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | mixed-gas_engine-2047 | gas_engine | 15 | 0.1 | 0 | 2045 | 2047 | 2077 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | offshore-2049-89 | offshore | 4 | 1 | 0 | 2045 | 2049 | 2079 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | onshore-2047-82 | onshore | 10 | 0.1 | 0 | 2045 | 2047 | 2072 | 25 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | solar-2047-83 | solar | 18 | 0.1 | 0 | 2045 | 2047 | 2077 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | battery-2048-88 | battery | 2 | 1 | 4 | 2046 | 2048 | 2063 | 15 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | gas-2050-97 | gas | 4 | 0.92 | 0 | 2046 | 2050 | 2085 | 35 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | offshore-2050-93 | offshore | 1 | 1 | 0 | 2046 | 2050 | 2080 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | onshore-2048-86 | onshore | 14 | 0.1 | 0 | 2046 | 2048 | 2073 | 25 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | solar-2048-87 | solar | 21 | 0.1 | 0 | 2046 | 2048 | 2078 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | mixed-gas_engine-2049 | gas_engine | 9 | 0.1 | 0 | 2047 | 2049 | 2079 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | onshore-2049-90 | onshore | 14 | 0.1 | 0 | 2047 | 2049 | 2074 | 25 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | solar-2049-91 | solar | 33 | 0.1 | 0 | 2047 | 2049 | 2079 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | battery-2050-96 | battery | 2 | 1 | 4 | 2048 | 2050 | 2065 | 15 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | mixed-gas_engine-2050 | gas_engine | 9 | 0.1 | 0 | 2048 | 2050 | 2080 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_central.plan.json
government | central | onshore-2050-94 | onshore | 7 | 0.1 | 0 | 2048 | 2050 | 2075 | 25 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | central | solar-2050-95 | solar | 36 | 0.1 | 0 | 2048 | 2050 | 2080 | 30 |  |  | Retained dated assumption | demand_plans/government_central.plan.json
government | high | offshore-2030-0 | offshore | 13 | 1 | 0 | 2026 | 2030 | 2060 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | offshore-2031-8 | offshore | 7 | 1 | 0 | 2027 | 2031 | 2061 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | battery-2030-3 | battery | 1 | 1 | 4 | 2028 | 2030 | 2045 | 15 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | offshore-2032-12 | offshore | 7 | 1 | 0 | 2028 | 2032 | 2062 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | onshore-2030-1 | onshore | 54 | 0.1 | 0 | 2028 | 2030 | 2055 | 25 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | solar-2030-2 | solar | 117 | 0.1 | 0 | 2028 | 2030 | 2060 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-battery-2031 | battery | 1 | 1 | 4 | 2029 | 2031 | 2046 | 15 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-gas-2033 | gas | 3 | 0.92 | 0 | 2029 | 2033 | 2068 | 35 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | mixed-gas-2033 | gas | 1 | 0.92 | 0 | 2029 | 2033 | 2068 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | mixed-gas_engine-2031 | gas_engine | 40 | 0.1 | 0 | 2029 | 2031 | 2061 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | adaptive-offshore-2033 | offshore | 9 | 1 | 0 | 2029 | 2033 | 2063 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-onshore-2031 | onshore | 39 | 0.1 | 0 | 2029 | 2031 | 2056 | 25 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-solar-2031 | solar | 34 | 0.1 | 0 | 2029 | 2031 | 2061 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-battery-2032 | battery | 1 | 1 | 4 | 2030 | 2032 | 2047 | 15 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | mixed-gas-2034 | gas | 4 | 0.92 | 0 | 2030 | 2034 | 2069 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | mixed-gas_engine-2032 | gas_engine | 40 | 0.1 | 0 | 2030 | 2032 | 2062 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | nuclear-2035-5 | nuclear | 1 | 0.47 | 0 | 2030 | 2035 | 2095 | 60 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | nuclear-2036-6 | nuclear | 1 | 0.47 | 0 | 2030 | 2035 | 2095 | 60 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | nuclear-2037-7 | nuclear | 1 | 0.47 | 0 | 2030 | 2035 | 2095 | 60 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-offshore-2034 | offshore | 8 | 1 | 0 | 2030 | 2034 | 2064 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-onshore-2032 | onshore | 23 | 0.1 | 0 | 2030 | 2032 | 2057 | 25 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-solar-2032 | solar | 24 | 0.1 | 0 | 2030 | 2032 | 2062 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-battery-2033 | battery | 1 | 1 | 4 | 2031 | 2033 | 2048 | 15 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-gas-2035 | gas | 2 | 0.92 | 0 | 2031 | 2035 | 2070 | 35 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | mixed-gas-2035 | gas | 2 | 0.92 | 0 | 2031 | 2035 | 2070 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | mixed-gas_engine-2033 | gas_engine | 36 | 0.1 | 0 | 2031 | 2033 | 2063 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | adaptive-offshore-2035 | offshore | 8 | 1 | 0 | 2031 | 2035 | 2065 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-onshore-2033 | onshore | 23 | 0.1 | 0 | 2031 | 2033 | 2058 | 25 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-solar-2033 | solar | 25 | 0.1 | 0 | 2031 | 2033 | 2063 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-gas-2036 | gas | 2 | 0.92 | 0 | 2032 | 2036 | 2071 | 35 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | mixed-gas-2036 | gas | 2 | 0.92 | 0 | 2032 | 2036 | 2071 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | mixed-gas_engine-2034 | gas_engine | 36 | 0.1 | 0 | 2032 | 2034 | 2064 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | adaptive-offshore-2036 | offshore | 6 | 1 | 0 | 2032 | 2036 | 2066 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-onshore-2034 | onshore | 22 | 0.1 | 0 | 2032 | 2034 | 2059 | 25 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-solar-2034 | solar | 27 | 0.1 | 0 | 2032 | 2034 | 2064 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-battery-2035 | battery | 2 | 1 | 4 | 2033 | 2035 | 2050 | 15 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-gas-2037 | gas | 3 | 0.92 | 0 | 2033 | 2037 | 2072 | 35 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | mixed-gas-2037 | gas | 1 | 0.92 | 0 | 2033 | 2037 | 2072 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | mixed-gas_engine-2035 | gas_engine | 36 | 0.1 | 0 | 2033 | 2035 | 2065 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | adaptive-offshore-2037 | offshore | 7 | 1 | 0 | 2033 | 2037 | 2067 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-onshore-2035 | onshore | 23 | 0.1 | 0 | 2033 | 2035 | 2060 | 25 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-solar-2035 | solar | 26 | 0.1 | 0 | 2033 | 2035 | 2065 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-battery-2036 | battery | 2 | 1 | 4 | 2034 | 2036 | 2051 | 15 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-gas-2038 | gas | 4 | 0.92 | 0 | 2034 | 2038 | 2073 | 35 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | mixed-gas_engine-2036 | gas_engine | 36 | 0.1 | 0 | 2034 | 2036 | 2066 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | adaptive-offshore-2038 | offshore | 7 | 1 | 0 | 2034 | 2038 | 2068 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-onshore-2036 | onshore | 33 | 0.1 | 0 | 2034 | 2036 | 2061 | 25 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-solar-2036 | solar | 51 | 0.1 | 0 | 2034 | 2036 | 2066 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-battery-2037 | battery | 3 | 1 | 4 | 2035 | 2037 | 2052 | 15 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-gas-2039 | gas | 2 | 0.92 | 0 | 2035 | 2039 | 2074 | 35 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | mixed-gas-2039 | gas | 2 | 0.92 | 0 | 2035 | 2039 | 2074 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | mixed-gas_engine-2037 | gas_engine | 36 | 0.1 | 0 | 2035 | 2037 | 2067 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | adaptive-offshore-2039 | offshore | 5 | 1 | 0 | 2035 | 2039 | 2069 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-onshore-2037 | onshore | 48 | 0.1 | 0 | 2035 | 2037 | 2062 | 25 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-solar-2037 | solar | 66 | 0.1 | 0 | 2035 | 2037 | 2067 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-battery-2038 | battery | 2 | 1 | 4 | 2036 | 2038 | 2053 | 15 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-gas-2040 | gas | 2 | 0.92 | 0 | 2036 | 2040 | 2075 | 35 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | mixed-gas-2040 | gas | 2 | 0.92 | 0 | 2036 | 2040 | 2075 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | mixed-gas_engine-2038 | gas_engine | 36 | 0.1 | 0 | 2036 | 2038 | 2068 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | adaptive-offshore-2040 | offshore | 6 | 1 | 0 | 2036 | 2040 | 2070 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-onshore-2038 | onshore | 41 | 0.1 | 0 | 2036 | 2038 | 2063 | 25 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-solar-2038 | solar | 50 | 0.1 | 0 | 2036 | 2038 | 2068 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-battery-2039 | battery | 3 | 1 | 4 | 2037 | 2039 | 2054 | 15 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-gas-2041 | gas | 2 | 0.92 | 0 | 2037 | 2041 | 2076 | 35 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | mixed-gas-2041 | gas | 2 | 0.92 | 0 | 2037 | 2041 | 2076 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | mixed-gas_engine-2039 | gas_engine | 24 | 0.1 | 0 | 2037 | 2039 | 2069 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | adaptive-offshore-2041 | offshore | 6 | 1 | 0 | 2037 | 2041 | 2071 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-onshore-2039 | onshore | 30 | 0.1 | 0 | 2037 | 2039 | 2064 | 25 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-solar-2039 | solar | 42 | 0.1 | 0 | 2037 | 2039 | 2069 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-battery-2040 | battery | 3 | 1 | 4 | 2038 | 2040 | 2055 | 15 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-gas-2042 | gas | 1 | 0.92 | 0 | 2038 | 2042 | 2077 | 35 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | mixed-gas-2042 | gas | 3 | 0.92 | 0 | 2038 | 2042 | 2077 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | mixed-gas_engine-2040 | gas_engine | 36 | 0.1 | 0 | 2038 | 2040 | 2070 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | adaptive-offshore-2042 | offshore | 5 | 1 | 0 | 2038 | 2042 | 2072 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-onshore-2040 | onshore | 32 | 0.1 | 0 | 2038 | 2040 | 2065 | 25 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-solar-2040 | solar | 48 | 0.1 | 0 | 2038 | 2040 | 2070 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-battery-2041 | battery | 1 | 1 | 4 | 2039 | 2041 | 2056 | 15 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | mixed-gas-2043 | gas | 4 | 0.92 | 0 | 2039 | 2043 | 2078 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | mixed-gas_engine-2041 | gas_engine | 12 | 0.1 | 0 | 2039 | 2041 | 2071 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | adaptive-offshore-2043 | offshore | 6 | 1 | 0 | 2039 | 2043 | 2073 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-onshore-2041 | onshore | 35 | 0.1 | 0 | 2039 | 2041 | 2066 | 25 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-solar-2041 | solar | 42 | 0.1 | 0 | 2039 | 2041 | 2071 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-battery-2042 | battery | 3 | 1 | 4 | 2040 | 2042 | 2057 | 15 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-gas-2044 | gas | 1 | 0.92 | 0 | 2040 | 2044 | 2079 | 35 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | gas-2030-4 | gas | 1 | 0.92 | 0 | 2040 | 2044 | 2079 | 35 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | mixed-gas-2044 | gas | 2 | 0.92 | 0 | 2040 | 2044 | 2079 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | mixed-gas_engine-2042 | gas_engine | 7 | 0.1 | 0 | 2040 | 2042 | 2072 | 30 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | adaptive-offshore-2044 | offshore | 3 | 1 | 0 | 2040 | 2044 | 2074 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-onshore-2042 | onshore | 41 | 0.1 | 0 | 2040 | 2042 | 2067 | 25 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-solar-2042 | solar | 43 | 0.1 | 0 | 2040 | 2042 | 2072 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-battery-2043 | battery | 10 | 1 | 4 | 2041 | 2043 | 2058 | 15 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | gas-2031-11 | gas | 1 | 0.92 | 0 | 2041 | 2045 | 2080 | 35 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | gas-2032-16 | gas | 1 | 0.92 | 0 | 2041 | 2045 | 2080 | 35 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | mixed-gas-2045 | gas | 2 | 0.92 | 0 | 2041 | 2045 | 2080 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | adaptive-offshore-2045 | offshore | 4 | 1 | 0 | 2041 | 2045 | 2075 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-onshore-2043 | onshore | 26 | 0.1 | 0 | 2041 | 2043 | 2068 | 25 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-solar-2043 | solar | 33 | 0.1 | 0 | 2041 | 2043 | 2073 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-battery-2044 | battery | 1 | 1 | 4 | 2042 | 2044 | 2059 | 15 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | mixed-gas-2046 | gas | 4 | 0.92 | 0 | 2042 | 2046 | 2081 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | adaptive-offshore-2046 | offshore | 2 | 1 | 0 | 2042 | 2046 | 2076 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-onshore-2044 | onshore | 16 | 0.1 | 0 | 2042 | 2044 | 2069 | 25 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-solar-2044 | solar | 23 | 0.1 | 0 | 2042 | 2044 | 2074 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-battery-2045 | battery | 13 | 1 | 4 | 2043 | 2045 | 2060 | 15 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | mixed-gas-2047 | gas | 4 | 0.92 | 0 | 2043 | 2047 | 2082 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | adaptive-offshore-2047 | offshore | 5 | 1 | 0 | 2043 | 2047 | 2077 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-onshore-2045 | onshore | 14 | 0.1 | 0 | 2043 | 2045 | 2070 | 25 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-solar-2045 | solar | 23 | 0.1 | 0 | 2043 | 2045 | 2075 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-battery-2046 | battery | 1 | 1 | 4 | 2044 | 2046 | 2061 | 15 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | mixed-gas-2048 | gas | 1 | 0.92 | 0 | 2044 | 2048 | 2083 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | adaptive-offshore-2048 | offshore | 4 | 1 | 0 | 2044 | 2048 | 2078 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-onshore-2046 | onshore | 14 | 0.1 | 0 | 2044 | 2046 | 2071 | 25 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-solar-2046 | solar | 22 | 0.1 | 0 | 2044 | 2046 | 2076 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-battery-2047 | battery | 2 | 1 | 4 | 2045 | 2047 | 2062 | 15 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-gas-2049 | gas | 1 | 0.92 | 0 | 2045 | 2049 | 2084 | 35 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | mixed-gas-2049 | gas | 1 | 0.92 | 0 | 2045 | 2049 | 2084 | 35 |  |  | M48 mixed-gas candidate | demand_plans/government_high.plan.json
government | high | adaptive-offshore-2049 | offshore | 4 | 1 | 0 | 2045 | 2049 | 2079 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-onshore-2047 | onshore | 13 | 0.1 | 0 | 2045 | 2047 | 2072 | 25 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-solar-2047 | solar | 24 | 0.1 | 0 | 2045 | 2047 | 2077 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-battery-2048 | battery | 2 | 1 | 4 | 2046 | 2048 | 2063 | 15 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-gas-2050 | gas | 4 | 0.92 | 0 | 2046 | 2050 | 2085 | 35 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-offshore-2050 | offshore | 1 | 1 | 0 | 2046 | 2050 | 2080 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-onshore-2048 | onshore | 17 | 0.1 | 0 | 2046 | 2048 | 2073 | 25 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-solar-2048 | solar | 27 | 0.1 | 0 | 2046 | 2048 | 2078 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-onshore-2049 | onshore | 14 | 0.1 | 0 | 2047 | 2049 | 2074 | 25 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-solar-2049 | solar | 33 | 0.1 | 0 | 2047 | 2049 | 2079 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-battery-2050 | battery | 3 | 1 | 4 | 2048 | 2050 | 2065 | 15 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-onshore-2050 | onshore | 11 | 0.1 | 0 | 2048 | 2050 | 2075 | 25 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
government | high | adaptive-solar-2050 | solar | 43 | 0.1 | 0 | 2048 | 2050 | 2080 | 30 |  |  | Retained dated assumption | demand_plans/government_high.plan.json
target | low | offshore-2030-0 | offshore | 13 | 1 | 0 | 2026 | 2030 | 2060 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | offshore-2031-8 | offshore | 7 | 1 | 0 | 2027 | 2031 | 2061 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | battery-2030-3 | battery | 1 | 1 | 4 | 2028 | 2030 | 2045 | 15 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | offshore-2032-12 | offshore | 7 | 1 | 0 | 2028 | 2032 | 2062 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | onshore-2030-1 | onshore | 54 | 0.1 | 0 | 2028 | 2030 | 2055 | 25 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | solar-2030-2 | solar | 117 | 0.1 | 0 | 2028 | 2030 | 2060 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-onshore-2031 | onshore | 14 | 0.1 | 0 | 2029 | 2031 | 2056 | 25 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | nuclear-2035-5 | nuclear | 1 | 0.47 | 0 | 2030 | 2035 | 2095 | 60 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | nuclear-2036-6 | nuclear | 1 | 0.47 | 0 | 2030 | 2035 | 2095 | 60 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | nuclear-2037-7 | nuclear | 1 | 0.47 | 0 | 2030 | 2035 | 2095 | 60 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-offshore-2034 | offshore | 6 | 1 | 0 | 2030 | 2034 | 2064 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-onshore-2032 | onshore | 14 | 0.1 | 0 | 2030 | 2032 | 2057 | 25 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-offshore-2035 | offshore | 4 | 1 | 0 | 2031 | 2035 | 2065 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-onshore-2033 | onshore | 14 | 0.1 | 0 | 2031 | 2033 | 2058 | 25 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-solar-2033 | solar | 2 | 0.1 | 0 | 2031 | 2033 | 2063 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | gas-2030-4 | gas | 1 | 0.92 | 0 | 2032 | 2036 | 2071 | 35 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-offshore-2036 | offshore | 2 | 1 | 0 | 2032 | 2036 | 2066 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-onshore-2034 | onshore | 12 | 0.1 | 0 | 2032 | 2034 | 2059 | 25 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-solar-2034 | solar | 10 | 0.1 | 0 | 2032 | 2034 | 2064 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | gas-2031-11 | gas | 1 | 0.92 | 0 | 2033 | 2037 | 2072 | 35 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | gas-2032-16 | gas | 1 | 0.92 | 0 | 2033 | 2037 | 2072 | 35 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-offshore-2037 | offshore | 2 | 1 | 0 | 2033 | 2037 | 2067 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-onshore-2035 | onshore | 12 | 0.1 | 0 | 2033 | 2035 | 2060 | 25 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-solar-2035 | solar | 6 | 0.1 | 0 | 2033 | 2035 | 2065 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-battery-2036 | battery | 1 | 1 | 4 | 2034 | 2036 | 2051 | 15 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-gas-2038 | gas | 2 | 0.92 | 0 | 2034 | 2038 | 2073 | 35 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-offshore-2038 | offshore | 3 | 1 | 0 | 2034 | 2038 | 2068 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-onshore-2036 | onshore | 14 | 0.1 | 0 | 2034 | 2036 | 2061 | 25 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-solar-2036 | solar | 17 | 0.1 | 0 | 2034 | 2036 | 2066 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-battery-2037 | battery | 1 | 1 | 4 | 2035 | 2037 | 2052 | 15 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-gas-2039 | gas | 2 | 0.92 | 0 | 2035 | 2039 | 2074 | 35 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-offshore-2039 | offshore | 2 | 1 | 0 | 2035 | 2039 | 2069 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-onshore-2037 | onshore | 23 | 0.1 | 0 | 2035 | 2037 | 2062 | 25 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-solar-2037 | solar | 18 | 0.1 | 0 | 2035 | 2037 | 2067 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-battery-2038 | battery | 1 | 1 | 4 | 2036 | 2038 | 2053 | 15 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-gas-2040 | gas | 2 | 0.92 | 0 | 2036 | 2040 | 2075 | 35 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-offshore-2040 | offshore | 3 | 1 | 0 | 2036 | 2040 | 2070 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-onshore-2038 | onshore | 23 | 0.1 | 0 | 2036 | 2038 | 2063 | 25 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-solar-2038 | solar | 18 | 0.1 | 0 | 2036 | 2038 | 2068 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-battery-2039 | battery | 1 | 1 | 4 | 2037 | 2039 | 2054 | 15 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-gas-2041 | gas | 1 | 0.92 | 0 | 2037 | 2041 | 2076 | 35 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-offshore-2041 | offshore | 4 | 1 | 0 | 2037 | 2041 | 2071 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-onshore-2039 | onshore | 17 | 0.1 | 0 | 2037 | 2039 | 2064 | 25 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-solar-2039 | solar | 18 | 0.1 | 0 | 2037 | 2039 | 2069 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-battery-2040 | battery | 2 | 1 | 4 | 2038 | 2040 | 2055 | 15 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-gas-2042 | gas | 1 | 0.92 | 0 | 2038 | 2042 | 2077 | 35 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-offshore-2042 | offshore | 3 | 1 | 0 | 2038 | 2042 | 2072 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-onshore-2040 | onshore | 18 | 0.1 | 0 | 2038 | 2040 | 2065 | 25 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-solar-2040 | solar | 22 | 0.1 | 0 | 2038 | 2040 | 2070 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-battery-2041 | battery | 1 | 1 | 4 | 2039 | 2041 | 2056 | 15 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-offshore-2043 | offshore | 4 | 1 | 0 | 2039 | 2043 | 2073 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-onshore-2041 | onshore | 26 | 0.1 | 0 | 2039 | 2041 | 2066 | 25 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-solar-2041 | solar | 26 | 0.1 | 0 | 2039 | 2041 | 2071 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-battery-2042 | battery | 2 | 1 | 4 | 2040 | 2042 | 2057 | 15 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-gas-2044 | gas | 1 | 0.92 | 0 | 2040 | 2044 | 2079 | 35 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-offshore-2044 | offshore | 2 | 1 | 0 | 2040 | 2044 | 2074 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-onshore-2042 | onshore | 30 | 0.1 | 0 | 2040 | 2042 | 2067 | 25 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-solar-2042 | solar | 22 | 0.1 | 0 | 2040 | 2042 | 2072 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-battery-2043 | battery | 10 | 1 | 4 | 2041 | 2043 | 2058 | 15 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-offshore-2045 | offshore | 4 | 1 | 0 | 2041 | 2045 | 2075 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-onshore-2043 | onshore | 18 | 0.1 | 0 | 2041 | 2043 | 2068 | 25 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-solar-2043 | solar | 19 | 0.1 | 0 | 2041 | 2043 | 2073 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-battery-2044 | battery | 1 | 1 | 4 | 2042 | 2044 | 2059 | 15 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-offshore-2046 | offshore | 2 | 1 | 0 | 2042 | 2046 | 2076 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-onshore-2044 | onshore | 15 | 0.1 | 0 | 2042 | 2044 | 2069 | 25 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-solar-2044 | solar | 20 | 0.1 | 0 | 2042 | 2044 | 2074 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-battery-2045 | battery | 12 | 1 | 4 | 2043 | 2045 | 2060 | 15 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-offshore-2047 | offshore | 4 | 1 | 0 | 2043 | 2047 | 2077 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-onshore-2045 | onshore | 13 | 0.1 | 0 | 2043 | 2045 | 2070 | 25 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-solar-2045 | solar | 21 | 0.1 | 0 | 2043 | 2045 | 2075 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-offshore-2048 | offshore | 3 | 1 | 0 | 2044 | 2048 | 2078 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-onshore-2046 | onshore | 12 | 0.1 | 0 | 2044 | 2046 | 2071 | 25 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-solar-2046 | solar | 20 | 0.1 | 0 | 2044 | 2046 | 2076 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-battery-2047 | battery | 1 | 1 | 4 | 2045 | 2047 | 2062 | 15 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-gas-2049 | gas | 1 | 0.92 | 0 | 2045 | 2049 | 2084 | 35 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-offshore-2049 | offshore | 4 | 1 | 0 | 2045 | 2049 | 2079 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-onshore-2047 | onshore | 10 | 0.1 | 0 | 2045 | 2047 | 2072 | 25 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-solar-2047 | solar | 18 | 0.1 | 0 | 2045 | 2047 | 2077 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-battery-2048 | battery | 1 | 1 | 4 | 2046 | 2048 | 2063 | 15 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-gas-2050 | gas | 4 | 0.92 | 0 | 2046 | 2050 | 2085 | 35 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-offshore-2050 | offshore | 2 | 1 | 0 | 2046 | 2050 | 2080 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-onshore-2048 | onshore | 15 | 0.1 | 0 | 2046 | 2048 | 2073 | 25 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-solar-2048 | solar | 22 | 0.1 | 0 | 2046 | 2048 | 2078 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-onshore-2049 | onshore | 15 | 0.1 | 0 | 2047 | 2049 | 2074 | 25 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-solar-2049 | solar | 35 | 0.1 | 0 | 2047 | 2049 | 2079 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-battery-2050 | battery | 1 | 1 | 4 | 2048 | 2050 | 2065 | 15 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-onshore-2050 | onshore | 12 | 0.1 | 0 | 2048 | 2050 | 2075 | 25 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | low | adaptive-solar-2050 | solar | 45 | 0.1 | 0 | 2048 | 2050 | 2080 | 30 |  |  | Retained dated assumption | demand_plans/target_low.plan.json
target | central | offshore-2030-0 | offshore | 13 | 1 | 0 | 2026 | 2030 | 2060 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | offshore-2031-8 | offshore | 7 | 1 | 0 | 2027 | 2031 | 2061 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | battery-2030-3 | battery | 1 | 1 | 4 | 2028 | 2030 | 2045 | 15 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | offshore-2032-12 | offshore | 7 | 1 | 0 | 2028 | 2032 | 2062 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | onshore-2030-1 | onshore | 54 | 0.1 | 0 | 2028 | 2030 | 2055 | 25 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | solar-2030-2 | solar | 117 | 0.1 | 0 | 2028 | 2030 | 2060 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | gas-2033-21 | gas | 1 | 0.92 | 0 | 2029 | 2033 | 2068 | 35 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | offshore-2033-17 | offshore | 7 | 1 | 0 | 2029 | 2033 | 2063 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | onshore-2031-9 | onshore | 33 | 0.1 | 0 | 2029 | 2031 | 2056 | 25 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | solar-2031-10 | solar | 22 | 0.1 | 0 | 2029 | 2031 | 2061 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | battery-2032-15 | battery | 1 | 1 | 4 | 2030 | 2032 | 2047 | 15 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | nuclear-2035-5 | nuclear | 1 | 0.47 | 0 | 2030 | 2035 | 2095 | 60 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | nuclear-2036-6 | nuclear | 1 | 0.47 | 0 | 2030 | 2035 | 2095 | 60 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | nuclear-2037-7 | nuclear | 1 | 0.47 | 0 | 2030 | 2035 | 2095 | 60 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | offshore-2034-22 | offshore | 7 | 1 | 0 | 2030 | 2034 | 2064 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | onshore-2032-13 | onshore | 21 | 0.1 | 0 | 2030 | 2032 | 2057 | 25 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | solar-2032-14 | solar | 22 | 0.1 | 0 | 2030 | 2032 | 2062 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | battery-2033-20 | battery | 1 | 1 | 4 | 2031 | 2033 | 2048 | 15 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | gas-2035-29 | gas | 2 | 0.92 | 0 | 2031 | 2035 | 2070 | 35 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | offshore-2035-25 | offshore | 7 | 1 | 0 | 2031 | 2035 | 2065 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | onshore-2033-18 | onshore | 22 | 0.1 | 0 | 2031 | 2033 | 2058 | 25 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | solar-2033-19 | solar | 22 | 0.1 | 0 | 2031 | 2033 | 2063 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | gas-2036-34 | gas | 2 | 0.92 | 0 | 2032 | 2036 | 2071 | 35 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | offshore-2036-30 | offshore | 5 | 1 | 0 | 2032 | 2036 | 2066 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | onshore-2034-23 | onshore | 19 | 0.1 | 0 | 2032 | 2034 | 2059 | 25 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | solar-2034-24 | solar | 22 | 0.1 | 0 | 2032 | 2034 | 2064 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | battery-2035-28 | battery | 1 | 1 | 4 | 2033 | 2035 | 2050 | 15 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | gas-2037-39 | gas | 2 | 0.92 | 0 | 2033 | 2037 | 2072 | 35 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | offshore-2037-35 | offshore | 5 | 1 | 0 | 2033 | 2037 | 2067 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | onshore-2035-26 | onshore | 21 | 0.1 | 0 | 2033 | 2035 | 2060 | 25 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | solar-2035-27 | solar | 22 | 0.1 | 0 | 2033 | 2035 | 2065 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | battery-2036-33 | battery | 2 | 1 | 4 | 2034 | 2036 | 2051 | 15 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | gas-2038-44 | gas | 3 | 0.92 | 0 | 2034 | 2038 | 2073 | 35 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | offshore-2038-40 | offshore | 5 | 1 | 0 | 2034 | 2038 | 2068 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | onshore-2036-31 | onshore | 28 | 0.1 | 0 | 2034 | 2036 | 2061 | 25 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | solar-2036-32 | solar | 43 | 0.1 | 0 | 2034 | 2036 | 2066 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | battery-2037-38 | battery | 2 | 1 | 4 | 2035 | 2037 | 2052 | 15 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | gas-2030-4 | gas | 1 | 0.92 | 0 | 2035 | 2039 | 2074 | 35 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | gas-2039-49 | gas | 2 | 0.92 | 0 | 2035 | 2039 | 2074 | 35 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | offshore-2039-45 | offshore | 4 | 1 | 0 | 2035 | 2039 | 2069 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | onshore-2037-36 | onshore | 35 | 0.1 | 0 | 2035 | 2037 | 2062 | 25 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | solar-2037-37 | solar | 42 | 0.1 | 0 | 2035 | 2037 | 2067 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | battery-2038-43 | battery | 2 | 1 | 4 | 2036 | 2038 | 2053 | 15 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | gas-2040-54 | gas | 2 | 0.92 | 0 | 2036 | 2040 | 2075 | 35 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | offshore-2040-50 | offshore | 6 | 1 | 0 | 2036 | 2040 | 2070 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | onshore-2038-41 | onshore | 35 | 0.1 | 0 | 2036 | 2038 | 2063 | 25 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | solar-2038-42 | solar | 39 | 0.1 | 0 | 2036 | 2038 | 2068 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | battery-2039-48 | battery | 2 | 1 | 4 | 2037 | 2039 | 2054 | 15 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | gas-2031-11 | gas | 1 | 0.92 | 0 | 2037 | 2041 | 2076 | 35 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | gas-2032-16 | gas | 1 | 0.92 | 0 | 2037 | 2041 | 2076 | 35 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | gas-2041-59 | gas | 1 | 0.92 | 0 | 2037 | 2041 | 2076 | 35 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | offshore-2041-55 | offshore | 4 | 1 | 0 | 2037 | 2041 | 2071 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | onshore-2039-46 | onshore | 26 | 0.1 | 0 | 2037 | 2039 | 2064 | 25 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | solar-2039-47 | solar | 34 | 0.1 | 0 | 2037 | 2039 | 2069 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | battery-2040-53 | battery | 3 | 1 | 4 | 2038 | 2040 | 2055 | 15 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | gas-2042-64 | gas | 1 | 0.92 | 0 | 2038 | 2042 | 2077 | 35 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | offshore-2042-60 | offshore | 4 | 1 | 0 | 2038 | 2042 | 2072 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | onshore-2040-51 | onshore | 29 | 0.1 | 0 | 2038 | 2040 | 2065 | 25 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | solar-2040-52 | solar | 43 | 0.1 | 0 | 2038 | 2040 | 2070 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | battery-2041-58 | battery | 1 | 1 | 4 | 2039 | 2041 | 2056 | 15 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | offshore-2043-65 | offshore | 5 | 1 | 0 | 2039 | 2043 | 2073 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | onshore-2041-56 | onshore | 28 | 0.1 | 0 | 2039 | 2041 | 2066 | 25 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | solar-2041-57 | solar | 29 | 0.1 | 0 | 2039 | 2041 | 2071 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | battery-2042-63 | battery | 2 | 1 | 4 | 2040 | 2042 | 2057 | 15 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | gas-2044-73 | gas | 1 | 0.92 | 0 | 2040 | 2044 | 2079 | 35 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | offshore-2044-69 | offshore | 3 | 1 | 0 | 2040 | 2044 | 2074 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | onshore-2042-61 | onshore | 34 | 0.1 | 0 | 2040 | 2042 | 2067 | 25 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | solar-2042-62 | solar | 30 | 0.1 | 0 | 2040 | 2042 | 2072 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | battery-2043-68 | battery | 10 | 1 | 4 | 2041 | 2043 | 2058 | 15 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | offshore-2045-74 | offshore | 4 | 1 | 0 | 2041 | 2045 | 2075 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | onshore-2043-66 | onshore | 23 | 0.1 | 0 | 2041 | 2043 | 2068 | 25 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | solar-2043-67 | solar | 28 | 0.1 | 0 | 2041 | 2043 | 2073 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | battery-2044-72 | battery | 1 | 1 | 4 | 2042 | 2044 | 2059 | 15 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | offshore-2046-78 | offshore | 3 | 1 | 0 | 2042 | 2046 | 2076 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | onshore-2044-70 | onshore | 16 | 0.1 | 0 | 2042 | 2044 | 2069 | 25 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | solar-2044-71 | solar | 22 | 0.1 | 0 | 2042 | 2044 | 2074 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | battery-2045-77 | battery | 13 | 1 | 4 | 2043 | 2045 | 2060 | 15 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | offshore-2047-81 | offshore | 4 | 1 | 0 | 2043 | 2047 | 2077 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | onshore-2045-75 | onshore | 17 | 0.1 | 0 | 2043 | 2045 | 2070 | 25 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | solar-2045-76 | solar | 29 | 0.1 | 0 | 2043 | 2045 | 2075 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | offshore-2048-85 | offshore | 3 | 1 | 0 | 2044 | 2048 | 2078 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | onshore-2046-79 | onshore | 16 | 0.1 | 0 | 2044 | 2046 | 2071 | 25 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | solar-2046-80 | solar | 26 | 0.1 | 0 | 2044 | 2046 | 2076 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | battery-2047-84 | battery | 2 | 1 | 4 | 2045 | 2047 | 2062 | 15 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | gas-2049-92 | gas | 1 | 0.92 | 0 | 2045 | 2049 | 2084 | 35 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | offshore-2049-89 | offshore | 4 | 1 | 0 | 2045 | 2049 | 2079 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | onshore-2047-82 | onshore | 10 | 0.1 | 0 | 2045 | 2047 | 2072 | 25 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | solar-2047-83 | solar | 18 | 0.1 | 0 | 2045 | 2047 | 2077 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | battery-2048-88 | battery | 2 | 1 | 4 | 2046 | 2048 | 2063 | 15 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | gas-2050-97 | gas | 4 | 0.92 | 0 | 2046 | 2050 | 2085 | 35 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | offshore-2050-93 | offshore | 1 | 1 | 0 | 2046 | 2050 | 2080 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | onshore-2048-86 | onshore | 14 | 0.1 | 0 | 2046 | 2048 | 2073 | 25 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | solar-2048-87 | solar | 21 | 0.1 | 0 | 2046 | 2048 | 2078 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | onshore-2049-90 | onshore | 14 | 0.1 | 0 | 2047 | 2049 | 2074 | 25 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | solar-2049-91 | solar | 33 | 0.1 | 0 | 2047 | 2049 | 2079 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | battery-2050-96 | battery | 2 | 1 | 4 | 2048 | 2050 | 2065 | 15 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | onshore-2050-94 | onshore | 7 | 0.1 | 0 | 2048 | 2050 | 2075 | 25 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | central | solar-2050-95 | solar | 36 | 0.1 | 0 | 2048 | 2050 | 2080 | 30 |  |  | Retained dated assumption | demand_plans/target_central.plan.json
target | high | offshore-2030-0 | offshore | 13 | 1 | 0 | 2026 | 2030 | 2060 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | offshore-2031-8 | offshore | 7 | 1 | 0 | 2027 | 2031 | 2061 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | battery-2030-3 | battery | 1 | 1 | 4 | 2028 | 2030 | 2045 | 15 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | offshore-2032-12 | offshore | 7 | 1 | 0 | 2028 | 2032 | 2062 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | onshore-2030-1 | onshore | 54 | 0.1 | 0 | 2028 | 2030 | 2055 | 25 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | solar-2030-2 | solar | 117 | 0.1 | 0 | 2028 | 2030 | 2060 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-battery-2031 | battery | 1 | 1 | 4 | 2029 | 2031 | 2046 | 15 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-gas-2033 | gas | 3 | 0.92 | 0 | 2029 | 2033 | 2068 | 35 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-offshore-2033 | offshore | 9 | 1 | 0 | 2029 | 2033 | 2063 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-onshore-2031 | onshore | 39 | 0.1 | 0 | 2029 | 2031 | 2056 | 25 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-solar-2031 | solar | 34 | 0.1 | 0 | 2029 | 2031 | 2061 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-battery-2032 | battery | 1 | 1 | 4 | 2030 | 2032 | 2047 | 15 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | nuclear-2035-5 | nuclear | 1 | 0.47 | 0 | 2030 | 2035 | 2095 | 60 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | nuclear-2036-6 | nuclear | 1 | 0.47 | 0 | 2030 | 2035 | 2095 | 60 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | nuclear-2037-7 | nuclear | 1 | 0.47 | 0 | 2030 | 2035 | 2095 | 60 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-offshore-2034 | offshore | 8 | 1 | 0 | 2030 | 2034 | 2064 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-onshore-2032 | onshore | 23 | 0.1 | 0 | 2030 | 2032 | 2057 | 25 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-solar-2032 | solar | 24 | 0.1 | 0 | 2030 | 2032 | 2062 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-battery-2033 | battery | 1 | 1 | 4 | 2031 | 2033 | 2048 | 15 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-gas-2035 | gas | 2 | 0.92 | 0 | 2031 | 2035 | 2070 | 35 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-offshore-2035 | offshore | 8 | 1 | 0 | 2031 | 2035 | 2065 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-onshore-2033 | onshore | 23 | 0.1 | 0 | 2031 | 2033 | 2058 | 25 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-solar-2033 | solar | 25 | 0.1 | 0 | 2031 | 2033 | 2063 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-gas-2036 | gas | 2 | 0.92 | 0 | 2032 | 2036 | 2071 | 35 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-offshore-2036 | offshore | 6 | 1 | 0 | 2032 | 2036 | 2066 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-onshore-2034 | onshore | 22 | 0.1 | 0 | 2032 | 2034 | 2059 | 25 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-solar-2034 | solar | 27 | 0.1 | 0 | 2032 | 2034 | 2064 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-battery-2035 | battery | 2 | 1 | 4 | 2033 | 2035 | 2050 | 15 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-gas-2037 | gas | 3 | 0.92 | 0 | 2033 | 2037 | 2072 | 35 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-offshore-2037 | offshore | 7 | 1 | 0 | 2033 | 2037 | 2067 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-onshore-2035 | onshore | 23 | 0.1 | 0 | 2033 | 2035 | 2060 | 25 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-solar-2035 | solar | 26 | 0.1 | 0 | 2033 | 2035 | 2065 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-battery-2036 | battery | 2 | 1 | 4 | 2034 | 2036 | 2051 | 15 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-gas-2038 | gas | 4 | 0.92 | 0 | 2034 | 2038 | 2073 | 35 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-offshore-2038 | offshore | 7 | 1 | 0 | 2034 | 2038 | 2068 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-onshore-2036 | onshore | 33 | 0.1 | 0 | 2034 | 2036 | 2061 | 25 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-solar-2036 | solar | 51 | 0.1 | 0 | 2034 | 2036 | 2066 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-battery-2037 | battery | 3 | 1 | 4 | 2035 | 2037 | 2052 | 15 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-gas-2039 | gas | 2 | 0.92 | 0 | 2035 | 2039 | 2074 | 35 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-offshore-2039 | offshore | 5 | 1 | 0 | 2035 | 2039 | 2069 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-onshore-2037 | onshore | 48 | 0.1 | 0 | 2035 | 2037 | 2062 | 25 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-solar-2037 | solar | 66 | 0.1 | 0 | 2035 | 2037 | 2067 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-battery-2038 | battery | 2 | 1 | 4 | 2036 | 2038 | 2053 | 15 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-gas-2040 | gas | 2 | 0.92 | 0 | 2036 | 2040 | 2075 | 35 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-offshore-2040 | offshore | 6 | 1 | 0 | 2036 | 2040 | 2070 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-onshore-2038 | onshore | 41 | 0.1 | 0 | 2036 | 2038 | 2063 | 25 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-solar-2038 | solar | 50 | 0.1 | 0 | 2036 | 2038 | 2068 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-battery-2039 | battery | 3 | 1 | 4 | 2037 | 2039 | 2054 | 15 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-gas-2041 | gas | 2 | 0.92 | 0 | 2037 | 2041 | 2076 | 35 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-offshore-2041 | offshore | 6 | 1 | 0 | 2037 | 2041 | 2071 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-onshore-2039 | onshore | 30 | 0.1 | 0 | 2037 | 2039 | 2064 | 25 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-solar-2039 | solar | 42 | 0.1 | 0 | 2037 | 2039 | 2069 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-battery-2040 | battery | 3 | 1 | 4 | 2038 | 2040 | 2055 | 15 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-gas-2042 | gas | 1 | 0.92 | 0 | 2038 | 2042 | 2077 | 35 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-offshore-2042 | offshore | 5 | 1 | 0 | 2038 | 2042 | 2072 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-onshore-2040 | onshore | 32 | 0.1 | 0 | 2038 | 2040 | 2065 | 25 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-solar-2040 | solar | 48 | 0.1 | 0 | 2038 | 2040 | 2070 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-battery-2041 | battery | 1 | 1 | 4 | 2039 | 2041 | 2056 | 15 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-offshore-2043 | offshore | 6 | 1 | 0 | 2039 | 2043 | 2073 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-onshore-2041 | onshore | 35 | 0.1 | 0 | 2039 | 2041 | 2066 | 25 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-solar-2041 | solar | 42 | 0.1 | 0 | 2039 | 2041 | 2071 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-battery-2042 | battery | 3 | 1 | 4 | 2040 | 2042 | 2057 | 15 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-gas-2044 | gas | 1 | 0.92 | 0 | 2040 | 2044 | 2079 | 35 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | gas-2030-4 | gas | 1 | 0.92 | 0 | 2040 | 2044 | 2079 | 35 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-offshore-2044 | offshore | 3 | 1 | 0 | 2040 | 2044 | 2074 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-onshore-2042 | onshore | 41 | 0.1 | 0 | 2040 | 2042 | 2067 | 25 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-solar-2042 | solar | 43 | 0.1 | 0 | 2040 | 2042 | 2072 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-battery-2043 | battery | 10 | 1 | 4 | 2041 | 2043 | 2058 | 15 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | gas-2031-11 | gas | 1 | 0.92 | 0 | 2041 | 2045 | 2080 | 35 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | gas-2032-16 | gas | 1 | 0.92 | 0 | 2041 | 2045 | 2080 | 35 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-offshore-2045 | offshore | 4 | 1 | 0 | 2041 | 2045 | 2075 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-onshore-2043 | onshore | 26 | 0.1 | 0 | 2041 | 2043 | 2068 | 25 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-solar-2043 | solar | 33 | 0.1 | 0 | 2041 | 2043 | 2073 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-battery-2044 | battery | 1 | 1 | 4 | 2042 | 2044 | 2059 | 15 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-offshore-2046 | offshore | 2 | 1 | 0 | 2042 | 2046 | 2076 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-onshore-2044 | onshore | 16 | 0.1 | 0 | 2042 | 2044 | 2069 | 25 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-solar-2044 | solar | 23 | 0.1 | 0 | 2042 | 2044 | 2074 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-battery-2045 | battery | 13 | 1 | 4 | 2043 | 2045 | 2060 | 15 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-offshore-2047 | offshore | 5 | 1 | 0 | 2043 | 2047 | 2077 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-onshore-2045 | onshore | 14 | 0.1 | 0 | 2043 | 2045 | 2070 | 25 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-solar-2045 | solar | 23 | 0.1 | 0 | 2043 | 2045 | 2075 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-battery-2046 | battery | 1 | 1 | 4 | 2044 | 2046 | 2061 | 15 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-offshore-2048 | offshore | 4 | 1 | 0 | 2044 | 2048 | 2078 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-onshore-2046 | onshore | 14 | 0.1 | 0 | 2044 | 2046 | 2071 | 25 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-solar-2046 | solar | 22 | 0.1 | 0 | 2044 | 2046 | 2076 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-battery-2047 | battery | 2 | 1 | 4 | 2045 | 2047 | 2062 | 15 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-gas-2049 | gas | 1 | 0.92 | 0 | 2045 | 2049 | 2084 | 35 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-offshore-2049 | offshore | 4 | 1 | 0 | 2045 | 2049 | 2079 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-onshore-2047 | onshore | 13 | 0.1 | 0 | 2045 | 2047 | 2072 | 25 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-solar-2047 | solar | 24 | 0.1 | 0 | 2045 | 2047 | 2077 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-battery-2048 | battery | 2 | 1 | 4 | 2046 | 2048 | 2063 | 15 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-gas-2050 | gas | 4 | 0.92 | 0 | 2046 | 2050 | 2085 | 35 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-offshore-2050 | offshore | 1 | 1 | 0 | 2046 | 2050 | 2080 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-onshore-2048 | onshore | 17 | 0.1 | 0 | 2046 | 2048 | 2073 | 25 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-solar-2048 | solar | 27 | 0.1 | 0 | 2046 | 2048 | 2078 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-onshore-2049 | onshore | 14 | 0.1 | 0 | 2047 | 2049 | 2074 | 25 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-solar-2049 | solar | 33 | 0.1 | 0 | 2047 | 2049 | 2079 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-battery-2050 | battery | 3 | 1 | 4 | 2048 | 2050 | 2065 | 15 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-onshore-2050 | onshore | 11 | 0.1 | 0 | 2048 | 2050 | 2075 | 25 |  |  | Retained dated assumption | demand_plans/target_high.plan.json
target | high | adaptive-solar-2050 | solar | 43 | 0.1 | 0 | 2048 | 2050 | 2080 | 30 |  |  | Retained dated assumption | demand_plans/target_high.plan.json

## All inputs
Complete configuration inventory
Curated assumptions are on the Assumptions sheet. This inventory also preserves historical, overridden and reference values with activity flags. Cohorts, build orders, demand and legacy support have dedicated tables. Exact file paths and keys are retained.
File | Parameter | Value | Activity | Context
assumptions.json | version | 0.1 | Active input, reference or documented sensitivity; see curated assumptions | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | price_base | 2024 real GBP | Active input, reference or documented sensitivity; see curated assumptions | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | demand_twh.Falling Behind.2030 | 324 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | demand_twh.Falling Behind.2035 | 373 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | demand_twh.Falling Behind.2040 | 434 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | demand_twh.Falling Behind.2045 | 504 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | demand_twh.Falling Behind.2050 | 559 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | demand_twh.Holistic Transition.2030 | 339 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | demand_twh.Holistic Transition.2035 | 433 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | demand_twh.Holistic Transition.2040 | 564 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | demand_twh.Holistic Transition.2045 | 654 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | demand_twh.Holistic Transition.2050 | 705 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | demand_twh.Electric Engagement.2030 | 345 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | demand_twh.Electric Engagement.2035 | 450 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | demand_twh.Electric Engagement.2040 | 617 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | demand_twh.Electric Engagement.2045 | 724 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | demand_twh.Electric Engagement.2050 | 785 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | nuclear_gw.Slower.2030 | 3.7 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | nuclear_gw.Slower.2035 | 5 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | nuclear_gw.Slower.2040 | 12 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | nuclear_gw.Slower.2045 | 25 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | nuclear_gw.Slower.2050 | 40 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | nuclear_gw.Reference.2030 | 3.7 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | nuclear_gw.Reference.2035 | 10 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | nuclear_gw.Reference.2040 | 22 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | nuclear_gw.Reference.2045 | 40 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | nuclear_gw.Reference.2050 | 53.3 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | nuclear_gw.Faster.2030 | 3.7 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | nuclear_gw.Faster.2035 | 12 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | nuclear_gw.Faster.2040 | 28 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | nuclear_gw.Faster.2045 | 46 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | nuclear_gw.Faster.2050 | 60.9 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | renewable_twh.2030 | 225 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | renewable_twh.2035 | 225 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | renewable_twh.2040 | 210 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | renewable_twh.2045 | 190 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | renewable_twh.2050 | 175 | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | renewable_split.offshore | 0.58512 | Active input, reference or documented sensitivity; see curated assumptions | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | renewable_split.onshore | 0.22237 | Active input, reference or documented sensitivity; see curated assumptions | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | renewable_split.solar | 0.19251 | Active input, reference or documented sensitivity; see curated assumptions | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | technology.solar.capex_gbp_kw.low | 504.2308 | Inherited capital proxy; new projects overridden | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded Model override v1.24: solar operating and capital-recovery life 30 years, replacing source-table 38-year cost proxy; original source data retained.
assumptions.json | technology.solar.capex_gbp_kw.central | 647.3077 | Inherited capital proxy; new projects overridden | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded Model override v1.24: solar operating and capital-recovery life 30 years, replacing source-table 38-year cost proxy; original source data retained.
assumptions.json | technology.solar.capex_gbp_kw.high | 694.6154 | Inherited capital proxy; new projects overridden | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded Model override v1.24: solar operating and capital-recovery life 30 years, replacing source-table 38-year cost proxy; original source data retained.
assumptions.json | technology.solar.fixed_gbp_kw_year | 7.5 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded Model override v1.24: solar operating and capital-recovery life 30 years, replacing source-table 38-year cost proxy; original source data retained.
assumptions.json | technology.solar.variable_gbp_mwh | 0 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded Model override v1.24: solar operating and capital-recovery life 30 years, replacing source-table 38-year cost proxy; original source data retained.
assumptions.json | technology.solar.lifetime_years | 30 | Inherited capital proxy; new projects overridden | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded Model override v1.24: solar operating and capital-recovery life 30 years, replacing source-table 38-year cost proxy; original source data retained.
assumptions.json | technology.solar.construction_years | 1 | Inherited capital proxy; new projects overridden | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded Model override v1.24: solar operating and capital-recovery life 30 years, replacing source-table 38-year cost proxy; original source data retained.
assumptions.json | technology.solar.wacc | 0.076 | Inherited capital proxy; new projects overridden | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded Model override v1.24: solar operating and capital-recovery life 30 years, replacing source-table 38-year cost proxy; original source data retained.
assumptions.json | technology.solar.capacity_factor | 0.12 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded Model override v1.24: solar operating and capital-recovery life 30 years, replacing source-table 38-year cost proxy; original source data retained.
assumptions.json | technology.solar.decommission_gbp_kw | 16.1 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded Model override v1.24: solar operating and capital-recovery life 30 years, replacing source-table 38-year cost proxy; original source data retained.
assumptions.json | technology.solar.efficiency | 0 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded Model override v1.24: solar operating and capital-recovery life 30 years, replacing source-table 38-year cost proxy; original source data retained.
assumptions.json | technology.solar.source | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded Model override v1.24: solar operating and capital-recovery life 30 years, replacing source-table 38-year cost proxy; original source data retained. | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded Model override v1.24: solar operating and capital-recovery life 30 years, replacing source-table 38-year cost proxy; original source data retained.
assumptions.json | technology.onshore.capex_gbp_kw.low | 1291.938 | Inherited capital proxy; new projects overridden | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.onshore.capex_gbp_kw.central | 1695.8915 | Inherited capital proxy; new projects overridden | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.onshore.capex_gbp_kw.high | 2328.6047 | Inherited capital proxy; new projects overridden | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.onshore.fixed_gbp_kw_year | 22.2 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.onshore.variable_gbp_mwh | 0 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.onshore.lifetime_years | 35 | Inherited capital proxy; new projects overridden | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.onshore.construction_years | 2 | Inherited capital proxy; new projects overridden | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.onshore.wacc | 0.076 | Inherited capital proxy; new projects overridden | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.onshore.capacity_factor | 0.36 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.onshore.decommission_gbp_kw | 31.9 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.onshore.efficiency | 0 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.onshore.source | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.offshore.capex_gbp_kw.low | 2210 | Inherited capital proxy; new projects overridden | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.offshore.capex_gbp_kw.central | 2670 | Inherited capital proxy; new projects overridden | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.offshore.capex_gbp_kw.high | 3340 | Inherited capital proxy; new projects overridden | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.offshore.fixed_gbp_kw_year | 54.9 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.offshore.variable_gbp_mwh | 0 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.offshore.lifetime_years | 30 | Inherited capital proxy; new projects overridden | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.offshore.construction_years | 3 | Inherited capital proxy; new projects overridden | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.offshore.wacc | 0.089 | Inherited capital proxy; new projects overridden | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.offshore.capacity_factor | 0.48 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.offshore.decommission_gbp_kw | 265.2 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.offshore.efficiency | 0 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.offshore.source | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.gas.capex_gbp_kw.low | 817.3229 | Inherited capital proxy; new projects overridden | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.gas.capex_gbp_kw.central | 1034.6459 | Inherited capital proxy; new projects overridden | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.gas.capex_gbp_kw.high | 1149.2917 | Inherited capital proxy; new projects overridden | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.gas.fixed_gbp_kw_year | 18.5 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.gas.variable_gbp_mwh | 5 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.gas.lifetime_years | 25 | Inherited capital proxy; new projects overridden | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.gas.construction_years | 3 | Inherited capital proxy; new projects overridden | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.gas.wacc | 0.089 | Inherited capital proxy; new projects overridden | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.gas.capacity_factor | 0.86 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.gas.decommission_gbp_kw | 0 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.gas.efficiency | 0.54 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.gas.source | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 column; source 2024 GBP; use-of-system charges excluded
assumptions.json | technology.nuclear.capex_gbp_kw.low | 6000 | Inherited capital proxy; new projects overridden | Policy illustration £4bn/470MW and £100m annual operating/lifecycle allowance, divided by illustrative 1.06 2026/2024 price deflator; ranges are analyst sensitivities, not bids. Nuclear fuel included in allowance.
assumptions.json | technology.nuclear.capex_gbp_kw.central | 8028.9041 | Inherited capital proxy; new projects overridden | Policy illustration £4bn/470MW and £100m annual operating/lifecycle allowance, divided by illustrative 1.06 2026/2024 price deflator; ranges are analyst sensitivities, not bids. Nuclear fuel included in allowance.
assumptions.json | technology.nuclear.capex_gbp_kw.high | 12000 | Inherited capital proxy; new projects overridden | Policy illustration £4bn/470MW and £100m annual operating/lifecycle allowance, divided by illustrative 1.06 2026/2024 price deflator; ranges are analyst sensitivities, not bids. Nuclear fuel included in allowance.
assumptions.json | technology.nuclear.fixed_gbp_kw_year | 200.7226 | Active input, reference or documented sensitivity; see curated assumptions | Policy illustration £4bn/470MW and £100m annual operating/lifecycle allowance, divided by illustrative 1.06 2026/2024 price deflator; ranges are analyst sensitivities, not bids. Nuclear fuel included in allowance.
assumptions.json | technology.nuclear.variable_gbp_mwh | 0 | Active input, reference or documented sensitivity; see curated assumptions | Policy illustration £4bn/470MW and £100m annual operating/lifecycle allowance, divided by illustrative 1.06 2026/2024 price deflator; ranges are analyst sensitivities, not bids. Nuclear fuel included in allowance.
assumptions.json | technology.nuclear.lifetime_years | 60 | Inherited capital proxy; new projects overridden | Policy illustration £4bn/470MW and £100m annual operating/lifecycle allowance, divided by illustrative 1.06 2026/2024 price deflator; ranges are analyst sensitivities, not bids. Nuclear fuel included in allowance.
assumptions.json | technology.nuclear.construction_years | 6 | Inherited capital proxy; new projects overridden | Policy illustration £4bn/470MW and £100m annual operating/lifecycle allowance, divided by illustrative 1.06 2026/2024 price deflator; ranges are analyst sensitivities, not bids. Nuclear fuel included in allowance.
assumptions.json | technology.nuclear.wacc | 0.056 | Inherited capital proxy; new projects overridden | Policy illustration £4bn/470MW and £100m annual operating/lifecycle allowance, divided by illustrative 1.06 2026/2024 price deflator; ranges are analyst sensitivities, not bids. Nuclear fuel included in allowance.
assumptions.json | technology.nuclear.capacity_factor | 0.9 | Active input, reference or documented sensitivity; see curated assumptions | Policy illustration £4bn/470MW and £100m annual operating/lifecycle allowance, divided by illustrative 1.06 2026/2024 price deflator; ranges are analyst sensitivities, not bids. Nuclear fuel included in allowance.
assumptions.json | technology.nuclear.decommission_gbp_kw | 0 | Active input, reference or documented sensitivity; see curated assumptions | Policy illustration £4bn/470MW and £100m annual operating/lifecycle allowance, divided by illustrative 1.06 2026/2024 price deflator; ranges are analyst sensitivities, not bids. Nuclear fuel included in allowance.
assumptions.json | technology.nuclear.efficiency | 0 | Active input, reference or documented sensitivity; see curated assumptions | Policy illustration £4bn/470MW and £100m annual operating/lifecycle allowance, divided by illustrative 1.06 2026/2024 price deflator; ranges are analyst sensitivities, not bids. Nuclear fuel included in allowance.
assumptions.json | technology.nuclear.capex_includes_construction_finance | TRUE | Active input, reference or documented sensitivity; see curated assumptions | Policy illustration £4bn/470MW and £100m annual operating/lifecycle allowance, divided by illustrative 1.06 2026/2024 price deflator; ranges are analyst sensitivities, not bids. Nuclear fuel included in allowance.
assumptions.json | technology.nuclear.source | Policy illustration £4bn/470MW and £100m annual operating/lifecycle allowance, divided by illustrative 1.06 2026/2024 price deflator; ranges are analyst sensitivities, not bids. Nuclear fuel included in allowance. | Active input, reference or documented sensitivity; see curated assumptions | Policy illustration £4bn/470MW and £100m annual operating/lifecycle allowance, divided by illustrative 1.06 2026/2024 price deflator; ranges are analyst sensitivities, not bids. Nuclear fuel included in allowance.
assumptions.json | gas.capacity_gw | 35 | Active input, reference or documented sensitivity; see curated assumptions | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates.
assumptions.json | gas.availability | 0.9 | Active input, reference or documented sensitivity; see curated assumptions | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates.
assumptions.json | gas.unit_gw | 0.5 | Active input, reference or documented sensitivity; see curated assumptions | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates.
assumptions.json | gas.min_load_fraction | 0.4 | Active input, reference or documented sensitivity; see curated assumptions | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates.
assumptions.json | gas.min_up_hours | 4 | Active input, reference or documented sensitivity; see curated assumptions | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates.
assumptions.json | gas.min_down_hours | 2 | Active input, reference or documented sensitivity; see curated assumptions | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates.
assumptions.json | gas.start_lead_hours | 2 | Active input, reference or documented sensitivity; see curated assumptions | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates.
assumptions.json | gas.ramp_fraction_per_hour | 0.6 | Active input, reference or documented sensitivity; see curated assumptions | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates.
assumptions.json | gas.efficiency_full_lhv | 0.58 | Active input, reference or documented sensitivity; see curated assumptions | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates.
assumptions.json | gas.efficiency_at_min_load_lhv | 0.47 | Active input, reference or documented sensitivity; see curated assumptions | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates.
assumptions.json | gas.start_fuel_mwh_per_mw | 1.5 | Active input, reference or documented sensitivity; see curated assumptions | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates.
assumptions.json | gas.start_wear_gbp_per_mw | 30 | Active input, reference or documented sensitivity; see curated assumptions | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates.
assumptions.json | gas.fuel_gbp_mwh_lhv | 30 | Active input, reference or documented sensitivity; see curated assumptions | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates.
assumptions.json | gas.co2_t_per_mwh_fuel_lhv | 0.202 | Active input, reference or documented sensitivity; see curated assumptions | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates.
assumptions.json | gas.source | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates. | Active input, reference or documented sensitivity; see curated assumptions | Operational parameters are provisional representative CCGT sensitivities; fuel-price and emissions values are scenario inputs, not plant-calibrated estimates.
assumptions.json | storage.power_gw | 10 | Overridden by fleet/pooling | Analyst storage sensitivity, not contracted fleet or supplier quote; zero initial charge avoids free energy.
assumptions.json | storage.energy_gwh | 40 | Overridden by fleet/pooling | Analyst storage sensitivity, not contracted fleet or supplier quote; zero initial charge avoids free energy.
assumptions.json | storage.roundtrip_efficiency | 0.85 | Overridden by fleet/pooling | Analyst storage sensitivity, not contracted fleet or supplier quote; zero initial charge avoids free energy.
assumptions.json | storage.initial_soc_gwh | 0 | Active input, reference or documented sensitivity; see curated assumptions | Analyst storage sensitivity, not contracted fleet or supplier quote; zero initial charge avoids free energy.
assumptions.json | storage.capex_gbp_kw | 200 | Inherited capital proxy; new projects overridden | Analyst storage sensitivity, not contracted fleet or supplier quote; zero initial charge avoids free energy.
assumptions.json | storage.capex_gbp_kwh | 150 | Inherited capital proxy; new projects overridden | Analyst storage sensitivity, not contracted fleet or supplier quote; zero initial charge avoids free energy.
assumptions.json | storage.fixed_gbp_kw_year | 10 | Active input, reference or documented sensitivity; see curated assumptions | Analyst storage sensitivity, not contracted fleet or supplier quote; zero initial charge avoids free energy.
assumptions.json | storage.life_years | 15 | Active input, reference or documented sensitivity; see curated assumptions | Analyst storage sensitivity, not contracted fleet or supplier quote; zero initial charge avoids free energy.
assumptions.json | storage.wacc | 0.07 | Inherited capital proxy; new projects overridden | Analyst storage sensitivity, not contracted fleet or supplier quote; zero initial charge avoids free energy.
assumptions.json | storage.source | Analyst storage sensitivity, not contracted fleet or supplier quote; zero initial charge avoids free energy. | Active input, reference or documented sensitivity; see curated assumptions | Analyst storage sensitivity, not contracted fleet or supplier quote; zero initial charge avoids free energy.
assumptions.json | operations.reserve_gw | 2 | Active input, reference or documented sensitivity; see curated assumptions | Fixed common operating screens, not a probabilistic reliability standard; inertia omits regional strength/dynamics. Other/coal use all-in proxy prices.
assumptions.json | operations.minimum_inertia_gws | 120 | Active input, reference or documented sensitivity; see curated assumptions | Fixed common operating screens, not a probabilistic reliability standard; inertia omits regional strength/dynamics. Other/coal use all-in proxy prices.
assumptions.json | operations.nuclear_inertia_seconds | 5 | Active input, reference or documented sensitivity; see curated assumptions | Fixed common operating screens, not a probabilistic reliability standard; inertia omits regional strength/dynamics. Other/coal use all-in proxy prices.
assumptions.json | operations.gas_inertia_seconds | 5 | Active input, reference or documented sensitivity; see curated assumptions | Fixed common operating screens, not a probabilistic reliability standard; inertia omits regional strength/dynamics. Other/coal use all-in proxy prices.
assumptions.json | operations.external_inertia_gws | 0 | Active input, reference or documented sensitivity; see curated assumptions | Fixed common operating screens, not a probabilistic reliability standard; inertia omits regional strength/dynamics. Other/coal use all-in proxy prices.
assumptions.json | operations.nuclear_availability | 0.9 | Active input, reference or documented sensitivity; see curated assumptions | Fixed common operating screens, not a probabilistic reliability standard; inertia omits regional strength/dynamics. Other/coal use all-in proxy prices.
assumptions.json | operations.imports_available_gw | 0 | Historical/overridden; see Methods M32 | Fixed common operating screens, not a probabilistic reliability standard; inertia omits regional strength/dynamics. Other/coal use all-in proxy prices.
assumptions.json | operations.import_price_gbp_mwh | 80 | Historical/overridden; see Methods M32 | Fixed common operating screens, not a probabilistic reliability standard; inertia omits regional strength/dynamics. Other/coal use all-in proxy prices.
assumptions.json | operations.other_twh | 15 | Historical/overridden; see Methods M32 | Fixed common operating screens, not a probabilistic reliability standard; inertia omits regional strength/dynamics. Other/coal use all-in proxy prices.
assumptions.json | operations.other_cost_gbp_mwh | 80 | Active input, reference or documented sensitivity; see curated assumptions | Fixed common operating screens, not a probabilistic reliability standard; inertia omits regional strength/dynamics. Other/coal use all-in proxy prices.
assumptions.json | operations.coal_gw | 2 | Historical/overridden; see Methods M32 | Fixed common operating screens, not a probabilistic reliability standard; inertia omits regional strength/dynamics. Other/coal use all-in proxy prices.
assumptions.json | operations.coal_load_factor | 0.25 | Historical/overridden; see Methods M32 | Fixed common operating screens, not a probabilistic reliability standard; inertia omits regional strength/dynamics. Other/coal use all-in proxy prices.
assumptions.json | operations.coal_cost_gbp_mwh | 100 | Historical/overridden; see Methods M32 | Fixed common operating screens, not a probabilistic reliability standard; inertia omits regional strength/dynamics. Other/coal use all-in proxy prices.
assumptions.json | operations.coal_co2_t_mwh | 0.9 | Historical/overridden; see Methods M32 | Fixed common operating screens, not a probabilistic reliability standard; inertia omits regional strength/dynamics. Other/coal use all-in proxy prices.
assumptions.json | operations.source | Fixed common operating screens, not a probabilistic reliability standard; inertia omits regional strength/dynamics. Other/coal use all-in proxy prices. | Active input, reference or documented sensitivity; see curated assumptions | Fixed common operating screens, not a probabilistic reliability standard; inertia omits regional strength/dynamics. Other/coal use all-in proxy prices.
assumptions.json | fiscal.carbon_gbp_t | 10 | Historical/overridden; see Methods M32 | Carbon tax is nominal £10; fixed 2024-price model treats £10 as real sensitivity pending inflation path. Legacy transfer is a fiscal illustration and is excluded from physical system cost.
assumptions.json | fiscal.carbon_start_year | 2031 | Historical/overridden; see Methods M32 | Carbon tax is nominal £10; fixed 2024-price model treats £10 as real sensitivity pending inflation path. Legacy transfer is a fiscal illustration and is excluded from physical system cost.
assumptions.json | fiscal.legacy_annual_gbp_bn | 12.5 | Historical/overridden; see Methods M32 | Carbon tax is nominal £10; fixed 2024-price model treats £10 as real sensitivity pending inflation path. Legacy transfer is a fiscal illustration and is excluded from physical system cost.
assumptions.json | fiscal.source | Carbon tax is nominal £10; fixed 2024-price model treats £10 as real sensitivity pending inflation path. Legacy transfer is a fiscal illustration and is excluded from physical system cost. | Historical/overridden; see Methods M32 | Carbon tax is nominal £10; fixed 2024-price model treats £10 as real sensitivity pending inflation path. Legacy transfer is a fiscal illustration and is excluded from physical system cost.
assumptions.json | unpriced_items[0] | network reinforcement and network operating costs | Active input, reference or documented sensitivity; see curated assumptions | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | unpriced_items[1] | locational constraint redispatch | Active input, reference or documented sensitivity; see curated assumptions | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | unpriced_items[2] | purchased stability services and regional system strength | Active input, reference or documented sensitivity; see curated assumptions | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | unpriced_items[3] | sub-hourly balancing and forecast error | Active input, reference or documented sensitivity; see curated assumptions | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | unpriced_items[4] | retail/administration | Active input, reference or documented sensitivity; see curated assumptions | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | unpriced_items[5] | actual legacy contract cashflows and market settlements | Active input, reference or documented sensitivity; see curated assumptions | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | unpriced_items[6] | fuel-security infrastructure | Active input, reference or documented sensitivity; see curated assumptions | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | screen.max_unserved_mwh | 1 | Active input, reference or documented sensitivity; see curated assumptions | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | screen.max_reserve_shortfall_hours | 0 | Active input, reference or documented sensitivity; see curated assumptions | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | screen.max_inertia_shortfall_hours | 0 | Active input, reference or documented sensitivity; see curated assumptions | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
assumptions.json | method | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation. | Historical/overridden; see Methods M32 | Deterministic heuristic block commitment, hourly energy balance, system-surplus-only storage, no cost optimisation. Historical profiles contain existing curtailment and fleet changes; future scaled shapes are proxies, not unconstrained weather simulation.
coal_assumptions.json | version | 0.2-coal | Historical coal study settings | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | status | Analyst sensitivities, not UK engineering bids or a mine-development forecast | Historical coal study settings | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.availability | 0.85 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.unit_gw | 0.5 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.min_load_fraction | 0.4 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.min_up_hours | 12 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.min_down_hours | 8 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.start_lead_hours | 8 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.ramp_fraction_per_hour | 0.25 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.efficiency_full_lhv | 0.4 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.efficiency_min_lhv | 0.33 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.start_fuel_mwh_per_mw | 5 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.inertia_seconds | 5 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.heat_content_mwh_tonne | 6.7 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.co2_t_mwh_fuel | 0.34 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.fuel_gbp_tonne | 100 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.capex_gbp_kw | 3000 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.capex_low_gbp_kw | 2000 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.capex_high_gbp_kw | 5000 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.fixed_gbp_kw_year | 50 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.variable_gbp_mwh | 6 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.start_wear_gbp_mw | 50 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.wacc | 0.089 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.recovery_years | 25 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.construction_years | 4 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.preconstruction_years | 2 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.decision_year | 2029 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.stock_days_full_output | 30 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.domestic_supply_mt_year | 0 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | coal.domestic_alternative_mt_year | 5 | Active input, reference or documented sensitivity; see curated assumptions | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | fuel_imports.gas_import_share | 0.6 | Historical coal study settings | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | fuel_imports.gas_import_share_low | 0.3 | Historical coal study settings | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | fuel_imports.gas_import_share_high | 0.9 | Historical coal study settings | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | stress.gas_capacity_fraction | 0.5 | Historical coal study settings | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | stress.gas_days | 14 | Historical coal study settings | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | stress.coal_import_interruption_days | 45 | Historical coal study settings | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | source_notes[0] | Coal operational parameters, costs and stock policies are editable analyst assumptions; they require supplier and operator validation. | Historical coal study settings | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | source_notes[1] | EIA 2022 reference lead times: coal 4 years, combined-cycle gas 3 years; neither is a current UK delivery quote. Two preconstruction years are added as an analyst assumption. https://www.eia.gov/outlooks/aeo/assumptions/pdf/table_8.2.pdf | Historical coal study settings | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | source_notes[2] | DUKES 2026 coal chapter: 2025 UK output 0.12 Mt; economically recoverable/minable resource estimate approximately 3.8 billion tonnes is not annual deliverability. https://assets.publishing.service.gov.uk/media/6a6a1c5724593dd070ba47cc/DUKES_2026_Chapter_2.pdf | Historical coal study settings | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | source_notes[3] | 0 to 5 Mt/year domestic supply and 30 to 90 percent imported gas are sensitivities, not forecasts. No new mine is assumed already contracted. | Historical coal study settings | Analyst sensitivities, not UK engineering bids or a mine-development forecast
coal_assumptions.json | source_notes[4] | All prices real 2024 GBP; no currency conversion of EIA construction cost estimates is used. Coal price includes assumed delivered fuel costs but new mine, rail and stockyard capital are unpriced. | Historical coal study settings | Analyst sensitivities, not UK engineering bids or a mine-development forecast
planner/lifecycle.json | version | 1.13.1 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | status | Agreed operating-life assumptions; financing recovery remains a separate editable input. | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.nuclear.life | 60 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.nuclear.recovery | 60 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.nuclear.life_range[0] | 60 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.nuclear.life_range[1] | 60 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.gas.life | 35 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.gas.recovery | 35 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.gas.life_range[0] | 30 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.gas.life_range[1] | 40 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.coal.life | 50 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.coal.recovery | 50 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.coal.life_range[0] | 40 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.coal.life_range[1] | 60 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.solar.life | 30 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.solar.recovery | 30 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.solar.life_range[0] | 25 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.solar.life_range[1] | 35 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.onshore.life | 25 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.onshore.recovery | 25 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.onshore.life_range[0] | 20 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.onshore.life_range[1] | 30 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.offshore.life | 30 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.offshore.recovery | 30 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.offshore.life_range[0] | 25 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.offshore.life_range[1] | 30 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.battery.life | 15 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.battery.recovery | 15 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.battery.life_range[0] | 15 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | technologies.battery.life_range[1] | 15 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | solar.degradation | 0.008 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | solar.degradation_range[0] | 0.005 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | solar.degradation_range[1] | 0.01 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | solar.inverter_interval | 15 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | solar.inverter_capital_fraction | 0.1 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | solar.inverter_fraction_range[0] | 0.05 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | solar.inverter_fraction_range[1] | 0.15 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | solar.replacement_accounting | Provisional 10% of original overnight capital per 15-year inverter replacement, funded from existing fixed O&M allowance (not added again to resource cost). Allocation is an analyst estimate, not a supplier quote; verify O&M scope before investment appraisal. Panel repowering requires a new project. | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | nuclear.lead | 5 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | nuclear.planning_years | 1 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | nuclear.repeat_construction_years | 4 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | nuclear.finance_quote_reference_years | 6 | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | nuclear.readiness | Five-year lead applies to repeat fleet units after design and factory readiness. User must schedule starts accordingly; no assumed date for first-of-kind readiness. | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | sources[0].url | https://www.rolls-royce-smr.com/our-approach | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | sources[0].use | Four-year on-site repeat-unit construction; one-year planning is policy assumption. | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | sources[1].url | https://oa.upm.es/43685/ | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | sources[1].use | Historical UK systems: approximately 0.8% annual degradation; extrapolation to future utility-scale equipment is an assumption. | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | sources[2].url | https://eprints.whiterose.ac.uk/id/eprint/177737/ | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | sources[2].use | UK study of 3000 installations, silicon degradation approximately 0.81–0.94% annually. | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | sources[3].url | https://atb-archive.nrel.gov/electricity/2019/index.html?m=1&s=omcfmdpr&t=insusrsccn | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | sources[3].use | Inverter replacement at 15 years precedent; does not establish our cost fraction. | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | scope | Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here. | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
planner/lifecycle.json | closure_policy | No policy-driven early coal closure assumed. Early retirement occurs only when explicitly entered by the user. | Active input, reference or documented sensitivity; see curated assumptions | Agreed operating-life assumptions; financing recovery remains a separate editable input.; Applies to dated build-plan editor and its hourly evaluator. Existing named fleet retirement dates preserved. Older comparison studies remain versioned historical results, not recalculated here.
construction/estimates.json | version | construction-reference-4 | Active input, reference or documented sensitivity; see curated assumptions | Reference cost / foreign currency per GBP × 2024 CPI / source-year CPI × target capacity / reference capacity. Gross-to-net assumptions applied only where disclosed here. Linear capacity scaling is a first-pass estimate; no economies of scale assumed.
construction/estimates.json | date | 2026-10-18 | Active input, reference or documented sensitivity; see curated assumptions | Reference cost / foreign currency per GBP × 2024 CPI / source-year CPI × target capacity / reference capacity. Gross-to-net assumptions applied only where disclosed here. Linear capacity scaling is a first-pass estimate; no economies of scale assumed.
construction/estimates.json | price_basis | 2024 GBP, except SMR assigned to that basis by explicit policy convention | Active input, reference or documented sensitivity; see curated assumptions | Reference cost / foreign currency per GBP × 2024 CPI / source-year CPI × target capacity / reference capacity. Gross-to-net assumptions applied only where disclosed here. Linear capacity scaling is a first-pass estimate; no economies of scale assumed.
construction/estimates.json | cpi_annual_2015_100.2012 | 96.1 | Active input, reference or documented sensitivity; see curated assumptions | Reference cost / foreign currency per GBP × 2024 CPI / source-year CPI × target capacity / reference capacity. Gross-to-net assumptions applied only where disclosed here. Linear capacity scaling is a first-pass estimate; no economies of scale assumed.
construction/estimates.json | cpi_annual_2015_100.2021 | 111.6 | Active input, reference or documented sensitivity; see curated assumptions | Reference cost / foreign currency per GBP × 2024 CPI / source-year CPI × target capacity / reference capacity. Gross-to-net assumptions applied only where disclosed here. Linear capacity scaling is a first-pass estimate; no economies of scale assumed.
construction/estimates.json | cpi_annual_2015_100.2023 | 130.5 | Active input, reference or documented sensitivity; see curated assumptions | Reference cost / foreign currency per GBP × 2024 CPI / source-year CPI × target capacity / reference capacity. Gross-to-net assumptions applied only where disclosed here. Linear capacity scaling is a first-pass estimate; no economies of scale assumed.
construction/estimates.json | cpi_annual_2015_100.2024 | 133.9 | Active input, reference or documented sensitivity; see curated assumptions | Reference cost / foreign currency per GBP × 2024 CPI / source-year CPI × target capacity / reference capacity. Gross-to-net assumptions applied only where disclosed here. Linear capacity scaling is a first-pass estimate; no economies of scale assumed.
construction/estimates.json | cpi_annual_2015_100.2025 | 138.4 | Active input, reference or documented sensitivity; see curated assumptions | Reference cost / foreign currency per GBP × 2024 CPI / source-year CPI × target capacity / reference capacity. Gross-to-net assumptions applied only where disclosed here. Linear capacity scaling is a first-pass estimate; no economies of scale assumed.
construction/estimates.json | fx_foreign_units_per_gbp.USD_2023_average | 1.2432 | Active input, reference or documented sensitivity; see curated assumptions | Reference cost / foreign currency per GBP × 2024 CPI / source-year CPI × target capacity / reference capacity. Gross-to-net assumptions applied only where disclosed here. Linear capacity scaling is a first-pass estimate; no economies of scale assumed.
construction/estimates.json | fx_foreign_units_per_gbp.PLN_2025_average | 4.9685 | Active input, reference or documented sensitivity; see curated assumptions | Reference cost / foreign currency per GBP × 2024 CPI / source-year CPI × target capacity / reference capacity. Gross-to-net assumptions applied only where disclosed here. Linear capacity scaling is a first-pass estimate; no economies of scale assumed.
construction/estimates.json | fx_foreign_units_per_gbp.PLN_2012_09_21 | 5.1678 | Active input, reference or documented sensitivity; see curated assumptions | Reference cost / foreign currency per GBP × 2024 CPI / source-year CPI × target capacity / reference capacity. Gross-to-net assumptions applied only where disclosed here. Linear capacity scaling is a first-pass estimate; no economies of scale assumed.
construction/estimates.json | sources.ons | https://www.ons.gov.uk/economy/inflationandpriceindices/timeseries/d7bt/mm23 | Active input, reference or documented sensitivity; see curated assumptions | Reference cost / foreign currency per GBP × 2024 CPI / source-year CPI × target capacity / reference capacity. Gross-to-net assumptions applied only where disclosed here. Linear capacity scaling is a first-pass estimate; no economies of scale assumed.
construction/estimates.json | sources.fx2023 | https://www.trade-tariff.service.gov.uk/exchange_rates/view/2023-12?type=average | Active input, reference or documented sensitivity; see curated assumptions | Reference cost / foreign currency per GBP × 2024 CPI / source-year CPI × target capacity / reference capacity. Gross-to-net assumptions applied only where disclosed here. Linear capacity scaling is a first-pass estimate; no economies of scale assumed.
construction/estimates.json | sources.fx2025 | https://www.trade-tariff.service.gov.uk/exchange_rates/view/2025-12?type=average | Active input, reference or documented sensitivity; see curated assumptions | Reference cost / foreign currency per GBP × 2024 CPI / source-year CPI × target capacity / reference capacity. Gross-to-net assumptions applied only where disclosed here. Linear capacity scaling is a first-pass estimate; no economies of scale assumed.
construction/estimates.json | sources.fx2012 | https://api.nbp.pl/api/exchangerates/rates/a/gbp/2012-09-21/?format=json | Active input, reference or documented sensitivity; see curated assumptions | Reference cost / foreign currency per GBP × 2024 CPI / source-year CPI × target capacity / reference capacity. Gross-to-net assumptions applied only where disclosed here. Linear capacity scaling is a first-pass estimate; no economies of scale assumed.
construction/estimates.json | sources.gas | https://ir.enea.pl/pr/855237/podpisanie-umowy-na-budowe-blokow-gazowo-parowych | Active input, reference or documented sensitivity; see curated assumptions | Reference cost / foreign currency per GBP × 2024 CPI / source-year CPI × target capacity / reference capacity. Gross-to-net assumptions applied only where disclosed here. Linear capacity scaling is a first-pass estimate; no economies of scale assumed.
construction/estimates.json | sources.coal | https://ir.enea.pl/pr/290738/zawarcie-przez-enea-wytwarzanie-s-a-umowy-na-budowe-bloku-energetycznego | Active input, reference or documented sensitivity; see curated assumptions | Reference cost / foreign currency per GBP × 2024 CPI / source-year CPI × target capacity / reference capacity. Gross-to-net assumptions applied only where disclosed here. Linear capacity scaling is a first-pass estimate; no economies of scale assumed.
construction/estimates.json | sources.eia | https://www.eia.gov/analysis/studies/powerplants/capitalcost/pdf/capital_cost_AEO2025.pdf | Active input, reference or documented sensitivity; see curated assumptions | Reference cost / foreign currency per GBP × 2024 CPI / source-year CPI × target capacity / reference capacity. Gross-to-net assumptions applied only where disclosed here. Linear capacity scaling is a first-pass estimate; no economies of scale assumed.
construction/estimates.json | sources.arup | https://assets.publishing.service.gov.uk/media/68ba91f411b4ded2da19fe92/onshore-wind-and-solar-pv-cost-electricity-report-update-2024.pdf | Active input, reference or documented sensitivity; see curated assumptions | Reference cost / foreign currency per GBP × 2024 CPI / source-year CPI × target capacity / reference capacity. Gross-to-net assumptions applied only where disclosed here. Linear capacity scaling is a first-pass estimate; no economies of scale assumed.
construction/estimates.json | sources.offshore | https://doggerbank.com/construction/dogger-bank-c-reaches-financial-close/ | Active input, reference or documented sensitivity; see curated assumptions | Reference cost / foreign currency per GBP × 2024 CPI / source-year CPI × target capacity / reference capacity. Gross-to-net assumptions applied only where disclosed here. Linear capacity scaling is a first-pass estimate; no economies of scale assumed.
construction/estimates.json | sources.smr | https://www.rolls-royce.com/media/press-releases/2021/17-05-2021-more-power-and-updated-design-revealed-as-nuclear-power-team-targets-first-place.aspx | Active input, reference or documented sensitivity; see curated assumptions | Reference cost / foreign currency per GBP × 2024 CPI / source-year CPI × target capacity / reference capacity. Gross-to-net assumptions applied only where disclosed here. Linear capacity scaling is a first-pass estimate; no economies of scale assumed.
construction/estimates.json | sources.desnz2025 | https://www.gov.uk/government/publications/electricity-generation-costs-2025 | Active input, reference or documented sensitivity; see curated assumptions | Reference cost / foreign currency per GBP × 2024 CPI / source-year CPI × target capacity / reference capacity. Gross-to-net assumptions applied only where disclosed here. Linear capacity scaling is a first-pass estimate; no economies of scale assumed.
construction/estimates.json | estimates[0].technology | Repeat SMR | Active input, reference or documented sensitivity; see curated assumptions | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.; Policy assumption; construction scope unverified
construction/estimates.json | estimates[0].unit | One 470 MW module | Active input, reference or documented sensitivity; see curated assumptions | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.; Policy assumption; construction scope unverified
construction/estimates.json | estimates[0].capacity_gw | 0.47 | Active input, reference or documented sensitivity; see curated assumptions | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.; Policy assumption; construction scope unverified
construction/estimates.json | estimates[0].capacity_basis | Manufacturer nameplate; export basis to confirm | Active input, reference or documented sensitivity; see curated assumptions | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.; Policy assumption; construction scope unverified
construction/estimates.json | estimates[0].cost_m | 1800 | Active input, reference or documented sensitivity; see curated assumptions | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.; Policy assumption; construction scope unverified
construction/estimates.json | estimates[0].formula | 1800: user-selected repeat-unit policy assumption | Active input, reference or documented sensitivity; see curated assumptions | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.; Policy assumption; construction scope unverified
construction/estimates.json | estimates[0].status | Policy assumption; construction scope unverified | Active input, reference or documented sensitivity; see curated assumptions | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.; Policy assumption; construction scope unverified
construction/estimates.json | estimates[0].sources[0] | smr | Active input, reference or documented sensitivity; see curated assumptions | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.; Policy assumption; construction scope unverified
construction/estimates.json | estimates[0].note | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections. | Active input, reference or documented sensitivity; see curated assumptions | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.; Policy assumption; construction scope unverified
construction/estimates.json | estimates[0].comparisons.Inflation-only illustration, assuming the £1.8bn target was in 2021 prices | 2159.6774 | Active input, reference or documented sensitivity; see curated assumptions | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.; Policy assumption; construction scope unverified
construction/estimates.json | estimates[0].derived_gbp_bn_per_gw | 3.8298 | Active input, reference or documented sensitivity; see curated assumptions | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.; Policy assumption; construction scope unverified
construction/estimates.json | estimates[0].indicative_annual_utilisation | 0.9 | Active input, reference or documented sensitivity; see curated assumptions | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.; Policy assumption; construction scope unverified
construction/estimates.json | estimates[0].annual_output_label | 90% | Active input, reference or documented sensitivity; see curated assumptions | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.; Policy assumption; construction scope unverified
construction/estimates.json | estimates[0].annual_output_assumption | Existing model nuclear utilisation assumption. | Active input, reference or documented sensitivity; see curated assumptions | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.; Policy assumption; construction scope unverified
construction/estimates.json | estimates[0].indicative_generation_twh_year | 3.7055 | Active input, reference or documented sensitivity; see curated assumptions | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.; Policy assumption; construction scope unverified
construction/estimates.json | estimates[0].annual_generation_basis | Before system curtailment, storage and network losses; not dependable capacity. | Active input, reference or documented sensitivity; see curated assumptions | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.; Policy assumption; construction scope unverified
construction/estimates.json | estimates[1].technology | Combined-cycle gas | Active input, reference or documented sensitivity; see curated assumptions | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.; Recent EPC proxy; associated infrastructure not fully separated
construction/estimates.json | estimates[1].unit | One 920 MW net station | Active input, reference or documented sensitivity; see curated assumptions | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.; Recent EPC proxy; associated infrastructure not fully separated
construction/estimates.json | estimates[1].capacity_gw | 0.92 | Active input, reference or documented sensitivity; see curated assumptions | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.; Recent EPC proxy; associated infrastructure not fully separated
construction/estimates.json | estimates[1].capacity_basis | Net export; assumed 2.5% auxiliary load | Active input, reference or documented sensitivity; see curated assumptions | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.; Recent EPC proxy; associated infrastructure not fully separated
construction/estimates.json | estimates[1].cost_m | 877.1633 | Active input, reference or documented sensitivity; see curated assumptions | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.; Recent EPC proxy; associated infrastructure not fully separated
construction/estimates.json | estimates[1].formula | 6378 / 4.9685 × (133.9 / 138.4) × 920 / (1336 × 0.975) | Active input, reference or documented sensitivity; see curated assumptions | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.; Recent EPC proxy; associated infrastructure not fully separated
construction/estimates.json | estimates[1].status | Recent EPC proxy; associated infrastructure not fully separated | Active input, reference or documented sensitivity; see curated assumptions | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.; Recent EPC proxy; associated infrastructure not fully separated
construction/estimates.json | estimates[1].sources[0] | gas | Active input, reference or documented sensitivity; see curated assumptions | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.; Recent EPC proxy; associated infrastructure not fully separated
construction/estimates.json | estimates[1].sources[1] | fx2025 | Active input, reference or documented sensitivity; see curated assumptions | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.; Recent EPC proxy; associated infrastructure not fully separated
construction/estimates.json | estimates[1].note | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption. | Active input, reference or documented sensitivity; see curated assumptions | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.; Recent EPC proxy; associated infrastructure not fully separated
construction/estimates.json | estimates[1].comparisons.Same contract scaled to 920 MW gross | 855.2342 | Active input, reference or documented sensitivity; see curated assumptions | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.; Recent EPC proxy; associated infrastructure not fully separated
construction/estimates.json | estimates[1].comparisons.US engineering EPC comparator, 920 MW net | 626.1732 | Active input, reference or documented sensitivity; see curated assumptions | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.; Recent EPC proxy; associated infrastructure not fully separated
construction/estimates.json | estimates[1].comparisons.Contract proxy with 1% auxiliary load | 863.873 | Active input, reference or documented sensitivity; see curated assumptions | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.; Recent EPC proxy; associated infrastructure not fully separated
construction/estimates.json | estimates[1].comparisons.Contract proxy with 3% auxiliary load | 881.6848 | Active input, reference or documented sensitivity; see curated assumptions | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.; Recent EPC proxy; associated infrastructure not fully separated
construction/estimates.json | estimates[1].derived_gbp_bn_per_gw | 0.95344 | Active input, reference or documented sensitivity; see curated assumptions | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.; Recent EPC proxy; associated infrastructure not fully separated
construction/estimates.json | estimates[1].indicative_annual_utilisation | 0.9 | Active input, reference or documented sensitivity; see curated assumptions | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.; Recent EPC proxy; associated infrastructure not fully separated
construction/estimates.json | estimates[1].annual_output_label | 90% | Active input, reference or documented sensitivity; see curated assumptions | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.; Recent EPC proxy; associated infrastructure not fully separated
construction/estimates.json | estimates[1].annual_output_assumption | Potential output using existing 90% gas availability assumption; fuel available and full dispatch when available. | Active input, reference or documented sensitivity; see curated assumptions | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.; Recent EPC proxy; associated infrastructure not fully separated
construction/estimates.json | estimates[1].indicative_generation_twh_year | 7.2533 | Active input, reference or documented sensitivity; see curated assumptions | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.; Recent EPC proxy; associated infrastructure not fully separated
construction/estimates.json | estimates[1].annual_generation_basis | Before system curtailment, storage and network losses; not dependable capacity. | Active input, reference or documented sensitivity; see curated assumptions | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.; Recent EPC proxy; associated infrastructure not fully separated
construction/estimates.json | estimates[2].technology | Coal, without carbon capture | Active input, reference or documented sensitivity; see curated assumptions | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.; Older European contract proxy; high UK transfer uncertainty
construction/estimates.json | estimates[2].unit | One 2,000 MW net station | Active input, reference or documented sensitivity; see curated assumptions | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.; Older European contract proxy; high UK transfer uncertainty
construction/estimates.json | estimates[2].capacity_gw | 2 | Active input, reference or documented sensitivity; see curated assumptions | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.; Older European contract proxy; high UK transfer uncertainty
construction/estimates.json | estimates[2].capacity_basis | Net export; assumed 7% auxiliary load | Active input, reference or documented sensitivity; see curated assumptions | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.; Older European contract proxy; high UK transfer uncertainty
construction/estimates.json | estimates[2].cost_m | 2750.8078 | Active input, reference or documented sensitivity; see curated assumptions | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.; Older European contract proxy; high UK transfer uncertainty
construction/estimates.json | estimates[2].formula | 5100 / 5.1678 × (133.9 / 96.1) × 2000 / (1075 × 0.93) | Active input, reference or documented sensitivity; see curated assumptions | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.; Older European contract proxy; high UK transfer uncertainty
construction/estimates.json | estimates[2].status | Older European contract proxy; high UK transfer uncertainty | Active input, reference or documented sensitivity; see curated assumptions | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.; Older European contract proxy; high UK transfer uncertainty
construction/estimates.json | estimates[2].sources[0] | coal | Active input, reference or documented sensitivity; see curated assumptions | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.; Older European contract proxy; high UK transfer uncertainty
construction/estimates.json | estimates[2].sources[1] | fx2012 | Active input, reference or documented sensitivity; see curated assumptions | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.; Older European contract proxy; high UK transfer uncertainty
construction/estimates.json | estimates[2].note | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine. | Active input, reference or documented sensitivity; see curated assumptions | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.; Older European contract proxy; high UK transfer uncertainty
construction/estimates.json | estimates[2].comparisons.Same contract scaled to 2,000 MW gross | 2558.2513 | Active input, reference or documented sensitivity; see curated assumptions | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.; Older European contract proxy; high UK transfer uncertainty
construction/estimates.json | estimates[2].comparisons.US engineering EPC comparator, 2,000 MW net | 6237.5879 | Active input, reference or documented sensitivity; see curated assumptions | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.; Older European contract proxy; high UK transfer uncertainty
construction/estimates.json | estimates[2].comparisons.Contract proxy with 5% auxiliary load | 2692.8961 | Active input, reference or documented sensitivity; see curated assumptions | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.; Older European contract proxy; high UK transfer uncertainty
construction/estimates.json | estimates[2].comparisons.Contract proxy with 10% auxiliary load | 2842.5014 | Active input, reference or documented sensitivity; see curated assumptions | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.; Older European contract proxy; high UK transfer uncertainty
construction/estimates.json | estimates[2].derived_gbp_bn_per_gw | 1.3754 | Active input, reference or documented sensitivity; see curated assumptions | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.; Older European contract proxy; high UK transfer uncertainty
construction/estimates.json | estimates[2].indicative_annual_utilisation | 0.85 | Active input, reference or documented sensitivity; see curated assumptions | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.; Older European contract proxy; high UK transfer uncertainty
construction/estimates.json | estimates[2].annual_output_label | 85% | Active input, reference or documented sensitivity; see curated assumptions | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.; Older European contract proxy; high UK transfer uncertainty
construction/estimates.json | estimates[2].annual_output_assumption | Provisional analyst availability allowance of 85%, including maintenance and outages; fuel available and full dispatch when available. Not a supplier guarantee. | Active input, reference or documented sensitivity; see curated assumptions | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.; Older European contract proxy; high UK transfer uncertainty
construction/estimates.json | estimates[2].indicative_generation_twh_year | 14.892 | Active input, reference or documented sensitivity; see curated assumptions | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.; Older European contract proxy; high UK transfer uncertainty
construction/estimates.json | estimates[2].annual_generation_basis | Before system curtailment, storage and network losses; not dependable capacity. | Active input, reference or documented sensitivity; see curated assumptions | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.; Older European contract proxy; high UK transfer uncertainty
construction/estimates.json | estimates[3].technology | Onshore wind | Active input, reference or documented sensitivity; see curated assumptions | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[3].unit | One 100 MW farm | Active input, reference or documented sensitivity; see curated assumptions | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[3].capacity_gw | 0.1 | Active input, reference or documented sensitivity; see curated assumptions | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[3].capacity_basis | Rated turbine capacity | Active input, reference or documented sensitivity; see curated assumptions | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[3].cost_m | 123.5369 | Active input, reference or documented sensitivity; see curated assumptions | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[3].formula | £1,204/kW × 100,000 kW / 1,000,000 × (133.9 / 130.5) | Active input, reference or documented sensitivity; see curated assumptions | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[3].status | UK construction category, separated from infrastructure and development | Active input, reference or documented sensitivity; see curated assumptions | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[3].sources[0] | arup | Active input, reference or documented sensitivity; see curated assumptions | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[3].note | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate. | Active input, reference or documented sensitivity; see curated assumptions | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[3].comparisons.Source low construction case | 98.809 | Active input, reference or documented sensitivity; see curated assumptions | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[3].comparisons.Source high construction case | 164.4764 | Active input, reference or documented sensitivity; see curated assumptions | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[3].derived_gbp_bn_per_gw | 1.2354 | Active input, reference or documented sensitivity; see curated assumptions | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[3].indicative_annual_utilisation | 0.36 | Active input, reference or documented sensitivity; see curated assumptions | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[3].annual_output_label | 36% | Active input, reference or documented sensitivity; see curated assumptions | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[3].annual_output_assumption | Existing model onshore capacity-factor assumption; site and weather vary. | Active input, reference or documented sensitivity; see curated assumptions | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[3].indicative_generation_twh_year | 0.31536 | Active input, reference or documented sensitivity; see curated assumptions | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[3].annual_generation_basis | Before system curtailment, storage and network losses; not dependable capacity. | Active input, reference or documented sensitivity; see curated assumptions | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[4].technology | Offshore wind | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.; DESNZ construction category; 2024 real GBP; pre-development excluded
construction/estimates.json | estimates[4].unit | One 1,000 MW farm | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.; DESNZ construction category; 2024 real GBP; pre-development excluded
construction/estimates.json | estimates[4].capacity_gw | 1 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.; DESNZ construction category; 2024 real GBP; pre-development excluded
construction/estimates.json | estimates[4].capacity_basis | Rated turbine capacity | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.; DESNZ construction category; 2024 real GBP; pre-development excluded
construction/estimates.json | estimates[4].cost_m | 2500 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.; DESNZ construction category; 2024 real GBP; pre-development excluded
construction/estimates.json | estimates[4].formula | DESNZ 2025 Annex A, Technical and Cost Assumptions, 2030 medium construction: £2,500/kW × 1,000 MW / 1,000 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.; DESNZ construction category; 2024 real GBP; pre-development excluded
construction/estimates.json | estimates[4].status | DESNZ construction category; 2024 real GBP; pre-development excluded | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.; DESNZ construction category; 2024 real GBP; pre-development excluded
construction/estimates.json | estimates[4].sources[0] | desnz2025 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.; DESNZ construction category; 2024 real GBP; pre-development excluded
construction/estimates.json | estimates[4].note | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total. | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.; DESNZ construction category; 2024 real GBP; pre-development excluded
construction/estimates.json | estimates[4].comparisons.DESNZ 2030 low construction case | 2100 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.; DESNZ construction category; 2024 real GBP; pre-development excluded
construction/estimates.json | estimates[4].comparisons.DESNZ 2030 high construction case | 3100 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.; DESNZ construction category; 2024 real GBP; pre-development excluded
construction/estimates.json | estimates[4].comparisons.Previous Dogger Bank C generation-investment proxy | 2049.6938 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.; DESNZ construction category; 2024 real GBP; pre-development excluded
construction/estimates.json | estimates[4].derived_gbp_bn_per_gw | 2.5 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.; DESNZ construction category; 2024 real GBP; pre-development excluded
construction/estimates.json | estimates[4].indicative_annual_utilisation | 0.48 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.; DESNZ construction category; 2024 real GBP; pre-development excluded
construction/estimates.json | estimates[4].annual_output_label | 48% | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.; DESNZ construction category; 2024 real GBP; pre-development excluded
construction/estimates.json | estimates[4].annual_output_assumption | Existing model offshore capacity-factor assumption; site and weather vary. | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.; DESNZ construction category; 2024 real GBP; pre-development excluded
construction/estimates.json | estimates[4].indicative_generation_twh_year | 4.2048 | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.; DESNZ construction category; 2024 real GBP; pre-development excluded
construction/estimates.json | estimates[4].annual_generation_basis | Before system curtailment, storage and network losses; not dependable capacity. | Active input, reference or documented sensitivity; see curated assumptions | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.; DESNZ construction category; 2024 real GBP; pre-development excluded
construction/estimates.json | estimates[5].technology | Solar PV | Active input, reference or documented sensitivity; see curated assumptions | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[5].unit | One 100 MWp farm | Active input, reference or documented sensitivity; see curated assumptions | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[5].capacity_gw | 0.1 | Active input, reference or documented sensitivity; see curated assumptions | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[5].capacity_basis | DC panel capacity, NOT 100 MW AC export | Active input, reference or documented sensitivity; see curated assumptions | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[5].cost_m | 53.56 | Active input, reference or documented sensitivity; see curated assumptions | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[5].formula | £522/kWp × 100,000 kWp / 1,000,000 × (133.9 / 130.5) | Active input, reference or documented sensitivity; see curated assumptions | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[5].status | UK construction category, separated from infrastructure and development | Active input, reference or documented sensitivity; see curated assumptions | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[5].sources[0] | arup | Active input, reference or documented sensitivity; see curated assumptions | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[5].note | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed. | Active input, reference or documented sensitivity; see curated assumptions | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[5].comparisons.Source low construction case | 43.4021 | Active input, reference or documented sensitivity; see curated assumptions | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[5].comparisons.Source high construction case | 61.6658 | Active input, reference or documented sensitivity; see curated assumptions | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[5].derived_gbp_bn_per_gw | 0.5356 | Active input, reference or documented sensitivity; see curated assumptions | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[5].indicative_annual_utilisation | 0.105 | Active input, reference or documented sensitivity; see curated assumptions | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[5].annual_output_label | 10.5% (10–11%) | Active input, reference or documented sensitivity; see curated assumptions | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[5].annual_output_assumption | New DC panels:10.5% first-year potential yield, then0.8% annual degradation and AC export clipping. Inherited fleet uses its separate12% calibration. | Active input, reference or documented sensitivity; see curated assumptions | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[5].indicative_generation_twh_year | 0.09198 | Active input, reference or documented sensitivity; see curated assumptions | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.; UK construction category, separated from infrastructure and development
construction/estimates.json | estimates[5].annual_generation_basis | Before system curtailment, storage and network losses; not dependable capacity. | Active input, reference or documented sensitivity; see curated assumptions | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.; UK construction category, separated from infrastructure and development
construction/estimates.json | dispatch_inputs_updated | TRUE | Active input, reference or documented sensitivity; see curated assumptions | Reference cost / foreign currency per GBP × 2024 CPI / source-year CPI × target capacity / reference capacity. Gross-to-net assumptions applied only where disclosed here. Linear capacity scaling is a first-pass estimate; no economies of scale assumed.
construction/estimates.json | method | Reference cost / foreign currency per GBP × 2024 CPI / source-year CPI × target capacity / reference capacity. Gross-to-net assumptions applied only where disclosed here. Linear capacity scaling is a first-pass estimate; no economies of scale assumed. | Active input, reference or documented sensitivity; see curated assumptions | Reference cost / foreign currency per GBP × 2024 CPI / source-year CPI × target capacity / reference capacity. Gross-to-net assumptions applied only where disclosed here. Linear capacity scaling is a first-pass estimate; no economies of scale assumed.
operating/estimates.json | price_base | 2024 real GBP | Active input, reference or documented sensitivity; see curated assumptions
operating/estimates.json | nuclear.advanced.fixed_gbp_kw_year | 104.9463 | Recorded sensitivity; UI uses central
operating/estimates.json | nuclear.advanced.variable_gbp_mwh | 1.9566 | Recorded sensitivity; UI uses central
operating/estimates.json | nuclear.advanced.fuel_gbp_mwh | 8.8938 | Recorded sensitivity; UI uses central
operating/estimates.json | nuclear.central.fixed_gbp_kw_year | 120.9551 | Active input, reference or documented sensitivity; see curated assumptions
operating/estimates.json | nuclear.central.variable_gbp_mwh | 2.3124 | Active input, reference or documented sensitivity; see curated assumptions
operating/estimates.json | nuclear.central.fuel_gbp_mwh | 9.7831 | Active input, reference or documented sensitivity; see curated assumptions
operating/estimates.json | nuclear.conservative.fixed_gbp_kw_year | 192.1051 | Recorded sensitivity; UI uses central
operating/estimates.json | nuclear.conservative.variable_gbp_mwh | 2.4903 | Recorded sensitivity; UI uses central
operating/estimates.json | nuclear.conservative.fuel_gbp_mwh | 10.7614 | Recorded sensitivity; UI uses central
operating/estimates.json | coal.fixed_gbp_kw_year | 50.8405 | Active input, reference or documented sensitivity; see curated assumptions
operating/estimates.json | coal.variable_gbp_mwh | 5.2821 | Active input, reference or documented sensitivity; see curated assumptions
operating/estimates.json | conversion.method | Source USD / annual USD per GBP * UK CPI 2024 / UK CPI source year. General inflation proxy, not an engineering cost index. | Active input, reference or documented sensitivity; see curated assumptions | Source USD / annual USD per GBP * UK CPI 2024 / UK CPI source year. General inflation proxy, not an engineering cost index.
operating/estimates.json | conversion.usd_per_gbp.2022 | 1.2371 | Active input, reference or documented sensitivity; see curated assumptions | Source USD / annual USD per GBP * UK CPI 2024 / UK CPI source year. General inflation proxy, not an engineering cost index.
operating/estimates.json | conversion.usd_per_gbp.2023 | 1.2432 | Active input, reference or documented sensitivity; see curated assumptions | Source USD / annual USD per GBP * UK CPI 2024 / UK CPI source year. General inflation proxy, not an engineering cost index.
operating/estimates.json | conversion.cpi.2022 | 121.7 | Active input, reference or documented sensitivity; see curated assumptions | Source USD / annual USD per GBP * UK CPI 2024 / UK CPI source year. General inflation proxy, not an engineering cost index.
operating/estimates.json | conversion.cpi.2023 | 130.5 | Active input, reference or documented sensitivity; see curated assumptions | Source USD / annual USD per GBP * UK CPI 2024 / UK CPI source year. General inflation proxy, not an engineering cost index.
operating/estimates.json | conversion.cpi.2024 | 133.9 | Active input, reference or documented sensitivity; see curated assumptions | Source USD / annual USD per GBP * UK CPI 2024 / UK CPI source year. General inflation proxy, not an engineering cost index.
operating/estimates.json | sources[0].url | https://inldigitallibrary.inl.gov/sites/STI/STI/Sort_107010.pdf | Active input, reference or documented sensitivity; see curated assumptions | US SMR forward estimates, not operating evidence or Rolls-Royce quote. Includes source annualised decommissioning and property-tax assumptions; no extra new-SMR decommission provision or shared-site discount.
operating/estimates.json | sources[0].reference | INL/RPT-24-77048 Rev 2, July 2024, Table 39; 2022 USD | Active input, reference or documented sensitivity; see curated assumptions | US SMR forward estimates, not operating evidence or Rolls-Royce quote. Includes source annualised decommissioning and property-tax assumptions; no extra new-SMR decommission provision or shared-site discount.
operating/estimates.json | sources[0].values | Advanced 118/2.2/10; moderate 136/2.6/11; conservative 216/2.8/12.1: fixed $/kW-year, variable and fuel $/MWh. | Active input, reference or documented sensitivity; see curated assumptions | US SMR forward estimates, not operating evidence or Rolls-Royce quote. Includes source annualised decommissioning and property-tax assumptions; no extra new-SMR decommission provision or shared-site discount.
operating/estimates.json | sources[0].scope | US SMR forward estimates, not operating evidence or Rolls-Royce quote. Includes source annualised decommissioning and property-tax assumptions; no extra new-SMR decommission provision or shared-site discount. | Active input, reference or documented sensitivity; see curated assumptions | US SMR forward estimates, not operating evidence or Rolls-Royce quote. Includes source annualised decommissioning and property-tax assumptions; no extra new-SMR decommission provision or shared-site discount.
operating/estimates.json | sources[1].url | https://www.eia.gov/analysis/studies/powerplants/capitalcost/pdf/capital_cost_AEO2025.pdf | Active input, reference or documented sensitivity; see curated assumptions | Includes maintenance; excludes property tax and insurance. Scaled linearly to the 2 GW reference station. Coal fuel and start wear remain separately modelled; no new UK quote.
operating/estimates.json | sources[1].reference | EIA/Sargent & Lundy, ultra-supercritical coal without CCS, 650 MW net; 2023 USD | Active input, reference or documented sensitivity; see curated assumptions | Includes maintenance; excludes property tax and insurance. Scaled linearly to the 2 GW reference station. Coal fuel and start wear remain separately modelled; no new UK quote.
operating/estimates.json | sources[1].values | Fixed 61.60 $/kW-year; variable nonfuel 6.40 $/MWh | Active input, reference or documented sensitivity; see curated assumptions | Includes maintenance; excludes property tax and insurance. Scaled linearly to the 2 GW reference station. Coal fuel and start wear remain separately modelled; no new UK quote.
operating/estimates.json | sources[1].scope | Includes maintenance; excludes property tax and insurance. Scaled linearly to the 2 GW reference station. Coal fuel and start wear remain separately modelled; no new UK quote. | Active input, reference or documented sensitivity; see curated assumptions | Includes maintenance; excludes property tax and insurance. Scaled linearly to the 2 GW reference station. Coal fuel and start wear remain separately modelled; no new UK quote.
operating/estimates.json | sources[2].url | https://www.federalreserve.gov/releases/g5a/20230109/ | Active input, reference or documented sensitivity; see curated assumptions
operating/estimates.json | sources[2].reference | 2022 annual USD per GBP | Active input, reference or documented sensitivity; see curated assumptions
operating/estimates.json | sources[3].url | https://www.trade-tariff.service.gov.uk/exchange_rates/view/2023-12?type=average | Active input, reference or documented sensitivity; see curated assumptions
operating/estimates.json | sources[3].reference | 2023 annual USD per GBP | Active input, reference or documented sensitivity; see curated assumptions
operating/estimates.json | sources[4].url | https://www.ons.gov.uk/economy/inflationandpriceindices/timeseries/d7bt/mm23 | Active input, reference or documented sensitivity; see curated assumptions
operating/estimates.json | sources[4].reference | Annual CPI all items, 2015=100 | Active input, reference or documented sensitivity; see curated assumptions
operating/estimates.json | methodology | Applies to user-entered new SMR and coal projects. Existing nuclear retains its original bundled allowance. New nuclear accepted output is allocated pro rata by annual nuclear capacity; no separate unit dispatch model. Central uses INL moderate. Other cases are retained as research sensitivities, not selectable UI scenarios. Historical comparison reports retain their original inputs. | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | version | 1.3-integrated-fleet | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | decision_year | 2029 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | start_year | 2030 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | end_year | 2050 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | weather_years[0] | 2018 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | weather_years[1] | 2019 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | weather_years[2] | 2020 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | weather_years[3] | 2021 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | weather_years[4] | 2022 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | weather_years[5] | 2023 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | weather_years[6] | 2024 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | milestones[0] | 2035 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | milestones[1] | 2040 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | milestones[2] | 2050 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | opening_gas_gw | 34.4879 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | opening_gas_retirement_start | 2036 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | opening_gas_retirement_end | 2050 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | opening_nuclear_gw | 3.7 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | opening_nuclear_retirement_year | 2045 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | opening_storage_gw | 27.3889 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | opening_storage_gwh | 73.8903 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | opening_storage_retirement_year | 2045 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | opening_flex_gw | 0 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | delivery.gas.lead_years | 4 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | delivery.gas.annual_limit_gw | 8 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | delivery.gas.life_years | 25 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | delivery.nuclear.lead_years | 6 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | delivery.nuclear.annual_limit_gw | 4 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | delivery.nuclear.life_years | 60 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | delivery.coal.lead_years | 6 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | delivery.coal.annual_limit_gw | 2 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | delivery.coal.life_years | 25 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | delivery.offshore.lead_years | 4 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | delivery.offshore.annual_limit_gw | 4 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | delivery.offshore.life_years | 30 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | delivery.solar.lead_years | 2 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | delivery.solar.annual_limit_gw | 5 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | delivery.solar.life_years | 30 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | delivery.storage_power.lead_years | 2 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | delivery.storage_power.annual_limit_gw | 5 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | delivery.storage_power.life_years | 15 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | delivery.storage_energy.lead_years | 2 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | delivery.storage_energy.annual_limit_gw | 60 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | delivery.storage_energy.life_years | 15 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | delivery.flex.lead_years | 2 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | delivery.flex.annual_limit_gw | 2 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | delivery.flex.life_years | 30 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | strategies.Gas and flexibility.coal_gw | 0 | Historical strategy/default; plans override where used
programme/config.json | strategies.Gas and flexibility.offshore_gw | 0 | Historical strategy/default; plans override where used
programme/config.json | strategies.Gas and flexibility.solar_gw | 0 | Historical strategy/default; plans override where used
programme/config.json | strategies.Gas and flexibility.storage_gw | 27.3889 | Historical strategy/default; plans override where used
programme/config.json | strategies.Gas and flexibility.storage_gwh | 73.8903 | Historical strategy/default; plans override where used
programme/config.json | strategies.Gas and flexibility.flex_gw | 5 | Historical strategy/default; plans override where used
programme/config.json | strategies.Coal 5 GW.coal_gw | 5 | Historical strategy/default; plans override where used
programme/config.json | strategies.Coal 5 GW.offshore_gw | 0 | Historical strategy/default; plans override where used
programme/config.json | strategies.Coal 5 GW.solar_gw | 0 | Historical strategy/default; plans override where used
programme/config.json | strategies.Coal 5 GW.storage_gw | 27.3889 | Historical strategy/default; plans override where used
programme/config.json | strategies.Coal 5 GW.storage_gwh | 73.8903 | Historical strategy/default; plans override where used
programme/config.json | strategies.Coal 5 GW.flex_gw | 5 | Historical strategy/default; plans override where used
programme/config.json | strategies.Coal 10 GW.coal_gw | 10 | Historical strategy/default; plans override where used
programme/config.json | strategies.Coal 10 GW.offshore_gw | 0 | Historical strategy/default; plans override where used
programme/config.json | strategies.Coal 10 GW.solar_gw | 0 | Historical strategy/default; plans override where used
programme/config.json | strategies.Coal 10 GW.storage_gw | 27.3889 | Historical strategy/default; plans override where used
programme/config.json | strategies.Coal 10 GW.storage_gwh | 73.8903 | Historical strategy/default; plans override where used
programme/config.json | strategies.Coal 10 GW.flex_gw | 5 | Historical strategy/default; plans override where used
programme/config.json | strategies.Additional offshore wind.coal_gw | 0 | Historical strategy/default; plans override where used
programme/config.json | strategies.Additional offshore wind.offshore_gw | 40 | Historical strategy/default; plans override where used
programme/config.json | strategies.Additional offshore wind.solar_gw | 0 | Historical strategy/default; plans override where used
programme/config.json | strategies.Additional offshore wind.storage_gw | 27.3889 | Historical strategy/default; plans override where used
programme/config.json | strategies.Additional offshore wind.storage_gwh | 73.8903 | Historical strategy/default; plans override where used
programme/config.json | strategies.Additional offshore wind.flex_gw | 5 | Historical strategy/default; plans override where used
programme/config.json | strategies.Additional wind and solar.coal_gw | 0 | Historical strategy/default; plans override where used
programme/config.json | strategies.Additional wind and solar.offshore_gw | 20 | Historical strategy/default; plans override where used
programme/config.json | strategies.Additional wind and solar.solar_gw | 40 | Historical strategy/default; plans override where used
programme/config.json | strategies.Additional wind and solar.storage_gw | 27.3889 | Historical strategy/default; plans override where used
programme/config.json | strategies.Additional wind and solar.storage_gwh | 73.8903 | Historical strategy/default; plans override where used
programme/config.json | strategies.Additional wind and solar.flex_gw | 5 | Historical strategy/default; plans override where used
programme/config.json | strategies.More storage and flexibility.coal_gw | 0 | Historical strategy/default; plans override where used
programme/config.json | strategies.More storage and flexibility.offshore_gw | 0 | Historical strategy/default; plans override where used
programme/config.json | strategies.More storage and flexibility.solar_gw | 0 | Historical strategy/default; plans override where used
programme/config.json | strategies.More storage and flexibility.storage_gw | 37.3889 | Historical strategy/default; plans override where used
programme/config.json | strategies.More storage and flexibility.storage_gwh | 193.8903 | Historical strategy/default; plans override where used
programme/config.json | strategies.More storage and flexibility.flex_gw | 10 | Historical strategy/default; plans override where used
programme/config.json | new_renewable_target_year | 2040 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | coal_target_year | 2035 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | flex_storage_target_year | 2035 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | discount_rate | 0.035 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | gas_import_share | 0.6 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | coal_import_share | 1 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | inflation_after_2024 | 0.02 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | carbon_tax_nominal_gbp_t | 10 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | stress.low_wind_multiplier | 0.8 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | stress.cold_spell_days | 14 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | stress.cold_demand_multiplier | 1.1 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | stress.cold_wind_multiplier | 0.15 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | stress.cold_solar_multiplier | 0.5 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | stress.nuclear_loss_gw | 2 | Older stress option; active suite separately fixes2GW outage
programme/config.json | stress.gas_capacity_fraction | 0.5 | Older stress option; active suite separately fixes2GW outage
programme/config.json | stress.outage_draws | 12 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | stress.outage_seed | 271828 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | stress.weather_years[0] | 2019 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | stress.weather_years[1] | 2024 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | unpriced.network |  | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | unpriced.regional_constraints |  | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | unpriced.purchased_stability |  | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | unpriced.retail |  | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | unpriced.fuel_supply_infrastructure |  | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | status.opening_fleets | Sourced physical cohorts plus separately labelled 2030 outlook residuals; estimated dates and retention recorded in results/fleet. Conditional baseline, not wholly contracted. | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | status.retirement_dates | Named nuclear boundaries and estimated retirements. Listed gas40, onshore25, offshore30, solar30, battery15 years; 2031 retention floor for old listed assets. New gas35. Unlisted renewable vintages are estimated from GB deployment history, with future residual completions spread over2027–2030. | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | status.delivery_limits | Explicit planning sensitivities, not supplier offers or evidence of achievable throughput. storage_energy annual_limit_gw is interpreted as GWh/year. | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | status.inherited_projects | Explicit opening cohort list includes HPC units, physical live renewables, outlook residuals and pumped hydro. No contract MW added to physical MW. Incremental programme spending excludes pre-opening and existing project capital. | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | status.cost_scope | Generation, storage and flexibility; omitted system costs are unknown, not zero. Comparison includes break-even headroom for differential omitted costs. | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | status.discount_rate | Analyst appraisal sensitivity, distinct from technology financing rates. | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | status.carbon | Nominal policy rate converted to real 2024 GBP at an assumed 2% annual inflation path; not legal or fiscal advice. | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | status.demand_shape | FES annual energy and published peak reconciled with explicit constant networked electrolysis; a sensitivity, not a sector forecast. Additional model flexibility may overlap the flexibility already in FES peak. | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | status.nuclear | Reference/Slower/Faster policy ramps retained. Inherited nuclear is part of targets, not added on top. Dates and reforms are conditional assumptions, not delivery probability estimates. | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | status.renewables | Inherited cohorts retire without automatic repowering; strategy additions are incremental to the surviving inherited fleet. | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | status.storage | Batteries replaced to maintain opening service; pumped hydro retained separately. Pooled dispatch at80% efficiency. More-storage strategy adds10GW/120GWh to revised opening. | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | status.other_generation | Non-CHP hydro/biomass/waste aggregate held at2030 output at existing all-in price; maintenance/renewal implicit, not a separate capital programme. CHP follows retirement estimates and retains fuel within industrial gas source. | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | status.solar_degradation | The inherited 12% yield is a 2030 fleet calibration, with 0.8% further degradation per year thereafter. It is not a first-year panel yield. New DC solar uses10.5%, a1.25DC/AC ratio and degradation from commissioning. Inherited capacity measurement basis remains uncertain; see audit. | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | demand_shape | peak_aligned | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | other_generation_by_year.2030 | 32.996 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | other_generation_by_year.2031 | 32.6663 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | other_generation_by_year.2032 | 32.6663 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | other_generation_by_year.2033 | 32.3779 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | other_generation_by_year.2034 | 32.3779 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | other_generation_by_year.2035 | 32.3779 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | other_generation_by_year.2036 | 32.3779 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | other_generation_by_year.2037 | 32.3779 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | other_generation_by_year.2038 | 32.3779 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | other_generation_by_year.2039 | 32.3779 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | other_generation_by_year.2040 | 29.0813 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | other_generation_by_year.2041 | 29.0813 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | other_generation_by_year.2042 | 29.0813 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | other_generation_by_year.2043 | 29.0813 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | other_generation_by_year.2044 | 25.642 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | other_generation_by_year.2045 | 25.642 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | other_generation_by_year.2046 | 25.642 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | other_generation_by_year.2047 | 25.642 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | other_generation_by_year.2048 | 25.642 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | other_generation_by_year.2049 | 25.642 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | other_generation_by_year.2050 | 25.642 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | chp_generation_by_year.2030 | 11.2109 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | chp_generation_by_year.2031 | 10.8813 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | chp_generation_by_year.2032 | 10.8813 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | chp_generation_by_year.2033 | 10.5928 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | chp_generation_by_year.2034 | 10.5928 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | chp_generation_by_year.2035 | 10.5928 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | chp_generation_by_year.2036 | 10.5928 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | chp_generation_by_year.2037 | 10.5928 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | chp_generation_by_year.2038 | 10.5928 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | chp_generation_by_year.2039 | 10.5928 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | chp_generation_by_year.2040 | 7.2963 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | chp_generation_by_year.2041 | 7.2963 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | chp_generation_by_year.2042 | 7.2963 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | chp_generation_by_year.2043 | 7.2963 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | chp_generation_by_year.2044 | 3.8569 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | chp_generation_by_year.2045 | 3.8569 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | chp_generation_by_year.2046 | 3.8569 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | chp_generation_by_year.2047 | 3.8569 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | chp_generation_by_year.2048 | 3.8569 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | chp_generation_by_year.2049 | 3.8569 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | chp_generation_by_year.2050 | 3.8569 | Active input, reference or documented sensitivity; see curated assumptions
programme/config.json | pumped_storage.power_gw | 2.744 | Active input, reference or documented sensitivity; see curated assumptions | Analyst replacement-cost sensitivities, not project quotes. Existing capital excluded from new-build NPV.
programme/config.json | pumped_storage.energy_gwh | 28.004 | Active input, reference or documented sensitivity; see curated assumptions | Analyst replacement-cost sensitivities, not project quotes. Existing capital excluded from new-build NPV.
programme/config.json | pumped_storage.retire_year | 2080 | Active input, reference or documented sensitivity; see curated assumptions | Analyst replacement-cost sensitivities, not project quotes. Existing capital excluded from new-build NPV.
programme/config.json | pumped_storage.capex_gbp_kw | 2500 | Active input, reference or documented sensitivity; see curated assumptions | Analyst replacement-cost sensitivities, not project quotes. Existing capital excluded from new-build NPV.
programme/config.json | pumped_storage.fixed_gbp_kw_year | 35 | Active input, reference or documented sensitivity; see curated assumptions | Analyst replacement-cost sensitivities, not project quotes. Existing capital excluded from new-build NPV.
programme/config.json | pumped_storage.wacc | 0.07 | Active input, reference or documented sensitivity; see curated assumptions | Analyst replacement-cost sensitivities, not project quotes. Existing capital excluded from new-build NPV.
programme/config.json | pumped_storage.life_years | 80 | Active input, reference or documented sensitivity; see curated assumptions | Analyst replacement-cost sensitivities, not project quotes. Existing capital excluded from new-build NPV.
programme/config.json | pumped_storage.status | Analyst replacement-cost sensitivities, not project quotes. Existing capital excluded from new-build NPV. | Active input, reference or documented sensitivity; see curated assumptions | Analyst replacement-cost sensitivities, not project quotes. Existing capital excluded from new-build NPV.
programme/config.json | pooled_storage_efficiency | 0.8 | Active input, reference or documented sensitivity; see curated assumptions
operations/config.json | version | 1.5-storage-stress | Experiment settings; active controller uses only horizon/reserve | Analyst operational/stress sensitivities; not probabilistic reliability estimates. 48-hour foresight assumes accurate residual-load forecasts within that window.
operations/config.json | storage_horizon_hours | 48 | Active input, reference or documented sensitivity; see curated assumptions | Analyst operational/stress sensitivities; not probabilistic reliability estimates. 48-hour foresight assumes accurate residual-load forecasts within that window.
operations/config.json | discretionary_reserve_fraction | 0.2 | Active input, reference or documented sensitivity; see curated assumptions | Analyst operational/stress sensitivities; not probabilistic reliability estimates. 48-hour foresight assumes accurate residual-load forecasts within that window.
operations/config.json | combined_days[0] | 14 | Experiment settings; active controller uses only horizon/reserve | Analyst operational/stress sensitivities; not probabilistic reliability estimates. 48-hour foresight assumes accurate residual-load forecasts within that window.
operations/config.json | combined_days[1] | 28 | Experiment settings; active controller uses only horizon/reserve | Analyst operational/stress sensitivities; not probabilistic reliability estimates. 48-hour foresight assumes accurate residual-load forecasts within that window.
operations/config.json | combined_gas_capacity_fraction | 0.75 | Experiment settings; active controller uses only horizon/reserve | Analyst operational/stress sensitivities; not probabilistic reliability estimates. 48-hour foresight assumes accurate residual-load forecasts within that window.
operations/config.json | combined_nuclear_loss_gw | 2 | Experiment settings; active controller uses only horizon/reserve | Analyst operational/stress sensitivities; not probabilistic reliability estimates. 48-hour foresight assumes accurate residual-load forecasts within that window.
operations/config.json | combined_weather_years[0] | 2019 | Experiment settings; active controller uses only horizon/reserve | Analyst operational/stress sensitivities; not probabilistic reliability estimates. 48-hour foresight assumes accurate residual-load forecasts within that window.
operations/config.json | combined_weather_years[1] | 2024 | Experiment settings; active controller uses only horizon/reserve | Analyst operational/stress sensitivities; not probabilistic reliability estimates. 48-hour foresight assumes accurate residual-load forecasts within that window.
operations/config.json | imports_gw | 0 | Experiment settings; active controller uses only horizon/reserve | Analyst operational/stress sensitivities; not probabilistic reliability estimates. 48-hour foresight assumes accurate residual-load forecasts within that window.
operations/config.json | status | Analyst operational/stress sensitivities; not probabilistic reliability estimates. 48-hour foresight assumes accurate residual-load forecasts within that window. | Experiment settings; active controller uses only horizon/reserve | Analyst operational/stress sensitivities; not probabilistic reliability estimates. 48-hour foresight assumes accurate residual-load forecasts within that window.
network/config.json | version | 1.9 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | sources[0].id | egl2 | Active input, reference or documented sensitivity; see curated assumptions | Approved allowance, not final outturn
network/config.json | sources[0].url | https://www.ofgem.gov.uk/sites/default/files/2024-08/EGL2_PA_Decision_Final.pdf | Active input, reference or documented sensitivity; see curated assumptions | Approved allowance, not final outturn
network/config.json | sources[0].fact | £3,449,161,471 allowance in 2018/19 prices; direct, indirect and risk; executive summary p4 | Active input, reference or documented sensitivity; see curated assumptions | Approved allowance, not final outturn
network/config.json | sources[0].status | Approved allowance, not final outturn | Active input, reference or documented sensitivity; see curated assumptions | Approved allowance, not final outturn
network/config.json | sources[1].id | egl2_capacity | Active input, reference or documented sensitivity; see curated assumptions | Project benchmark, not marginal system cost
network/config.json | sources[1].url | https://www.nationalgrid.com/media-centre/press-releases/go-ahead-uks-biggest-subsea-connection-project | Active input, reference or documented sensitivity; see curated assumptions | Project benchmark, not marginal system cost
network/config.json | sources[1].fact | 2 GW wider-transmission link; £4.3bn headline and 2018/19 regulatory-price explanation | Active input, reference or documented sensitivity; see curated assumptions | Project benchmark, not marginal system cost
network/config.json | sources[1].status | Project benchmark, not marginal system cost | Active input, reference or documented sensitivity; see curated assumptions | Project benchmark, not marginal system cost
network/config.json | sources[2].id | network_finance | Active input, reference or documented sensitivity; see curated assumptions | Published November 2024 modelling convention, not latest funding settlement
network/config.json | sources[2].url | https://www.neso.energy/document/346806/download | Active input, reference or documented sensitivity; see curated assumptions | Published November 2024 modelling convention, not latest funding settlement
network/config.json | sources[2].fact | Clean Power 2030 cost annex p9: 4.06% WACC, 45-year transmission life | Active input, reference or documented sensitivity; see curated assumptions | Published November 2024 modelling convention, not latest funding settlement
network/config.json | sources[2].status | Published November 2024 modelling convention, not latest funding settlement | Active input, reference or documented sensitivity; see curated assumptions | Published November 2024 modelling convention, not latest funding settlement
network/config.json | sources[3].id | inertia_contracts | Active input, reference or documented sensitivity; see curated assumptions | Estimated contract costs, not technology resource costs
network/config.json | sources[3].url | https://www.neso.energy/industry-information/balancing-services/stability-market/mid-term-y-1-stability-market | Active input, reference or documented sensitivity; see curated assumptions | Estimated contract costs, not technology resource costs
network/config.json | sources[3].fact | Round 1 £25.4m for 5 GVA.s, Oct2025–Sep2026; round 2 £10.3m for 7.3 GVA.s, Oct2026–Sep2027 | Active input, reference or documented sensitivity; see curated assumptions | Estimated contract costs, not technology resource costs
network/config.json | sources[3].status | Estimated contract costs, not technology resource costs | Active input, reference or documented sensitivity; see curated assumptions | Estimated contract costs, not technology resource costs
network/config.json | sources[4].id | balancing | Active input, reference or documented sensitivity; see curated assumptions | Rounded observed cash aggregates; not additive independent resource costs
network/config.json | sources[4].url | https://www.neso.energy/document/362561/download | Active input, reference or documented sensitivity; see curated assumptions | Rounded observed cash aggregates; not additive independent resource costs
network/config.json | sources[4].fact | 2024/25: total balancing £2.7bn p18; thermal constraints £1.7bn p19; stability constraint £41m p23. p25 defines turndown, replacement and imbalance components. | Active input, reference or documented sensitivity; see curated assumptions | Rounded observed cash aggregates; not additive independent resource costs
network/config.json | sources[4].status | Rounded observed cash aggregates; not additive independent resource costs | Active input, reference or documented sensitivity; see curated assumptions | Rounded observed cash aggregates; not additive independent resource costs
network/config.json | sources[5].id | deflator | Active input, reference or documented sensitivity; see curated assumptions | GDP deflator rebase; stability service-year mapping is approximate
network/config.json | sources[5].url | https://www.gov.uk/government/statistics/gdp-deflators-at-market-prices-and-money-gdp-september-2026-quarterly-national-accounts | Active input, reference or documented sensitivity; see curated assumptions | GDP deflator rebase; stability service-year mapping is approximate
network/config.json | sources[5].fact | Calendar2024 96.5672; FY2018/19 76.2884; FY2025/26 100; FY2026/27 growth2.005742% | Active input, reference or documented sensitivity; see curated assumptions | GDP deflator rebase; stability service-year mapping is approximate
network/config.json | sources[5].status | GDP deflator rebase; stability service-year mapping is approximate | Active input, reference or documented sensitivity; see curated assumptions | GDP deflator rebase; stability service-year mapping is approximate
network/config.json | benchmark.capex_bn_2018_19 | 3.4492 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | benchmark.transfer_gw | 2 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | benchmark.gdp_2018_19 | 76.2884 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | benchmark.gdp_2024 | 96.5672 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | scenarios[0].name | Light reinforcement | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | scenarios[0].wind_transfer_fraction | 0.25 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | scenarios[0].solar_transfer_fraction | 0.05 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | scenarios[0].egl2_equivalent_cost_fraction | 0.25 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | scenarios[0].wacc | 0.03 | Separate experiment/source; plan finance overridesnetworkWACC
network/config.json | scenarios[0].life | 45 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | scenarios[0].annual_om_fraction | 0.005 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | scenarios[1].name | Reference sensitivity | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | scenarios[1].wind_transfer_fraction | 0.5 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | scenarios[1].solar_transfer_fraction | 0.15 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | scenarios[1].egl2_equivalent_cost_fraction | 0.5 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | scenarios[1].wacc | 0.0406 | Separate experiment/source; plan finance overridesnetworkWACC
network/config.json | scenarios[1].life | 45 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | scenarios[1].annual_om_fraction | 0.01 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | scenarios[2].name | Heavy reinforcement | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | scenarios[2].wind_transfer_fraction | 1 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | scenarios[2].solar_transfer_fraction | 0.3 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | scenarios[2].egl2_equivalent_cost_fraction | 1 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | scenarios[2].wacc | 0.06 | Separate experiment/source; plan finance overridesnetworkWACC
network/config.json | scenarios[2].life | 45 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | scenarios[2].annual_om_fraction | 0.015 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | scenario_method | Analyst siting sensitivities: added nameplate × transfer share × EGL2 cost/GW × equivalent cost fraction. Fractions represent headroom, co-location and route scope; not a linear engineering distance law or a fitted estimate. No probability assigned. | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | inertia.latest_cost_m | 10.3 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | inertia.latest_gws | 7.3 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | inertia.earlier_cost_m | 25.4 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | inertia.earlier_gws | 5 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | inertia.latest_deflator | 102.0057 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | inertia.earlier_deflator | 100 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | inertia.additional_gws[0] | 7.3 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | inertia.additional_gws[1] | 20 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | inertia.assumption | Independent continuous external inertia, with analyst-estimated auxiliary demand of 1 MW per GWs supplied. Constant service availability is idealised; no voltage, short-circuit or dynamic stability claim. Procurement prices shown separately from physical dispatch. | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | inertia.auxiliary_mw_per_gws | 1 | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | constraint.default_efficiency_lhv | 0.58 | Separate experiment/source; plan finance overridesnetworkWACC | Worked sensitivity only. Additional network-curtailed output must exclude energy already spilled in the copperplate model. Replace one-for-one with gas; no extra starts, losses or capital counted. Do not interpret as an adequacy-tested dispatch.
network/config.json | constraint.variable_om_gbp_mwh | 5 | Separate experiment/source; plan finance overridesnetworkWACC | Worked sensitivity only. Additional network-curtailed output must exclude energy already spilled in the copperplate model. Replace one-for-one with gas; no extra starts, losses or capital counted. Do not interpret as an adequacy-tested dispatch.
network/config.json | constraint.default_turndown_payment_gbp_mwh | 50 | Separate experiment/source; plan finance overridesnetworkWACC | Worked sensitivity only. Additional network-curtailed output must exclude energy already spilled in the copperplate model. Replace one-for-one with gas; no extra starts, losses or capital counted. Do not interpret as an adequacy-tested dispatch.
network/config.json | constraint.default_replacement_offer_gbp_mwh | 100 | Separate experiment/source; plan finance overridesnetworkWACC | Worked sensitivity only. Additional network-curtailed output must exclude energy already spilled in the copperplate model. Replace one-for-one with gas; no extra starts, losses or capital counted. Do not interpret as an adequacy-tested dispatch.
network/config.json | constraint.method | Worked sensitivity only. Additional network-curtailed output must exclude energy already spilled in the copperplate model. Replace one-for-one with gas; no extra starts, losses or capital counted. Do not interpret as an adequacy-tested dispatch. | Separate experiment/source; plan finance overridesnetworkWACC | Worked sensitivity only. Additional network-curtailed output must exclude energy already spilled in the copperplate model. Replace one-for-one with gas; no extra starts, losses or capital counted. Do not interpret as an adequacy-tested dispatch.
network/config.json | boundaries[0] | Wider transmission only: local connections already in generation CAPEX excluded | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | boundaries[1] | Distribution reinforcement, electrical losses and construction sequencing remain unpriced | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | boundaries[2] | No automatic credit for grid capacity released by reduced gas fleet | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | boundaries[3] | No paid curtailment inferred from national model spill | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | boundaries[4] | No gross balancing expenditure added to physical generation costs | Active input, reference or documented sensitivity; see curated assumptions
network/config.json | boundaries[5] | Inertia procurement is a separate matched dispatch experiment | Active input, reference or documented sensitivity; see curated assumptions
policy_update/assumptions.json | version | 1.19 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | price_base | Real 2024 GBP | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | status | Editable analyst scenarios, not project bids or confidence intervals | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | coal_defaults.domestic_start | 2035 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | coal_defaults.domestic_ramp_years | 5 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | coal_defaults.domestic_mt_year | 3 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | coal_defaults.domestic_gbp_tonne | 100 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | coal_defaults.import_gbp_tonne | 100 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | coal_defaults.stock_days | 30 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | coal_price_cases[0] | 70 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | coal_price_cases[1] | 100 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | coal_price_cases[2] | 150 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | gas_deliveries_twh_day[0] | 1 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | gas_deliveries_twh_day[1] | 2 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | gas_deliveries_twh_day[2] | 3 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[0].name | Low allowance | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[0].local_connection_bn_gw | 0 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[0].other_wider_network_bn_gw | 0 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[0].coal_logistics_bn_gw | 0 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[0].storage_bn_twh | 0.15 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[0].withdrawal_bn_gw | 0.01 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[0].fuel_delivery_bn_per_twh_day | 0.1 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[0].annual_om_fraction | 0.01 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[0].stability_gws | 0 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[0].distribution_gbp_mwh_growth | 0 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[1].name | Central allowance | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[1].local_connection_bn_gw | 0.05 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[1].other_wider_network_bn_gw | 0.05 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[1].coal_logistics_bn_gw | 0.05 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[1].storage_bn_twh | 0.25 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[1].withdrawal_bn_gw | 0.02 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[1].fuel_delivery_bn_per_twh_day | 0.3 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[1].annual_om_fraction | 0.02 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[1].stability_gws | 7.3 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[1].distribution_gbp_mwh_growth | 5 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[2].name | High allowance | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[2].local_connection_bn_gw | 0.15 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[2].other_wider_network_bn_gw | 0.2 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[2].coal_logistics_bn_gw | 0.15 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[2].storage_bn_twh | 0.4 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[2].withdrawal_bn_gw | 0.04 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[2].fuel_delivery_bn_per_twh_day | 0.6 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[2].annual_om_fraction | 0.03 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[2].stability_gws | 20 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | cost_cases[2].distribution_gbp_mwh_growth | 15 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | infrastructure_life | 40 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | infrastructure_build_years | 5 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | gas_fuel_gbp_mwh | 30 | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | sources[0].url | https://en.newsroom.engie.com/news/official-opening-of-the-stublach-gas-storage-facility-a-key-asset-to-meet-uk-gas-market-needs-a8b7-314df.html | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | sources[0].fact | 2014 published Stublach project investment £500m; initial two caverns 40 million cubic metres. | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | sources[0].use | Historical cost-scale context, not present UK unit-price quote. | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | sources[1].url | https://www.engie.co.uk/gas-storage/natural-gas/ | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | sources[1].fact | Operator describes over £500m investment and 400 million cubic metres total storage capacity. | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | sources[1].use | 400 mcm × 11 GWh/mcm GCV × 0.90 LHV/GCV = 3.96 TWh LHV; historical £500m / 3.96 = £0.126bn/TWh. Selected £0.15–0.40bn/TWh range allows general cost escalation and project risk without claiming engineering rebasing or identical scope. | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | sources[2].url | https://www.neso.energy/industry-information/balancing-services/stability-market/mid-term-y-1-stability-market | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | sources[2].fact | Existing model register records £10.3m/7.3 GWs and £25.4m/5 GWs contract examples. | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | sources[2].use | Separate financial service-price proxy only, not physical resource cost, no reliability credit. Price conversion retained in network/config.json. | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | method[0] | Domestic coal grows linearly from one-fifth of 3 Mt/year in 2035 to full capacity in 2039. These are policy test assumptions; no mine, contract, reserves or production forecast is asserted. Deliveries are capped hourly and by stock headroom. Coal prices are delivered inclusive of mining, restoration and transport costs; do not also add mine capital. | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | method[1] | Local connections: zero/£50m/£150m per GW only for project rows whose connection_bn is blank. Explicit zero is respected. Broad allowances are judgement estimates, not supplier data. Existing source overlap is uncertain; zero lower case allows inclusion in source CAPEX. | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | method[2] | Wider reinforcement adds zero/£50m/£200m per GW for nuclear, gas, coal, onshore and batteries, excluding offshore/solar already covered by their separate proxy. All nameplate technologies use the same broad bands pending location. Distribution sensitivity is £0/5/15 per MWh of demand growth above 2030, with no generation-type attribution. No inherited network base is added. | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | method[3] | Coal handling/logistics outside station source scope: zero/£50m/£150m per GW. Zero tests source inclusion. Private mine investment remains embedded in delivered coal price. | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | method[4] | Gas infrastructure service equivalent: max(stock TWh × £bn/TWh, peak withdrawal GW × £bn/GW), plus delivery allowance per TWh/day. Max avoids adding two complete storage systems. Supply-allocation cases are independent, not probabilities. Default zero dedicated existing capacity credit is conservative; do not equate national storage to capacity reserved for electricity. | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | method[5] | Gas assets priced as service-equivalent requirements by year with 40-year recovery and five-year construction financing uplift. This is an annual replacement-cost screen, not a dated construction programme or proof of feasible geology, hydraulic capacity or commissioning. No automatic capacity credit is granted. | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
policy_update/assumptions.json | method[6] | Infrastructure prices and operation fractions are analyst ranges. Stability service estimates are financial overlays shown separately, never added to physical resource totals. Dynamic stability and geographic constraints remain unproved. No cheap allowance may turn a failed electricity screen into a pass. | Active input, reference or documented sensitivity; see curated assumptions | Editable analyst scenarios, not project bids or confidence intervals
presets/assumptions.json | version | 1.20 | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | as_of | 2026-10-17 | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | named_nuclear[0].id | SZC-1 | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | named_nuclear[0].name | Sizewell C unit 1 | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | named_nuclear[0].technology | nuclear | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | named_nuclear[0].capacity | 1.6 | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | named_nuclear[0].online_year | 2038 | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | named_nuclear[0].retire_year | 2098 | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | named_nuclear[0].inherited | TRUE | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | named_nuclear[1].id | SZC-2 | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | named_nuclear[1].name | Sizewell C unit 2 | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | named_nuclear[1].technology | nuclear | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | named_nuclear[1].capacity | 1.6 | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | named_nuclear[1].online_year | 2039 | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | named_nuclear[1].retire_year | 2099 | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | named_nuclear[1].inherited | TRUE | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | targets_2030.offshore | 46.5 | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | targets_2030.onshore | 28 | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | targets_2030.solar | 55.5 | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | targets_2030.battery | 25 | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | targets_2030.gas | 35 | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | reference_2035.offshore | 80.5 | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | reference_2035.onshore | 36 | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | reference_2035.solar | 66.5 | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | reference_2035.battery | 26.5 | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | reference_2035.gas | 35 | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | sources[0].url | https://www.gov.uk/government/publications/clean-power-2030-action-plan/clean-power-2030-action-plan-a-new-era-of-clean-electricity-main-report | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | sources[0].use | 2030 ambitions: offshore 43–50 GW, onshore 27–29 GW, solar 45–47 GW, batteries 23–27 GW, unabated gas 35 GW. Midpoints are scenario choices, not forecasts. | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | sources[1].url | https://www.gov.uk/government/publications/clean-power-2030-action-plan/clean-power-2030-action-plan-a-new-era-of-clean-electricity-connections-reform-annex | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | sources[1].use | April 2025 connections annex: 2035 ranges offshore 72–89 GW, onshore 35–37 GW, solar 45–69 GW, batteries 24–29 GW. The annex expressly says these are NOT a government deployment pathway or funding commitment. Footnote 10 identifies another 9–10 GW rooftop solar outside connection-impact allocations; model adds 9.5 GW to solar midpoint in both 2030 and 2035. | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | sources[2].url | https://www.gov.uk/government/publications/clean-power-2030-action-plan/clean-power-2030-action-plan-a-new-era-of-clean-electricity-technical-annex | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | sources[2].use | Gas-share metric excludes waste and non-major-producer gas CHP. This model approximates exclusions proportionately from its other-generation pool; exact major-producer CHP classification is unresolved. A 5% gas check is not certification of all official clean-power metrics. | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | sources[3].url | https://www.gov.uk/government/publications/sizewell-c-project-summary-business-case | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | sources[3].use | Sizewell C financially closed; named 3.2 GW project, generation targeted mid-to-late 2030s. Model assumes unit dates 2038 and 2039, not guaranteed dates. No generic large-reactor build option added. | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | sources[4].url | https://www.gov.uk/government/news/uk-smr-programme-at-wylfa-hitting-target-for-british-contracts | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | sources[4].use | Initial Wylfa programme: three units, about 1.4 GW. Model stages 470 MW units in 2035–2037; no further government nuclear orders assumed. | Active input, reference or documented sensitivity; see curated assumptions
presets/assumptions.json | method[0] | Both presets share the existing baseline, Hinkley dates already in that baseline, Sizewell C 2038/39 and an assumed delivery of 2030 wind/solar/battery ambitions. Additional 2030 capacity above the baseline is rounded up to whole model units, with implied project starts before 2029. These are assumed policy-pipeline additions, not verified contracted projects. They are common to both presets so a 2029 policy change does not erase work already underway. No claim that the 2030 target is secured. | Historical preset derivation; active gas top-ups and cost overrides are in release_1_26 and the six dated plans
presets/assumptions.json | method[1] | Pre-2029 orders are now explicit project rows; both presets include their construction and financing. They can be edited. The new-build schedule includes total project capital; pre-2029 and 2029-onward spending are distinguished. Shared Sizewell/Hinkley existing-project capital cash is outside incremental build spending; annual inherited nuclear costs retain the model's generic allowance, not project-specific contract settlement. | Historical preset derivation; active gas top-ups and cost overrides are in release_1_26 and the six dated plans
presets/assumptions.json | method[2] | Government preset interpolates from 2030 midpoint capacities to 2035 connections-reference midpoints. After 2035, wind/solar/battery target capacity scales with the selected preset's original Holistic Transition annual demand relative to 2035. Replacements maintain those capacities through retirements. This is an analyst continuation, NOT a published 2050 government schedule, an optimised mix, or proof that the 5% target is met. Editing demand does not silently resize orders. | Historical preset derivation; active gas top-ups and cost overrides are in release_1_26 and the six dated plans
presets/assumptions.json | method[3] | Government gas capacity is maintained at approximately 35 GW through replacement stations; extending the 2030 gas-capacity level after 2030 is an analyst assumption. The 5% annual unabated-gas-share test is extended through 2050 as requested, not represented as a published year-by-year rule. Dispatch is supply-first; excess gas use is displayed rather than silently labelled compliant. Shortages are reported separately; no artificial claim of rationing under a hard fuel budget. | Historical preset derivation; active gas top-ups and cost overrides are in release_1_26 and the six dated plans
presets/assumptions.json | method[4] | Wylfa's three SMRs are included within our existing accelerated SMR ramp, not added twice. The government preset has only those three new SMRs. Large reactor additions are limited to the named inherited Sizewell project; no repeat large-reactor option is enabled. | Historical preset derivation; active gas top-ups and cost overrides are in release_1_26 and the six dated plans
presets/assumptions.json | method[5] | Both presets use the same 4.5% real finance rate, construction unit costs, fuel assumptions, weather protocol and £10 carbon-tax scenario. This isolates generation strategy; it is not a costing of the government's actual financing arrangements, ETS or tax policy. New wind, solar and battery construction is priced on the same basis as our programme. | Historical preset derivation; active gas top-ups and cost overrides are in release_1_26 and the six dated plans
presets/assumptions.json | method[6] | Government plans also include more long-duration storage, hydrogen/gas with carbon capture, demand flexibility and interconnection. This engine retains existing pumped storage/other generation but does not implement those new resources or their full costs. New batteries are four-hour units. Zero dependable electricity imports is a common security stress, not a government import policy. Consequently shortages are conditional model results, not proof that the complete official programme is infeasible. | Historical preset derivation; active gas top-ups and cost overrides are in release_1_26 and the six dated plans
presets/assumptions.json | method[7] | The 5% proxy uses actual generated energy, excluding battery discharge to avoid double counting, and excludes a proportional share of waste and gas CHP. It uses actual dispatched renewable energy, not curtailed potential or electricity demand. Gas plus coal share is also shown so adding coal cannot manufacture a clean-power pass. Normal-year shares and synthetic-stress shares are separate. Inertia constraints may increase thermal dispatch; unmodelled independent stability services could change that requirement. | Historical preset derivation; active gas top-ups and cost overrides are in release_1_26 and the six dated plans
legacy/inputs.json | version | 1.8 | Active input, reference or documented sensitivity; see curated assumptions
legacy/inputs.json | base_year | 2024 | Active input, reference or documented sensitivity; see curated assumptions
legacy/inputs.json | period | Financial years beginning April | Active input, reference or documented sensitivity; see curated assumptions
legacy/inputs.json | ro.years[0] | 2025 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.years[1] | 2026 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.years[2] | 2027 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.years[3] | 2028 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.years[4] | 2029 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.years[5] | 2030 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.years[6] | 2031 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.years[7] | 2032 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.years[8] | 2033 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.years[9] | 2034 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.years[10] | 2035 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.years[11] | 2036 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.cpi_cost_bn_2024_25[0] | 7.9 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.cpi_cost_bn_2024_25[1] | 7.7 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.cpi_cost_bn_2024_25[2] | 5.9 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.cpi_cost_bn_2024_25[3] | 5.8 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.cpi_cost_bn_2024_25[4] | 5.5 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.cpi_cost_bn_2024_25[5] | 5.2 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.cpi_cost_bn_2024_25[6] | 4.8 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.cpi_cost_bn_2024_25[7] | 4 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.cpi_cost_bn_2024_25[8] | 3.3 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.cpi_cost_bn_2024_25[9] | 2.5 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.cpi_cost_bn_2024_25[10] | 1.9 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.cpi_cost_bn_2024_25[11] | 1.5 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.source | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.locator | Table 2, option 1 CPI; UK total, rounded to £0.1bn | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.gb_share_proxy | 0.94543 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.gb_share_method | Constant share of ROCs issued in GB in 2024/25; Ofgem RO SY23 Figure 3.2. Proxy for GB attribution, not measured annual GB scheme cost. | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | ro.gb_share_source | https://www.ofgem.gov.uk/sites/default/files/2026-03/RO_24-25_SY23_Annual_Report-20260327121336.pdf | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.years[0] | 2025 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.years[1] | 2026 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.years[2] | 2027 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.years[3] | 2028 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.years[4] | 2029 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.years[5] | 2030 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.years[6] | 2031 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.years[7] | 2032 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.years[8] | 2033 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.years[9] | 2034 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.years[10] | 2035 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.years[11] | 2036 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.cpi_cost_bn_2024_25[0] | 1.9 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.cpi_cost_bn_2024_25[1] | 1.9 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.cpi_cost_bn_2024_25[2] | 1.9 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.cpi_cost_bn_2024_25[3] | 1.9 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.cpi_cost_bn_2024_25[4] | 1.8 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.cpi_cost_bn_2024_25[5] | 1.7 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.cpi_cost_bn_2024_25[6] | 1.5 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.cpi_cost_bn_2024_25[7] | 1.4 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.cpi_cost_bn_2024_25[8] | 1.3 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.cpi_cost_bn_2024_25[9] | 1.1 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.cpi_cost_bn_2024_25[10] | 1 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.cpi_cost_bn_2024_25[11] | 0.8 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.source | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.locator | Table 1 option 1 CPI; GB, rounded to £0.1bn. Published aggregate estimate, includes export payments and scheme administration. | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.tail_zero_year | 2042 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | fit.tail_method | Analyst linear extension from 2036/37 published value to zero in 2042/43; selectable zero years 2040,2042,2044, not confidence limits. | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage
legacy/inputs.json | conversion.gdp_2024 | 96.5672 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/statistics/gdp-deflators-at-market-prices-and-money-gdp-september-2026-quarterly-national-accounts
legacy/inputs.json | conversion.gdp_2020 | 82.2004 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/statistics/gdp-deflators-at-market-prices-and-money-gdp-september-2026-quarterly-national-accounts
legacy/inputs.json | conversion.gdp_fy2024_25 | 96.757 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/statistics/gdp-deflators-at-market-prices-and-money-gdp-september-2026-quarterly-national-accounts
legacy/inputs.json | conversion.source | https://www.gov.uk/government/statistics/gdp-deflators-at-market-prices-and-money-gdp-september-2026-quarterly-national-accounts | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/statistics/gdp-deflators-at-market-prices-and-money-gdp-september-2026-quarterly-national-accounts
legacy/inputs.json | conversion.cpi_2012 | 96.1 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/statistics/gdp-deflators-at-market-prices-and-money-gdp-september-2026-quarterly-national-accounts
legacy/inputs.json | conversion.cpi_2024 | 133.9 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/statistics/gdp-deflators-at-market-prices-and-money-gdp-september-2026-quarterly-national-accounts
legacy/inputs.json | conversion.cpi_source | https://www.ons.gov.uk/economy/inflationandpriceindices/timeseries/d7bt/mm23 | Active input, reference or documented sensitivity; see curated assumptions | https://www.gov.uk/government/statistics/gdp-deflators-at-market-prices-and-money-gdp-september-2026-quarterly-national-accounts
legacy/inputs.json | reference_prices_2024[0] | 40 | Active input, reference or documented sensitivity; see curated assumptions
legacy/inputs.json | reference_prices_2024[1] | 70 | Active input, reference or documented sensitivity; see curated assumptions
legacy/inputs.json | reference_prices_2024[2] | 100 | Active input, reference or documented sensitivity; see curated assumptions
legacy/inputs.json | reference_method | Analyst flat, output-weighted reference-price scenarios in real 2024 GBP/MWh, not wholesale forecasts or dispatch optimisation. | Active input, reference or documented sensitivity; see curated assumptions
legacy/inputs.json | excluded[0] | Nuclear CfD (reported separately) | Active input, reference or documented sensitivity; see curated assumptions
legacy/inputs.json | excluded[1] | Post-CfD generation | Active input, reference or documented sensitivity; see curated assumptions
legacy/inputs.json | excluded[2] | Future unawarded AR8+ contracts | Active input, reference or documented sensitivity; see curated assumptions
legacy/inputs.json | excluded[3] | New procurement under user build plans | Active input, reference or documented sensitivity; see curated assumptions
legacy/inputs.json | excluded[4] | CfD non-generation settlement adjustments | Active input, reference or documented sensitivity; see curated assumptions
legacy/inputs.json | excluded[5] | Net value of FIT exported electricity is not deducted from gross scheme outlay | Active input, reference or documented sensitivity; see curated assumptions
legacy/inputs.json | retrieved_on | 2026-10-17 | Active input, reference or documented sensitivity; see curated assumptions
fleet/other_display.json | components[0].label | Biomass, including biomass CHP | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | components[0].twh | 7.3807 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | components[1].label | Waste, including waste CHP | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | components[1].twh | 10.5345 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | components[2].label | Conventional hydro | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | components[2].twh | 3.6224 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | components[3].label | Other renewables: marine and geothermal | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | components[3].twh | 0.24749 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[0].year | 2030 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[0].other_non_chp_twh | 21.785 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[0].chp_twh | 11.2109 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[0].other_twh | 32.996 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[1].year | 2031 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[1].other_non_chp_twh | 21.785 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[1].chp_twh | 10.8813 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[1].other_twh | 32.6663 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[2].year | 2032 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[2].other_non_chp_twh | 21.785 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[2].chp_twh | 10.8813 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[2].other_twh | 32.6663 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[3].year | 2033 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[3].other_non_chp_twh | 21.785 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[3].chp_twh | 10.5928 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[3].other_twh | 32.3779 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[4].year | 2034 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[4].other_non_chp_twh | 21.785 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[4].chp_twh | 10.5928 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[4].other_twh | 32.3779 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[5].year | 2035 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[5].other_non_chp_twh | 21.785 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[5].chp_twh | 10.5928 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[5].other_twh | 32.3779 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[6].year | 2036 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[6].other_non_chp_twh | 21.785 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[6].chp_twh | 10.5928 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[6].other_twh | 32.3779 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[7].year | 2037 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[7].other_non_chp_twh | 21.785 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[7].chp_twh | 10.5928 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[7].other_twh | 32.3779 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[8].year | 2038 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[8].other_non_chp_twh | 21.785 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[8].chp_twh | 10.5928 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[8].other_twh | 32.3779 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[9].year | 2039 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[9].other_non_chp_twh | 21.785 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[9].chp_twh | 10.5928 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[9].other_twh | 32.3779 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[10].year | 2040 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[10].other_non_chp_twh | 21.785 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[10].chp_twh | 7.2963 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[10].other_twh | 29.0813 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[11].year | 2041 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[11].other_non_chp_twh | 21.785 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[11].chp_twh | 7.2963 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[11].other_twh | 29.0813 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[12].year | 2042 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[12].other_non_chp_twh | 21.785 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[12].chp_twh | 7.2963 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[12].other_twh | 29.0813 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[13].year | 2043 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[13].other_non_chp_twh | 21.785 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[13].chp_twh | 7.2963 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[13].other_twh | 29.0813 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[14].year | 2044 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[14].other_non_chp_twh | 21.785 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[14].chp_twh | 3.8569 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[14].other_twh | 25.642 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[15].year | 2045 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[15].other_non_chp_twh | 21.785 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[15].chp_twh | 3.8569 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[15].other_twh | 25.642 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[16].year | 2046 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[16].other_non_chp_twh | 21.785 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[16].chp_twh | 3.8569 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[16].other_twh | 25.642 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[17].year | 2047 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[17].other_non_chp_twh | 21.785 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[17].chp_twh | 3.8569 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[17].other_twh | 25.642 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[18].year | 2048 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[18].other_non_chp_twh | 21.785 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[18].chp_twh | 3.8569 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[18].other_twh | 25.642 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[19].year | 2049 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[19].other_non_chp_twh | 21.785 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[19].chp_twh | 3.8569 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[19].other_twh | 25.642 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[20].year | 2050 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[20].other_non_chp_twh | 21.785 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[20].chp_twh | 3.8569 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | annual[20].other_twh | 25.642 | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
fleet/other_display.json | source | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv | Active input, reference or documented sensitivity; see curated assumptions | data/evidence/tyo2026_es1.csv; results/fleet/other_generation.csv
planner/data.json | finance_rate | 0.045 | Resolved new-project default
planner/data.json | planning_years | 1 | Resolved new-project default
planner/data.json | solar_dc_ac_ratio | 1.25 | Resolved new-project default
planner/data.json | technologies.nuclear.label | Nuclear | Resolved new-project default | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.
planner/data.json | technologies.nuclear.unit_gw | 0.47 | Resolved new-project default | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.
planner/data.json | technologies.nuclear.lead | 5 | Resolved new-project default | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.
planner/data.json | technologies.nuclear.life | 60 | Resolved new-project default | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.
planner/data.json | technologies.nuclear.recovery | 60 | Resolved new-project default | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.
planner/data.json | technologies.nuclear.annual_limit_gw | 4 | Resolved new-project default | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.
planner/data.json | technologies.nuclear.capex_bn_per_gw.low | 3.8298 | Resolved new-project default | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.
planner/data.json | technologies.nuclear.capex_bn_per_gw.central | 3.8298 | Resolved new-project default | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.
planner/data.json | technologies.nuclear.capex_bn_per_gw.high | 4.5951 | Resolved new-project default | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.
planner/data.json | technologies.nuclear.fixed_bn_per_gw_year | 0.12096 | Resolved new-project default | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.
planner/data.json | technologies.nuclear.source | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections. | Resolved new-project default | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.
planner/data.json | technologies.nuclear.potential_fraction | 0.9 | Resolved new-project default | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.
planner/data.json | technologies.nuclear.cost_status | Policy assumption; construction scope unverified | Resolved new-project default | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.
planner/data.json | technologies.nuclear.capacity_basis | Manufacturer nameplate; export basis to confirm | Resolved new-project default | Retains the agreed £1.8bn. Treating this as 2024 pounds is a model convention, not an updated supplier quotation. The 2021 release did not specify a price base or separate planning, financing and connections.
planner/data.json | technologies.gas.label | Gas station | Resolved new-project default | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.
planner/data.json | technologies.gas.unit_gw | 0.92 | Resolved new-project default | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.
planner/data.json | technologies.gas.lead | 4 | Resolved new-project default | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.
planner/data.json | technologies.gas.life | 35 | Resolved new-project default | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.
planner/data.json | technologies.gas.recovery | 35 | Resolved new-project default | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.
planner/data.json | technologies.gas.annual_limit_gw | 8 | Resolved new-project default | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.
planner/data.json | technologies.gas.capex_bn_per_gw.low | 0.68062 | Resolved new-project default | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.
planner/data.json | technologies.gas.capex_bn_per_gw.central | 0.95344 | Resolved new-project default | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.
planner/data.json | technologies.gas.capex_bn_per_gw.high | 0.95344 | Resolved new-project default | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.
planner/data.json | technologies.gas.fixed_bn_per_gw_year | 0.0185 | Resolved new-project default | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.
planner/data.json | technologies.gas.source | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption. | Resolved new-project default | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.
planner/data.json | technologies.gas.potential_fraction | 0.9 | Resolved new-project default | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.
planner/data.json | technologies.gas.cost_status | Recent EPC proxy; associated infrastructure not fully separated | Resolved new-project default | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.
planner/data.json | technologies.gas.capacity_basis | Net export; assumed 2.5% auxiliary load | Resolved new-project default | PLN6,378m EPC for two 668 MW gross units, July 2025, excluding VAT. Separate maintenance contract excluded. Engineering, procurement and construction (EPC) includes associated infrastructure: external-connection content remains unquantified. Auxiliary load is an analyst assumption.
planner/data.json | technologies.coal.label | Coal station | Resolved new-project default | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.
planner/data.json | technologies.coal.unit_gw | 2 | Resolved new-project default | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.
planner/data.json | technologies.coal.lead | 6 | Resolved new-project default | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.
planner/data.json | technologies.coal.life | 50 | Resolved new-project default | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.
planner/data.json | technologies.coal.recovery | 50 | Resolved new-project default | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.
planner/data.json | technologies.coal.annual_limit_gw | 2 | Resolved new-project default | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.
planner/data.json | technologies.coal.capex_bn_per_gw.low | 1.3754 | Resolved new-project default | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.
planner/data.json | technologies.coal.capex_bn_per_gw.central | 1.3754 | Resolved new-project default | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.
planner/data.json | technologies.coal.capex_bn_per_gw.high | 3.1188 | Resolved new-project default | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.
planner/data.json | technologies.coal.fixed_bn_per_gw_year | 0.05084 | Resolved new-project default | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.
planner/data.json | technologies.coal.source | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine. | Resolved new-project default | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.
planner/data.json | technologies.coal.potential_fraction | 0.85 | Resolved new-project default | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.
planner/data.json | technologies.coal.cost_status | Older European contract proxy; high UK transfer uncertainty | Resolved new-project default | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.
planner/data.json | technologies.coal.capacity_basis | Net export; assumed 7% auxiliary load | Resolved new-project default | PLN5,100m contract excluding VAT for 1,075 MW gross, September 2012. Contract-date NBP exchange rate. Existing-site reference; no quantified UK greenfield/site premium. Auxiliary load is an analyst assumption. This is a multi-unit station-sized scaling, not a proposed 2 GW turbine.
planner/data.json | technologies.offshore.label | Offshore wind | Resolved new-project default | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.
planner/data.json | technologies.offshore.unit_gw | 1 | Resolved new-project default | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.
planner/data.json | technologies.offshore.lead | 4 | Resolved new-project default | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.
planner/data.json | technologies.offshore.life | 30 | Resolved new-project default | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.
planner/data.json | technologies.offshore.recovery | 30 | Resolved new-project default | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.
planner/data.json | technologies.offshore.annual_limit_gw | 4 | Resolved new-project default | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.
planner/data.json | technologies.offshore.capex_bn_per_gw.low | 2.1 | Resolved new-project default | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.
planner/data.json | technologies.offshore.capex_bn_per_gw.central | 2.5 | Resolved new-project default | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.
planner/data.json | technologies.offshore.capex_bn_per_gw.high | 3.1 | Resolved new-project default | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.
planner/data.json | technologies.offshore.fixed_bn_per_gw_year | 0.0549 | Resolved new-project default | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.
planner/data.json | technologies.offshore.source | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total. | Resolved new-project default | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.
planner/data.json | technologies.offshore.potential_fraction | 0.48 | Resolved new-project default | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.
planner/data.json | technologies.offshore.cost_status | DESNZ construction category; 2024 real GBP; pre-development excluded | Resolved new-project default | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.
planner/data.json | technologies.offshore.capacity_basis | Rated turbine capacity | Resolved new-project default | DESNZ 2025 Annex A, Technical and Cost Assumptions: 2030 fixed offshore wind construction is £2,500/kW in 2024 prices. Separate £170/kW pre-development is excluded, consistent with the common planning account. Use-of-system charges are excluded. Offshore electrical/transmission boundary is not fully reconciled with the separate network allowance; the latter remains an overlay, not a verified additive total.
planner/data.json | technologies.onshore.label | Onshore wind | Resolved new-project default | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.
planner/data.json | technologies.onshore.unit_gw | 0.1 | Resolved new-project default | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.
planner/data.json | technologies.onshore.lead | 2 | Resolved new-project default | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.
planner/data.json | technologies.onshore.life | 25 | Resolved new-project default | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.
planner/data.json | technologies.onshore.recovery | 25 | Resolved new-project default | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.
planner/data.json | technologies.onshore.annual_limit_gw | 3 | Resolved new-project default | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.
planner/data.json | technologies.onshore.capex_bn_per_gw.low | 0.98809 | Resolved new-project default | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.
planner/data.json | technologies.onshore.capex_bn_per_gw.central | 1.2354 | Resolved new-project default | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.
planner/data.json | technologies.onshore.capex_bn_per_gw.high | 1.6448 | Resolved new-project default | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.
planner/data.json | technologies.onshore.fixed_bn_per_gw_year | 0.0222 | Resolved new-project default | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.
planner/data.json | technologies.onshore.source | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate. | Resolved new-project default | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.
planner/data.json | technologies.onshore.potential_fraction | 0.36 | Resolved new-project default | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.
planner/data.json | technologies.onshore.cost_status | UK construction category, separated from infrastructure and development | Resolved new-project default | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.
planner/data.json | technologies.onshore.capacity_basis | Rated turbine capacity | Resolved new-project default | Arup construction category includes turbines and construction contingency. Infrastructure and pre-development remain separate.
planner/data.json | technologies.solar.label | Solar panels (DC) | Resolved new-project default | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.
planner/data.json | technologies.solar.unit_gw | 0.1 | Resolved new-project default | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.
planner/data.json | technologies.solar.lead | 2 | Resolved new-project default | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.
planner/data.json | technologies.solar.life | 30 | Resolved new-project default | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.
planner/data.json | technologies.solar.recovery | 30 | Resolved new-project default | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.
planner/data.json | technologies.solar.annual_limit_gw | 5 | Resolved new-project default | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.
planner/data.json | technologies.solar.capex_bn_per_gw.low | 0.43402 | Resolved new-project default | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.
planner/data.json | technologies.solar.capex_bn_per_gw.central | 0.5356 | Resolved new-project default | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.
planner/data.json | technologies.solar.capex_bn_per_gw.high | 0.61666 | Resolved new-project default | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.
planner/data.json | technologies.solar.fixed_bn_per_gw_year | 0.0075 | Resolved new-project default | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.
planner/data.json | technologies.solar.source | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed. | Resolved new-project default | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.
planner/data.json | technologies.solar.potential_fraction | 0.105 | Resolved new-project default | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.
planner/data.json | technologies.solar.cost_status | UK construction category, separated from infrastructure and development | Resolved new-project default | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.
planner/data.json | technologies.solar.capacity_basis | DC panel capacity, NOT 100 MW AC export | Resolved new-project default | Includes panels, mounts, inverters, cabling and construction contingency. Infrastructure and pre-development excluded. New-build dispatch uses DC nameplate with a1.25 DC/AC ratio; inherited measurement basis is separately disclosed.
planner/data.json | technologies.battery.label | Battery storage | Resolved new-project default | Existing storage assumptions: battery power and energy priced separately; no distinct low/high cost evidence supplied.
planner/data.json | technologies.battery.unit_gw | 1 | Resolved new-project default | Existing storage assumptions: battery power and energy priced separately; no distinct low/high cost evidence supplied.
planner/data.json | technologies.battery.unit_gwh | 4 | Resolved new-project default | Existing storage assumptions: battery power and energy priced separately; no distinct low/high cost evidence supplied.
planner/data.json | technologies.battery.lead | 2 | Resolved new-project default | Existing storage assumptions: battery power and energy priced separately; no distinct low/high cost evidence supplied.
planner/data.json | technologies.battery.life | 15 | Resolved new-project default | Existing storage assumptions: battery power and energy priced separately; no distinct low/high cost evidence supplied.
planner/data.json | technologies.battery.recovery | 15 | Resolved new-project default | Existing storage assumptions: battery power and energy priced separately; no distinct low/high cost evidence supplied.
planner/data.json | technologies.battery.annual_limit_gw | 5 | Resolved new-project default | Existing storage assumptions: battery power and energy priced separately; no distinct low/high cost evidence supplied.
planner/data.json | technologies.battery.annual_limit_gwh | 60 | Resolved new-project default | Existing storage assumptions: battery power and energy priced separately; no distinct low/high cost evidence supplied.
planner/data.json | technologies.battery.capex_bn_per_gw.low | 0.2 | Resolved new-project default | Existing storage assumptions: battery power and energy priced separately; no distinct low/high cost evidence supplied.
planner/data.json | technologies.battery.capex_bn_per_gw.central | 0.2 | Resolved new-project default | Existing storage assumptions: battery power and energy priced separately; no distinct low/high cost evidence supplied.
planner/data.json | technologies.battery.capex_bn_per_gw.high | 0.2 | Resolved new-project default | Existing storage assumptions: battery power and energy priced separately; no distinct low/high cost evidence supplied.
planner/data.json | technologies.battery.capex_bn_per_gwh | 0.15 | Resolved new-project default | Existing storage assumptions: battery power and energy priced separately; no distinct low/high cost evidence supplied.
planner/data.json | technologies.battery.fixed_bn_per_gw_year | 0.01 | Resolved new-project default | Existing storage assumptions: battery power and energy priced separately; no distinct low/high cost evidence supplied.
planner/data.json | technologies.battery.source | Existing storage assumptions: battery power and energy priced separately; no distinct low/high cost evidence supplied. | Resolved new-project default | Existing storage assumptions: battery power and energy priced separately; no distinct low/high cost evidence supplied.
programme/demand_shape.py | Algorithm constants / rules M05 | Raise positive historical demand shape to an exponent; normalise to annual non-electrolysis energy; solve exponent to published peak. Add annual electrolysis / replay hours as flat demand. | Active hard-coded method | Historical timing, future peak and flat electrolysis are approximations. Seven8760/8784-hour calendars reused; not sector forecasts or price-responsive demand.
programme/engine.py; planner/security_protocol.py | Algorithm constants / rules M09 | Available output = dated nuclear capacity × clip(0.90 +0.04 cos(2πt/N),0,1); synthetic outage deducts2GW for28days, floored at zero. | Active hard-coded method | Smooth seasonal availability, not unit outage probabilities. Curtailment allowed. Multiunit outage correlation and delivery probabilities not estimated.
operations/thermal.py; model.py | Algorithm constants / rules M10 | Derate fleet90%; split into0.5GW representative blocks and final fraction. Commit with start/ramp lookahead and minimum up/down times; dispatch blocks sequentially. | Active hard-coded method | Perfect demand/availability foresight within horizon. Constant derating, not explicit forced-outage process. Initial units already committed; no artificial national cold start.
operations/storage.py; programme/engine.py | Algorithm constants / rules M13 | ηcharge=ηdischarge=√0.80; SOCnext=SOC+ηcharge×charge−discharge/ηdischarge.48h forecast need and20% discretionary reserve; repair infeasible charging monotonically. | Active hard-coded method | Batteries and pumped hydro pooled; empty at start of each replay year; no carryover or degradation trajectory. Maintenance/replacement assumptions replace detailed cell ageing.
model.py; programme/engine.py; trade/dispatch.py | Algorithm constants / rules M14 | Accepted nuclear+renewables+other+coal+gas+imports+battery discharge+unserved = demand+charging+exports. Track curtailed generation separately. | Active hard-coded method | Copperplate GB. Curtail VRE then nuclear,other,coal,gas. Thermal fuel remains charged for forced output subsequently dumped.
planner/security_protocol.py | Algorithm constants / rules M16 | Per model year:7 normal historical shapes2018–24 plus28-day cold-calm and2GW nuclear outage on2019,2024. Pass if unserved≤1MWh and zero reserve/inertia shortfall hours. | Active hard-coded method | Zero-import autonomy tests. No probability attached. Gas physical deliverability assessed separately; passing electricity screens does not prove fuel security.
trade/dispatch.py | Algorithm constants / rules M18 | Imports≤residual and available capacity×(1−loss); schedule if sending-end price/(1−loss)<gas full-load fuel+variable O&M. Rescue actual shortage from unused capacity. Export otherwise-curtailed VRE then nuclear. | Active hard-coded method | Exogenous foreign prices and availability. No simultaneous importing/exporting. No induced European prices,cable-specific outages or optimal storage arbitrage.
demand_plans/build.py; demand_plans/METHODS.md | Algorithm constants / rules M30 | Our low/high nuclear target scales central nuclear by demand ratio, constrained2/4/6/8SMRs/year; gas sized by discrete adequacy search and delivery ceilings. Government low/high scalescentral capacitytargets, retaining inherited orders. | Active hard-coded method | Saved orders frozen for this audit; no reoptimisation. Government continuation beyond2030 is analyst-defined and omits proposed hydrogen,CCS,LDES/flexibility. Costs do not compare equal reliability.
operations/peaker_assumptions.json | peaker.version | 1 | string | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.price_basis | Real 2024 GBP; borrowing costs calculated separately at the common plan rate. | string | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.source | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf | string | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.source_name | DESNZ / CEPA / GHD unabated gas cost study, published January 2026 | string | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.label | Open-cycle gas turbine | string | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.unit_gw | 0.3 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.equipment_modules | 1 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.lead | 3 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.life | 30 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.recovery | 30 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.annual_limit_gw | 3.6 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.capex_bn_per_gw.low | 0.45 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.capex_bn_per_gw.central | 0.95 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.capex_bn_per_gw.high | 1.45 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.fixed_bn_per_gw_year | 0.01529 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.potential_fraction | 0.95 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.availability | 0.95 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.dispatch_unit_gw | 0.3 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.efficiency_full_lhv | 0.389 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.efficiency_at_min_load_lhv | 0.3 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.min_load_fraction | 0.25 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.min_up_hours | 1 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.min_down_hours | 1 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.start_lead_hours | 1 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.ramp_fraction_per_hour | 1 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.inertia_seconds | 5 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.start_fuel_mwh_per_mw | 0.2 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.start_wear_gbp_per_mw | 0 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.variable_gbp_mwh | 4.76 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.cost_status | Survey range with heterogeneous connection scope; midpoint, not a supplier bid. | string | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.capacity_basis | Net site capacity rounded from the report's 299 MW reference. | string | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_ocgt.source | Sections 3.3 and 5.1.3. Survey construction range £450–1,450/kW; central is midpoint. Embedded gas/electric connection content cannot be separated and is retained, not deducted speculatively. Separate new planning and wider-grid allowances remain excluded unless entered. Fixed £11.49/kW/year plus 0.4% of central construction cost for insurance; variable £4.76/MWh includes an assumed cycling regime, so no additional start-wear charge is added. Efficiency/availability are report references. One-year planning plus two-year construction is the reformed lead. Part-load efficiency, hourly start/ramp/minimum-load/inertia/start-fuel parameters and delivery cap are explicit analyst assumptions, not supplier warranties. | string | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.label | Gas-engine site (5 × 20 MW) | string | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.unit_gw | 0.1 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.equipment_modules | 5 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.lead | 2 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.life | 30 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.recovery | 30 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.annual_limit_gw | 4 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.capex_bn_per_gw.low | 0.55 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.capex_bn_per_gw.central | 0.65 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.capex_bn_per_gw.high | 0.75 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.fixed_bn_per_gw_year | 0.01723 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.potential_fraction | 0.95 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.availability | 0.95 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.dispatch_unit_gw | 0.1 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.efficiency_full_lhv | 0.446 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.efficiency_at_min_load_lhv | 0.4 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.min_load_fraction | 0.15 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.min_up_hours | 1 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.min_down_hours | 1 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.start_lead_hours | 0 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.ramp_fraction_per_hour | 1 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.inertia_seconds | 2.5 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.start_fuel_mwh_per_mw | 0.03 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.start_wear_gbp_per_mw | 0 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.variable_gbp_mwh | 6.73 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.cost_status | Favourably connected-site survey midpoint; transfer to new sites is uncertain. | string | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.capacity_basis | Analyst 100 MW site grouping of five 20 MW reference engines; dispatch uses grouped sites, not independent engine outages. | string | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.technologies.gas_engine.source | Sections 3.5 and 5.1.4. Construction survey £550–750/kW, midpoint £650/kW, excluding contingency; nearby/existing connection scope remains embedded and unquantified. Fixed £14.63/kW/year plus 0.4% of central construction cost insurance; £6.73/MWh variable from the conservative 500-hour case, no extra start-wear charge. 44.6% efficiency and 95% availability are source references, not the best achievable manufacturer design. One-year construction plus one-year reformed planning is an analyst delivery case. Zero whole-hour start delay approximates a few-minute engine start; sub-hour security is not certified. Other operational parameters, 30-year life/recovery, site grouping and annual delivery cap are analyst assumptions. | string | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.procurement.earliest_order | 2029 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.procurement.ccgt_stations_per_year | 4 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.procurement.aggregate_gas_gw_per_year | 7.36 | number | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf
operations/peaker_assumptions.json | peaker.procurement.meaning | Candidate procurement envelope, not confirmed factory allocations. CCGT limited to four 920 MW stations annually; OCGT and engine limits are separate, with a shared 7.36 GW annual commissioning envelope. Compare original schedules separately; no pre-2029 discretionary orders. Equipment lead times and UK allocation require tender evidence. | string | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf

## Sources
Sources and verification status
Primary sources, retained snapshots and model references. Verification states distinguish inputs rechecked during this audit from held references. Snapshot hashes and source files are included in the model ZIP; retrieval date is 18 October 2026 for new checks.
ID | Use | URL | Files | Verification | Locator
S001 | demand_2022.csv | https://api.neso.energy/dataset/8f2fe0af-871c-488d-8bad-960426f24601/resource/bb44a1b5-75b1-4db2-8491-257f23385006/download/demanddata_2022.csv | data/raw/demand_2022.csv | Snapshot retained; byte hashes checked where manifest supplies a hash
S002 | demand_2023.csv | https://api.neso.energy/dataset/8f2fe0af-871c-488d-8bad-960426f24601/resource/bf5ab335-9b40-4ea4-b93a-ab4af7bce003/download/demanddata_2023.csv | data/raw/demand_2023.csv | Snapshot retained; byte hashes checked where manifest supplies a hash
S003 | demand_2024.csv | https://api.neso.energy/dataset/8f2fe0af-871c-488d-8bad-960426f24601/resource/f6d02c0f-957b-48cb-82ee-09003f2ba759/download/demanddata_2024.csv | data/raw/demand_2024.csv | Snapshot retained; byte hashes checked where manifest supplies a hash
S004 | generation.csv | https://api.neso.energy/dataset/88313ae5-94e4-4ddc-a790-593554d8c6b9/resource/f93d1835-75bc-43e5-84ad-12472b180a98/download/df_fuel_ckan.csv | data/raw/generation.csv | Snapshot retained; byte hashes checked where manifest supplies a hash
S005 | desnz_costs_2025.xlsx | https://assets.publishing.service.gov.uk/media/69d8efec96c86b7513170229/annex-a-additional-estimates-and-key-assumptions-2025.xlsx | data/raw/desnz_costs_2025.xlsx | Snapshot retained; byte hashes checked where manifest supplies a hash
S006 | Annual demand input | https://api.neso.energy/dataset/2c15c755-d8fe-4229-9169-3b6dd7c88fec/resource/300c07b9-baeb-4411-bc40-987cbb4aec0b/download/fes2025_ed1_v006.csv | data/raw/fes2025_ed1.csv | Snapshot retained; byte hashes checked where manifest supplies a hash
S007 | Accounting definition / cross-check; not a substituted fleet forecast | https://api.neso.energy/dataset/2c15c755-d8fe-4229-9169-3b6dd7c88fec/resource/93761974-17f5-43da-a690-71faaab610a5/download/fes2025_ed2_v004.pdf | data/raw/fes2025_ed2.pdf | Snapshot retained; byte hashes checked where manifest supplies a hash
S008 | Accounting definition / cross-check; not a substituted fleet forecast | https://api.neso.energy/dataset/549b0667-b533-4748-95bd-f6e13933a47d/resource/6c78a777-b885-4bb6-bc35-8100f9e137a2/download/fes2025_es1_v006.csv | data/raw/fes2025_es1.csv | Snapshot retained; byte hashes checked where manifest supplies a hash
S009 | data/evidence/dukes_stations.xlsx | https://assets.publishing.service.gov.uk/media/6a6a365b0ddb7e4831c629f3/DUKES_5.11.xlsx | data/evidence/dukes_stations.xlsx | Snapshot retained; byte hashes checked where manifest supplies a hash
S010 | data/evidence/dukes_storage.xlsx | https://assets.publishing.service.gov.uk/media/6a6a36a0bf4a7aca8f8976c6/DUKES_5.16.xlsx | data/evidence/dukes_storage.xlsx | Snapshot retained; byte hashes checked where manifest supplies a hash
S011 | data/evidence/dukes_interconnectors.xlsx | https://assets.publishing.service.gov.uk/media/6a6a3675bf4a7aca8f8976c3/DUKES_5.13.xlsx | data/evidence/dukes_interconnectors.xlsx | Snapshot retained; byte hashes checked where manifest supplies a hash
S012 | data/evidence/repd.csv | https://assets.publishing.service.gov.uk/media/6a6cbdc00c36759b5ccaa305/REPD_Publication_Q2_2026.csv | data/evidence/repd.csv | Snapshot retained; byte hashes checked where manifest supplies a hash
S013 | data/evidence/tyo 2026_es 1.csv | https://api.neso.energy/dataset/549b0667-b533-4748-95bd-f6e13933a47d/resource/b3bf8ac0-d27a-447c-975c-208ae92c0fa5/download/10yo2026_es1_v001.csv | data/evidence/tyo2026_es1.csv | Snapshot retained; byte hashes checked where manifest supplies a hash
S014 | data/evidence/cfd_datastore.json | https://dp.lowcarboncontracts.uk/api/3/action/datastore_search?resource_id=fdaf09d2-8cff-4799-a5b0-1c59444e492b&limit=5000 | data/evidence/cfd_datastore.json | Snapshot retained; byte hashes checked where manifest supplies a hash
S015 | data/raw/demand_2018.csv | https://api.neso.energy/dataset/8f2fe0af-871c-488d-8bad-960426f24601/resource/fcb12133-0db0-4f27-a4a5-1669fd9f6d33/download/demanddata_2018.csv | data/raw/demand_2018.csv | Snapshot retained; byte hashes checked where manifest supplies a hash
S016 | data/raw/demand_2019.csv | https://api.neso.energy/dataset/8f2fe0af-871c-488d-8bad-960426f24601/resource/dd9de980-d724-415a-b344-d8ae11321432/download/demanddata_2019.csv | data/raw/demand_2019.csv | Snapshot retained; byte hashes checked where manifest supplies a hash
S017 | data/raw/demand_2020.csv | https://api.neso.energy/dataset/8f2fe0af-871c-488d-8bad-960426f24601/resource/33ba6857-2a55-479f-9308-e5c4c53d4381/download/demanddata_2020.csv | data/raw/demand_2020.csv | Snapshot retained; byte hashes checked where manifest supplies a hash
S018 | data/raw/demand_2021.csv | https://api.neso.energy/dataset/8f2fe0af-871c-488d-8bad-960426f24601/resource/18c69c42-f20d-46f0-84e9-e279045befc6/download/demanddata_2021.csv | data/raw/demand_2021.csv | Snapshot retained; byte hashes checked where manifest supplies a hash
S019 | legacy/sources/api_manifest.json | https://dp.lowcarboncontracts.uk/api/3/action/datastore_search?resource_id=fdaf09d2-8cff-4799-a5b0-1c59444e492b&limit=10000 | legacy/sources | Snapshot retained; byte hashes checked where manifest supplies a hash
S020 | legacy/sources/api_manifest.json | https://dp.lowcarboncontracts.uk/api/3/action/datastore_search?resource_id=79ed671c-6cb2-40d6-aed8-6eddf21b9ce4&limit=10000 | legacy/sources | Snapshot retained; byte hashes checked where manifest supplies a hash
S021 | legacy/sources/api_manifest.json | https://dp.lowcarboncontracts.uk/api/3/action/datastore_search?resource_id=098ef836-a47c-4710-b9ec-22a2175c65d9&limit=10000 | legacy/sources | Snapshot retained; byte hashes checked where manifest supplies a hash
S022 | legacy/sources/api_manifest.json | https://dp.lowcarboncontracts.uk/api/3/action/datastore_search?resource_id=55bd2d1e-d25d-4980-8569-ea27f6ec7217&limit=10000 | legacy/sources | Snapshot retained; byte hashes checked where manifest supplies a hash
S023 | Construction / ons | https://www.ons.gov.uk/economy/inflationandpriceindices/timeseries/d7bt/mm23 | construction/estimates.json; operating; legacy/inputs.json | Held source/reference; no fresh full-source revalidation | ons
S024 | Construction / fx 2023 | https://www.trade-tariff.service.gov.uk/exchange_rates/view/2023-12?type=average | construction/estimates.json; operating | Held source/reference; no fresh full-source revalidation | fx 2023
S025 | Construction / fx 2025 | https://www.trade-tariff.service.gov.uk/exchange_rates/view/2025-12?type=average | construction/estimates.json | Held source/reference; no fresh full-source revalidation | fx 2025
S026 | Construction / fx 2012 | https://api.nbp.pl/api/exchangerates/rates/a/gbp/2012-09-21/?format=json | construction/estimates.json | Held source/reference; no fresh full-source revalidation | fx 2012
S027 | Construction / gas | https://ir.enea.pl/pr/855237/podpisanie-umowy-na-budowe-blokow-gazowo-parowych | construction/estimates.json | Primary source reopened 18 October 2026; quoted input checked; future outturn remains uncertain | gas
S028 | Construction / coal | https://ir.enea.pl/pr/290738/zawarcie-przez-enea-wytwarzanie-s-a-umowy-na-budowe-bloku-energetycznego | construction/estimates.json | Held source/reference; no fresh full-source revalidation | coal
S029 | Construction / eia | https://www.eia.gov/analysis/studies/powerplants/capitalcost/pdf/capital_cost_AEO2025.pdf | construction/estimates.json; operating | Held source/reference; no fresh full-source revalidation | eia
S030 | Construction / arup | https://assets.publishing.service.gov.uk/media/68ba91f411b4ded2da19fe92/onshore-wind-and-solar-pv-cost-electricity-report-update-2024.pdf | construction/estimates.json | Primary source reopened 18 October 2026; quoted input checked; future outturn remains uncertain | arup
S031 | Construction / offshore | https://doggerbank.com/construction/dogger-bank-c-reaches-financial-close/ | construction/estimates.json | Primary source reopened 18 October 2026; quoted input checked; future outturn remains uncertain | offshore
S032 | Construction / smr | https://www.rolls-royce.com/media/press-releases/2021/17-05-2021-more-power-and-updated-design-revealed-as-nuclear-power-team-targets-first-place.aspx | construction/estimates.json | Primary source reopened 18 October 2026; quoted input checked; future outturn remains uncertain | smr
S033 | Construction / desnz 2025 | https://www.gov.uk/government/publications/electricity-generation-costs-2025 | construction/estimates.json | Held source/reference; no fresh full-source revalidation | desnz 2025
S034 | Operating: INL/RPT-24-77048 Rev 2, July 2024, Table 39; 2022 USD | https://inldigitallibrary.inl.gov/sites/STI/STI/Sort_107010.pdf | operating | Primary source reopened 18 October 2026; quoted input checked; future outturn remains uncertain | INL/RPT-24-77048 Rev 2, July 2024, Table 39; 2022 USD
S035 | Operating: 2022 annual USD per GBP | https://www.federalreserve.gov/releases/g5a/20230109/ | operating | Held source/reference; no fresh full-source revalidation | 2022 annual USD per GBP
S036 | Lifecycle: Four-year on-site repeat-unit construction; one-year planning is policy assumption. | https://www.rolls-royce-smr.com/our-approach | lifecycle | Held source/reference; no fresh full-source revalidation
S037 | Lifecycle: Historical UK systems: approximately 0.8% annual degradation; extrapolation to future utility-scale equipment is an assumption. | https://oa.upm.es/43685/ | lifecycle | Held source/reference; no fresh full-source revalidation
S038 | Lifecycle: UK study of 3000 installations, silicon degradation approximately 0.81–0.94% annually. | https://eprints.whiterose.ac.uk/id/eprint/177737/ | lifecycle | Held source/reference; no fresh full-source revalidation
S039 | Lifecycle: Inverter replacement at 15 years precedent; does not establish our cost fraction. | https://atb-archive.nrel.gov/electricity/2019/index.html?m=1&s=omcfmdpr&t=insusrsccn | lifecycle | Held source/reference; no fresh full-source revalidation
S040 | Networks: £3,449,161,471 allowance in 2018/19 prices; direct, indirect and risk; executive summary p 4 | https://www.ofgem.gov.uk/sites/default/files/2024-08/EGL2_PA_Decision_Final.pdf | networks | Held source/reference; no fresh full-source revalidation
S041 | Networks: 2 GW wider-transmission link; £4.3 bn headline and 2018/19 regulatory-price explanation | https://www.nationalgrid.com/media-centre/press-releases/go-ahead-uks-biggest-subsea-connection-project | networks | Held source/reference; no fresh full-source revalidation
S042 | Networks: Clean Power 2030 cost annex p 9: 4.06% WACC, 45-year transmission life | https://www.neso.energy/document/346806/download | networks | Held source/reference; no fresh full-source revalidation
S043 | Networks: Round 1 £25.4 m for 5 GVA.s, Oct 2025–Sep 2026; round 2 £10.3 m for 7.3 GVA.s, Oct 2026–Sep 2027 | https://www.neso.energy/industry-information/balancing-services/stability-market/mid-term-y-1-stability-market | networks; infrastructure | Held source/reference; no fresh full-source revalidation
S044 | Networks: 2024/25: total balancing £2.7 bn p 18; thermal constraints £1.7 bn p 19; stability constraint £41 m p 23. p 25 defines turndown, replacement and imbalance components. | https://www.neso.energy/document/362561/download | networks | Held source/reference; no fresh full-source revalidation
S045 | Networks: Calendar 2024 96.5672; FY 2018/19 76.2884; FY 2025/26 100; FY 2026/27 growth 2.005742% | https://www.gov.uk/government/statistics/gdp-deflators-at-market-prices-and-money-gdp-september-2026-quarterly-national-accounts | networks; legacy/inputs.json | Held source/reference; no fresh full-source revalidation
S046 | Infrastructure: Historical cost-scale context, not present UK unit-price quote. | https://en.newsroom.engie.com/news/official-opening-of-the-stublach-gas-storage-facility-a-key-asset-to-meet-uk-gas-market-needs-a8b7-314df.html | infrastructure | Held source/reference; no fresh full-source revalidation
S047 | Infrastructure: 400 mcm × 11 GWh/mcm GCV × 0.90 LHV/GCV = 3.96 TWh LHV; historical £500 m / 3.96 = £0.126 bn/TWh. Selected £0.15–0.40 bn/TWh range allows general cost escalation and project risk without claiming engineering rebasing or identical scope. | https://www.engie.co.uk/gas-storage/natural-gas/ | infrastructure | Held source/reference; no fresh full-source revalidation
S048 | Presets: 2030 ambitions: offshore 43–50 GW, onshore 27–29 GW, solar 45–47 GW, batteries 23–27 GW, unabated gas 35 GW. Midpoints are scenario choices, not forecasts. | https://www.gov.uk/government/publications/clean-power-2030-action-plan/clean-power-2030-action-plan-a-new-era-of-clean-electricity-main-report | presets | Held source/reference; no fresh full-source revalidation
S049 | Presets: April 2025 connections annex: 2035 ranges offshore 72–89 GW, onshore 35–37 GW, solar 45–69 GW, batteries 24–29 GW. The annex expressly says these are NOT a government deployment pathway or funding commitment. Footnote 10 identifies another 9–10 GW rooftop solar outside connection-impact allocations; model adds 9.5 GW to solar midpoint in both 2030 and 2035. | https://www.gov.uk/government/publications/clean-power-2030-action-plan/clean-power-2030-action-plan-a-new-era-of-clean-electricity-connections-reform-annex | presets | Held source/reference; no fresh full-source revalidation
S050 | Presets: Gas-share metric excludes waste and non-major-producer gas CHP. This model approximates exclusions proportionately from its other-generation pool; exact major-producer CHP classification is unresolved. A 5% gas check is not certification of all official clean-power metrics. | https://www.gov.uk/government/publications/clean-power-2030-action-plan/clean-power-2030-action-plan-a-new-era-of-clean-electricity-technical-annex | presets | Held source/reference; no fresh full-source revalidation
S051 | Presets: Sizewell C financially closed; named 3.2 GW project, generation targeted mid-to-late 2030 s. Model assumes unit dates 2038 and 2039, not guaranteed dates. No generic large-reactor build option added. | https://www.gov.uk/government/publications/sizewell-c-project-summary-business-case | presets | Held source/reference; no fresh full-source revalidation
S052 | Presets: Initial Wylfa programme: three units, about 1.4 GW. Model stages 470 MW units in 2035–2037; no further government nuclear orders assumed. | https://www.gov.uk/government/news/uk-smr-programme-at-wylfa-hitting-target-for-british-contracts | presets | Held source/reference; no fresh full-source revalidation
S053 | GB monthly solar deployment; June 2026 stock and annual history | https://assets.publishing.service.gov.uk/media/6aba729a734e2435f202f19e/ET_6.3_SOLAR_PV_SEP_26.xlsx | audit/sources/solar_deployment.xlsx | Downloaded 18 October 2026; extracted figures and reconciliation checked
S054 | England+Scotland+Wales quarterly wind capacity; June 2026 and historical 4 th quarters | https://assets.publishing.service.gov.uk/media/6aba724dfceb6fb3a65012d2/ET_6.1_SEP_26.xlsx | audit/sources/et61.xlsx | Downloaded 18 October 2026; extracted figures and reconciliation checked
S055 | July 2026 Sizewell B extension:2055, conditional contract/approvals | https://www.gov.uk/government/news/sizewell-b-power-plant-given-lifetime-extension-to-2055 | programme/config.json; trade/METHODS.md | Primary source checked 18 October 2026
S056 | EDF July 2026:£800 m refurbishment, proposed£70.50/MWh 2025 price CfD 2035–55 | https://www.edfenergy.com/media-centre/milestone-moment-sizewell-b-life-extension-agreement | programme/config.json; trade/METHODS.md | Primary source checked 18 October 2026
S057 | AGR extensions toMarch 2030 | https://www.edfenergy.com/media-centre/uk-energy-security-supported-further-nuclear-power-station-life-extensions | programme/config.json; trade/METHODS.md | Primary reference retained
S058 | 10.3 GW interconnection benchmark | https://www.gov.uk/government/publications/clean-flexibility-roadmap/clean-flexibility-roadmap | programme/config.json; trade/METHODS.md | Primary reference retained
S059 | coal_assumptions.json | https://www.eia.gov/outlooks/aeo/assumptions/pdf/table_8.2.pdf | coal_assumptions.json | Held source/reference; no fresh full-source revalidation
S060 | coal_assumptions.json | https://assets.publishing.service.gov.uk/media/6a6a1c5724593dd070ba47cc/DUKES_2026_Chapter_2.pdf | coal_assumptions.json | Held source/reference; no fresh full-source revalidation
S061 | programme/config.json | https://www.gov.uk/government/publications/desnz-annual-report-and-accounts-2025-to-2026/financial-statements | programme/config.json | Held source/reference; no fresh full-source revalidation
S062 | programme/config.json | https://www.scottishpower.com/documents/d/guest/SPUK_2025_Annual_Accounts | programme/config.json; audit/physical_corrections.json | Held source/reference; no fresh full-source revalidation
S063 | legacy/inputs.json | https://www.gov.uk/government/consultations/renewables-obligation-ro-scheme-indexation-changes/outcome/renewables-obligation-ro-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage | legacy/inputs.json | Held source/reference; no fresh full-source revalidation
S064 | legacy/inputs.json | https://www.ofgem.gov.uk/sites/default/files/2026-03/RO_24-25_SY23_Annual_Report-20260327121336.pdf | legacy/inputs.json | Held source/reference; no fresh full-source revalidation
S065 | legacy/inputs.json | https://www.gov.uk/government/consultations/feed-in-tariffs-fit-scheme-indexation-changes/outcome/feed-in-tariffs-fit-scheme-final-consultation-analytical-annex-impact-of-indexation-options-accessible-webpage | legacy/inputs.json | Held source/reference; no fresh full-source revalidation
S066 | results/security/gas_source_tables.json | https://www.ssethermal.com/energy-storage/aldbrough/ | results/security/gas_source_tables.json | Held source/reference; no fresh full-source revalidation
S067 | results/security/gas_source_tables.json | https://www.scottishpower.com/userfiles/file/Hatfield-Site-Information-2014.pdf | results/security/gas_source_tables.json | Held source/reference; no fresh full-source revalidation
S068 | results/security/gas_source_tables.json | https://kistosplc.com/operations/hill-top-and-hole-house-uk/ | results/security/gas_source_tables.json | Held source/reference; no fresh full-source revalidation
S069 | results/security/gas_source_tables.json | https://www.uniper.energy/united-kingdom/power-plants-in-the-united-kingdom/holford | results/security/gas_source_tables.json | Held source/reference; no fresh full-source revalidation
S070 | results/security/gas_source_tables.json | https://www.ssethermal.com/energy-storage/atwick/ | results/security/gas_source_tables.json | Held source/reference; no fresh full-source revalidation
S071 | results/security/gas_source_tables.json | https://www.humblyenergy.co.uk/ | results/security/gas_source_tables.json | Held source/reference; no fresh full-source revalidation
S072 | results/security/gas_source_tables.json | https://www.centrica.com/our-businesses/upstream/centrica-energy-storage-limited-cesplus/ | results/security/gas_source_tables.json | Held source/reference; no fresh full-source revalidation
S073 | results/security/gas_source_tables.json | https://www.storengy.co.uk/storengy-uk-stublach-site | results/security/gas_source_tables.json | Held source/reference; no fresh full-source revalidation
S074 | results/security/gas_source_tables.json | https://www.fluxys.com/en/about-us/interconnector-uk | results/security/gas_source_tables.json | Held source/reference; no fresh full-source revalidation
S075 | results/security/gas_source_tables.json | https://www.bblcompany.com/about-bbl | results/security/gas_source_tables.json | Held source/reference; no fresh full-source revalidation
S076 | results/security/gas_source_tables.json | https://www.nationalgrid.com/national-grid-ventures/grain-lng/operational-information | results/security/gas_source_tables.json | Held source/reference; no fresh full-source revalidation
S077 | results/security/gas_source_tables.json | https://www.southhooklng.com/about/commercial/ | results/security/gas_source_tables.json | Held source/reference; no fresh full-source revalidation
S078 | results/security/gas_source_tables.json | https://www.dragonlng.co.uk/2029capacity | results/security/gas_source_tables.json | Held source/reference; no fresh full-source revalidation
S079 | results/security/gas_source_tables.json | https://www.norskpetroleum.no/en/production-and-exports/the-oil-and-gas-pipeline-system/ | results/security/gas_source_tables.json | Held source/reference; no fresh full-source revalidation
S080 | Great Eppleton: old turbines removed, 8.2 MW replacement | https://uk.rwe.com/locations/great-eppleton-onshore-wind-farm/ | audit/physical_corrections.json | Primary source checked 18 October 2026
S081 | Harlock Hill: five old turbines decommissioned January 2016 | https://bwect.org.uk/baywind/ | audit/physical_corrections.json | Primary source checked 18 October 2026
S082 | Coal Clough: 9.6 MW old turbines replaced with 16 MW | https://www.scottishpowerrenewables.com/onshore/england/wind/coal_clough | audit/physical_corrections.json | Primary source checked 18 October 2026
S083 | Minety: separate 50 MW units, not duplicate project entries | https://eclipsepower.co.uk/minety-battery-storage/ | audit/physical_corrections.json | Primary source checked 18 October 2026
S084 | Buxton: developer confirms 30 MW total | https://www.linkedin.com/posts/atlantic-green-uk_we-are-proud-to-announce-that-our-buxton-activity-7217182118177566721-OUQu | audit/physical_corrections.json | Primary source checked 18 October 2026
DESIGN-GAS | Modern combined-cycle gas design benchmark: Keadby 2, Siemens/SSE, announced 2018 | https://press.siemens.com/global/en/pressrelease/siemens-will-deliver-one-worlds-most-efficient-combined-cycle-power-plants-uk | planner/reference_units.json | Published plant design benchmark, applied to the standard 920 MW reference unit. Engineering proxy, not a guaranteed efficiency for the separate Enea EPC construction-cost proxy. Applied on the model's lower-heating-value fuel-price convention. Actual project acceptance must use matching fuel and efficiency measurement bases. | 5 June 2018 release: combined-cycle power station design efficiency 63%
DESIGN-COAL | Kozienice unit 11 design benchmark, Enea, 2014 | https://media.enea.pl/pr/289964/na-budowie-nowego-bloku-energetycznego-w-kozienicach-postawiono-pierwsza-kolumne-kotla | planner/reference_units.json | Published net design efficiency for the coal construction reference, scaled to the standard 2 GW station. O&M remains the separately documented EIA proxy. Applied on the model's lower-heating-value coal heat-content convention; the press release identifies net efficiency but does not state calorific basis. Matching that basis is an explicit reference-table convention. | 12 June 2014 release: design net efficiency 45.6%
EPR2-COST | Six-reactor French programme: €72.8bn in 2020 prices; first Penly reactor targeted 2038; construction finance described separately. | https://www.edf.fr/en/the-edf-group/dedicated-sections/journalists/all-press-releases/edf-shares-its-forecasted-cost-estimate-of-the-epr2-programme-for-eu728bn | planner/large_nuclear.json; demand_plans/ours_*.plan.json | Primary EDF publication checked 19 October 2026. Transfer to one UK reactor, seven-year build and cost conversion are explicit estimates. | 18 December 2025 release
EPR2-TECH | Slide 30: three pairs of 1.7 GW EPR2 reactors; task force aims to reduce construction to 70 months. Slide 32: Sizewell C construction estimate £38bn in 2024 prices, providing £19bn per reactor high comparator. | https://www.edf.fr/sites/groupe/files/2026-02/annual-results-edf-2025-presentation-2026-02-20.pdf | planner/large_nuclear.json; demand_plans/ours_*.plan.json | Primary EDF publication checked 19 October 2026. Transfer to one UK reactor, seven-year build and cost conversion are explicit estimates. | 2025 annual results presentation, 20 February 2026: slides 30 and 32
WYLFA-DATES | First operational Wylfa SMRs targeted from the mid-2030s; no published annual sequence in this answer. | https://questions-statements.parliament.uk/written-questions/detail/2025-11-18/HL12084/ | demand_plans/*.plan.json; planner/programmes.json | Primary parliamentary answer checked 19 October 2026. All-three commissioning in 2035 is an analyst assumption. | Lord Vallance, answer 2 December 2025, HL12084
ELECTRO-FES | Electrolysis expected to operate at lower load factors using electricity at high renewable generation; annual electrical demand from existing ED1 snapshot. | https://www.neso.energy/document/364541/download | data/raw/fes2025_ed1.csv; electrolysis/METHODS.md | Primary FES 2025 report checked 19 October 2026; capacity/window/buffer are separate analyst assumptions. | FES 2025 pp.58–59; ED1 Networked Electrolysis annual GWh
ELECTRO-DESNZ | Technical and commercial flexibility, end-user continuity and hydrogen storage constraints. | https://www.gov.uk/government/calls-for-evidence/flexibility-in-electrolytic-hydrogen-production-and-use | electrolysis/METHODS.md | Primary DESNZ call for evidence checked 19 October 2026; no quantitative default inferred. | 2026 call for evidence; supply and end-user questions
PEAKER-DESNZ | OCGT and engine capital, efficiency, availability, O&M and construction reference ranges. | https://assets.publishing.service.gov.uk/media/696616c68d599f4c09e1ffae/unabated-gas-electricity-generation-costs-2025.pdf | operations/peaker_assumptions.json; operations/mixed_gas.py | Primary report checked 19 October 2026. Survey scopes vary; numerical central values and operational estimates explicitly separated. | Sections 3.3, 3.5, 5.1.3 and 5.1.4; tables 3.12, 3.15, 3.24, 3.27, 5.3, 5.4
PEAKER-BRIGG | Existing UK modular-engine project and fast-start technical example. | https://www.wartsila.com/media/news/28-05-2024-wartsila-power-plant-will-provide-critical-grid-balancing-as-uk-expands-its-renewable-energy-supply-3453414 | operations/peaker_assumptions.json | Manufacturer project release; four engines, 48 MW and as little as 2.5 minutes to full output. Does not validate our site size, costs or national delivery envelope. | 28 May 2024, Brigg/Centrica project
PEAKER-GE | Evidence of global equipment backlog and advance slot reservations, not proof of UK delivery quantities. | https://www.gevernova.com/news/articles/ge-vernova-releases-second-quarter-2026-financial-results | peaker_study/METHODS.md | Primary July 2026 release: 116 GW gas equipment backlog plus slot reservations. Procurement caps in the model remain assumptions. | Second-quarter 2026 highlights
RETENTION-DESNZ | Five-year refurbishment cost and engineering inspection requirements | https://www.gov.uk/government/publications/electricity-generation-cost-study-extending-the-life-of-existing-generation-assets | operations/life_extension_assumptions.json | Primary commissioned CEPA/GHD study. Modern1700MW archetype; transfer to ageing inherited fleet is explicitly estimated. | May2025 sections2.3–2.4
RETENTION-SSE | Existing fleet retention is an operator investment option | https://www.sse.com/media/pizorw4m/sse-plc_prospectus-2026-final.pdf | operations/life_extension_assumptions.json | Primary operator prospectus2026. No blanket age50 guarantee. | SSE Thermal programmes
PROCUREMENT-WARTSILA | Expanding engine capacity and extending lead times | https://www.wartsila.com/investors/blog/post/highlights-from-the-ceo-strategy-call-q2-2026 | retention_study/METHODS.md | Primary June2026 update:65% planned technical capacity increase; not a UK equipment allocation. | Production capacity expansion and customer commitments

## Legacy support
Legacy renewable-support calculation inputs
Financial settlements are separate from physical resource costs and physical project capacity. CfD reference-price sensitivities retain signed repayments. This ledger ends in 2049/50 and excludes nuclear support and unawarded rounds.
financial year | round | technology | connection | generation twh | strike 2024 gbp mwh | contract value bn | scope | price method
2026/27 | Allocation Round 1 | Offshore Wind | Transmission | 3.5832 | 191.8387 | 0.6874 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2026/27 | Allocation Round 2 | Offshore Wind | Transmission | 8.057 | 73.7529 | 0.59423 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2026/27 | Allocation Round 3 | Offshore Wind | Transmission | 5.4249 | 62.4811 | 0.33895 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2026/27 | Allocation Round 4 | Offshore Wind | Transmission | 0.0049 | 52.0413 | 0.000255 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2026/27 | Investment Contract | Offshore Wind | Transmission | 10.0657 | 144.8197 | 1.4577 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2026/27 | Allocation Round 5 | Geothermal | Distribution | 0.0236 | 165.8075 | 0.0039131 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2026/27 | Allocation Round 1 | Energy from Waste | Distribution | 0.1393 | 130.7763 | 0.018217 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2026/27 | Allocation Round 1 | Onshore Wind | Distribution | 0.7264 | 119.3594 | 0.086703 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2026/27 | Allocation Round 1 | Onshore Wind | Transmission | 0.6413 | 133.3124 | 0.085493 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2026/27 | Allocation Round 4 | Onshore Wind | Transmission | 0.0773 | 59.1752 | 0.0045742 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2026/27 | Allocation Round 5 | Onshore Wind | Distribution | 0.0533 | 72.8578 | 0.0038833 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2026/27 | Allocation Round 5 | Onshore Wind | Transmission | 0.1247 | 72.8578 | 0.0090854 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2026/27 | Allocation Round 6 | Onshore Wind | Distribution | 0.0684 | 70.921 | 0.004851 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2026/27 | Allocation Round 6 | Onshore Wind | Transmission | 0.2374 | 70.921 | 0.016837 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2026/27 | Allocation Round 7 | Onshore Wind | Transmission | 0.0917 | 72.24 | 0.0066244 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2026/27 | Investment Contract | Biomass Conversion | Distribution | 2.3392 | 170.5777 | 0.39902 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2026/27 | Investment Contract | Biomass Conversion | Transmission | 4.0814 | 162.3073 | 0.66244 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2026/27 | Allocation Round 5 | Tidal Stream | Distribution | 0.0014 | 275.8814 | 0.00038623 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2026/27 | Allocation Round 4 | Tidal Stream | Distribution | 0.001 | 248.767 | 0.00024877 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2026/27 | Investment Contract | Dedicated Biomass | Transmission | 1.6367 | 203.9414 | 0.33379 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2026/27 | Allocation Round 1 | Advanced Conversion Technology | Distribution | 0.0762 | 195.9882 | 0.014934 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2026/27 | Allocation Round 4 | Remote Island Wind | Transmission | 0.0021 | 64.6371 | 0.00013574 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2026/27 | Allocation Round 4 | Solar PV | Distribution | 1.0313 | 64.0797 | 0.066085 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2026/27 | Allocation Round 7 | Solar PV | Distribution | 0.009 | 65.23 | 0.00058707 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2026/27 | Allocation Round 6 | Solar PV | Distribution | 0.3239 | 69.7645 | 0.022597 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2026/27 | Allocation Round 5 | Solar PV | Transmission | 0.0141 | 65.487 | 0.00092337 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2026/27 | Allocation Round 1 | Solar PV | Distribution | 0.0193 | 13.2162 | 0.00025507 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2026/27 | Allocation Round 5 | Solar PV | Distribution | 0.1916 | 65.487 | 0.012547 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2026/27 | Allocation Round 4 | Solar PV | Transmission | 0.0997 | 64.0797 | 0.0063887 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2027/28 | Allocation Round 1 | Advanced Conversion Technology | Distribution | 0.0918 | 195.9882 | 0.017992 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2027/28 | Allocation Round 5 | Geothermal | Distribution | 0.0732 | 165.8075 | 0.012137 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2027/28 | Allocation Round 1 | Offshore Wind | Transmission | 4.2759 | 191.8387 | 0.82028 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2027/28 | Allocation Round 2 | Offshore Wind | Transmission | 9.6522 | 73.7529 | 0.71188 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2027/28 | Allocation Round 3 | Offshore Wind | Transmission | 13.8162 | 62.6039 | 0.86495 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2027/28 | Allocation Round 4 | Offshore Wind | Transmission | 2.9813 | 52.0413 | 0.15515 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2027/28 | Allocation Round 6 | Offshore Wind | Transmission | 2.4149 | 79.9608 | 0.1931 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2027/28 | Investment Contract | Offshore Wind | Transmission | 12.0229 | 144.8197 | 1.7412 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2027/28 | Investment Contract | Dedicated Biomass | Transmission | 1.9705 | 203.9414 | 0.40187 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2027/28 | Allocation Round 1 | Energy from Waste | Distribution | 0.1677 | 130.7763 | 0.021931 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2027/28 | Allocation Round 1 | Onshore Wind | Distribution | 0.878 | 119.3594 | 0.1048 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2027/28 | Allocation Round 1 | Onshore Wind | Transmission | 0.7861 | 133.3124 | 0.1048 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2027/28 | Allocation Round 4 | Onshore Wind | Transmission | 1.3393 | 59.1752 | 0.079253 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2027/28 | Allocation Round 5 | Onshore Wind | Distribution | 0.2781 | 72.8578 | 0.020262 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2027/28 | Allocation Round 5 | Onshore Wind | Transmission | 0.5213 | 72.8578 | 0.037981 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2027/28 | Allocation Round 6 | Onshore Wind | Distribution | 0.354 | 70.921 | 0.025106 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2027/28 | Allocation Round 6 | Onshore Wind | Transmission | 0.4925 | 70.921 | 0.034929 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2027/28 | Allocation Round 7 | Onshore Wind | Distribution | 0.0451 | 72.24 | 0.003258 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2027/28 | Allocation Round 7 | Onshore Wind | Transmission | 0.3801 | 72.24 | 0.027458 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2027/28 | Allocation Round 5 | Tidal Stream | Transmission | 0.0001 | 275.8814 | 2.7588e-05 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2027/28 | Allocation Round 4 | Tidal Stream | Distribution | 0.0426 | 248.767 | 0.010597 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2027/28 | Allocation Round 5 | Tidal Stream | Distribution | 0.0203 | 275.8814 | 0.0056004 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2027/28 | Allocation Round 4 | Remote Island Wind | Transmission | 0.7508 | 64.6371 | 0.04853 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2027/28 | Allocation Round 5 | Remote Island Wind | Transmission | 0.0021 | 72.8578 | 0.000153 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2027/28 | Allocation Round 1 | Solar PV | Distribution | 0.0265 | 13.2162 | 0.00035023 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2027/28 | Allocation Round 7 | Solar PV | Transmission | 0.0106 | 65.23 | 0.00069144 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2027/28 | Allocation Round 4 | Solar PV | Distribution | 1.6612 | 64.0797 | 0.10645 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2027/28 | Allocation Round 6 | Solar PV | Transmission | 0.0325 | 69.7645 | 0.0022673 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2027/28 | Allocation Round 5 | Solar PV | Distribution | 0.503 | 65.487 | 0.03294 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2027/28 | Allocation Round 4 | Solar PV | Transmission | 0.2161 | 64.0797 | 0.013848 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2027/28 | Allocation Round 6 | Solar PV | Distribution | 1.2084 | 69.7645 | 0.084303 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2027/28 | Allocation Round 7 | Solar PV | Distribution | 0.3351 | 65.23 | 0.021859 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2027/28 | Allocation Round 5 | Solar PV | Transmission | 0.1292 | 65.487 | 0.0084609 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Allocation Round 7 | Solar PV | Distribution | 1.9981 | 65.23 | 0.13034 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Allocation Round 6 | Solar PV | Distribution | 2.8791 | 69.7645 | 0.20086 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Allocation Round 1 | Solar PV | Distribution | 0.0265 | 13.2162 | 0.00035023 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2028/29 | Allocation Round 5 | Solar PV | Distribution | 1.5222 | 65.487 | 0.099684 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Allocation Round 6 | Solar PV | Transmission | 0.545 | 69.7645 | 0.038022 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Allocation Round 5 | Solar PV | Transmission | 0.2669 | 65.487 | 0.017478 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Allocation Round 4 | Solar PV | Distribution | 1.746 | 64.0797 | 0.11188 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Allocation Round 4 | Solar PV | Transmission | 0.2227 | 64.0797 | 0.014271 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Allocation Round 7 | Solar PV | Transmission | 0.1003 | 65.23 | 0.0065426 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Allocation Round 1 | Energy from Waste | Distribution | 0.1673 | 130.7763 | 0.021879 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2028/29 | Allocation Round 1 | Onshore Wind | Distribution | 0.8756 | 119.3594 | 0.10451 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2028/29 | Allocation Round 1 | Onshore Wind | Transmission | 0.7838 | 133.3124 | 0.10449 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2028/29 | Allocation Round 4 | Onshore Wind | Transmission | 1.4505 | 59.1752 | 0.085834 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Allocation Round 5 | Onshore Wind | Distribution | 0.5032 | 72.8578 | 0.036662 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Allocation Round 5 | Onshore Wind | Transmission | 1.851 | 72.8578 | 0.13486 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Allocation Round 6 | Onshore Wind | Distribution | 0.5533 | 70.921 | 0.039241 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Allocation Round 6 | Onshore Wind | Transmission | 1.2325 | 70.921 | 0.08741 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Allocation Round 7 | Onshore Wind | Distribution | 0.4206 | 72.24 | 0.030384 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Allocation Round 7 | Onshore Wind | Transmission | 0.9934 | 72.24 | 0.071763 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Allocation Round 1 | Advanced Conversion Technology | Distribution | 0.0915 | 195.9882 | 0.017933 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2028/29 | Investment Contract | Dedicated Biomass | Transmission | 1.9651 | 203.9414 | 0.40077 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2028/29 | Allocation Round 1 | Offshore Wind | Transmission | 4.2635 | 191.8387 | 0.8179 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2028/29 | Allocation Round 2 | Offshore Wind | Transmission | 9.6239 | 73.7529 | 0.70979 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2028/29 | Allocation Round 3 | Offshore Wind | Transmission | 18.7256 | 62.6494 | 1.1731 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2028/29 | Allocation Round 4 | Offshore Wind | Transmission | 10.203 | 52.0413 | 0.53098 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Allocation Round 6 | Offshore Wind | Transmission | 6.4863 | 79.9608 | 0.51865 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Allocation Round 7 | Offshore Wind | Transmission | 0.8486 | 90.9138 | 0.077149 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Investment Contract | Offshore Wind | Transmission | 11.9899 | 144.8197 | 1.7364 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2028/29 | Allocation Round 5 | Geothermal | Distribution | 0.0922 | 165.8075 | 0.015287 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Allocation Round 3 | Remote Island Wind | Transmission | 0.0953 | 60.9592 | 0.0058094 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2028/29 | Allocation Round 4 | Remote Island Wind | Distribution | 0.0607 | 64.6371 | 0.0039235 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Allocation Round 4 | Remote Island Wind | Transmission | 0.7487 | 64.6371 | 0.048394 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Allocation Round 5 | Remote Island Wind | Transmission | 0.7609 | 72.8578 | 0.055437 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Allocation Round 5 | Tidal Stream | Distribution | 0.044 | 275.8814 | 0.012139 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Allocation Round 7 | Tidal Stream | Transmission | 0.0049 | 265 | 0.0012985 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Allocation Round 4 | Tidal Stream | Distribution | 0.0425 | 248.767 | 0.010573 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Allocation Round 6 | Tidal Stream | Distribution | 0.0008 | 239.6545 | 0.00019172 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Allocation Round 5 | Tidal Stream | Transmission | 0.0489 | 275.8814 | 0.013491 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2028/29 | Allocation Round 6 | Tidal Stream | Transmission | 0.0301 | 239.6545 | 0.0072136 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Allocation Round 4 | Solar PV | Distribution | 1.7464 | 64.0797 | 0.11191 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Allocation Round 4 | Solar PV | Transmission | 0.2856 | 64.0797 | 0.018301 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Allocation Round 6 | Solar PV | Distribution | 2.9745 | 69.7645 | 0.20751 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Allocation Round 5 | Solar PV | Distribution | 1.5574 | 65.487 | 0.10199 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Allocation Round 7 | Solar PV | Distribution | 4.0433 | 65.23 | 0.26374 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Allocation Round 5 | Solar PV | Transmission | 0.3454 | 65.487 | 0.022619 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Allocation Round 7 | Solar PV | Transmission | 0.2934 | 65.23 | 0.019138 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Allocation Round 6 | Solar PV | Transmission | 0.6418 | 69.7645 | 0.044775 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Allocation Round 1 | Solar PV | Distribution | 0.0265 | 13.2162 | 0.00035023 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2029/30 | Allocation Round 1 | Energy from Waste | Distribution | 0.1673 | 130.7763 | 0.021879 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2029/30 | Allocation Round 1 | Onshore Wind | Distribution | 0.8756 | 119.3594 | 0.10451 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2029/30 | Allocation Round 1 | Onshore Wind | Transmission | 0.7838 | 133.3124 | 0.10449 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2029/30 | Allocation Round 4 | Onshore Wind | Transmission | 1.4505 | 59.1752 | 0.085834 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Allocation Round 5 | Onshore Wind | Distribution | 0.6226 | 72.8578 | 0.045361 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Allocation Round 5 | Onshore Wind | Transmission | 2.2332 | 72.8578 | 0.16271 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Allocation Round 6 | Onshore Wind | Distribution | 0.6437 | 70.921 | 0.045652 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Allocation Round 6 | Onshore Wind | Transmission | 1.788 | 70.921 | 0.12681 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Allocation Round 7 | Onshore Wind | Distribution | 0.8234 | 72.24 | 0.059482 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Allocation Round 7 | Onshore Wind | Transmission | 1.8444 | 72.24 | 0.13324 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Investment Contract | Dedicated Biomass | Transmission | 1.9651 | 203.9414 | 0.40077 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2029/30 | Allocation Round 1 | Advanced Conversion Technology | Distribution | 0.0915 | 195.9882 | 0.017933 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2029/30 | Allocation Round 6 | Floating Offshore Wind | Transmission | 0.7136 | 194.9701 | 0.13913 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Allocation Round 3 | Remote Island Wind | Transmission | 0.125 | 60.9592 | 0.0076199 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2029/30 | Allocation Round 4 | Remote Island Wind | Distribution | 0.1012 | 64.6371 | 0.0065413 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Allocation Round 4 | Remote Island Wind | Transmission | 0.7487 | 64.6371 | 0.048394 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Allocation Round 5 | Remote Island Wind | Transmission | 0.7609 | 72.8578 | 0.055437 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Allocation Round 5 | Geothermal | Distribution | 0.0922 | 165.8075 | 0.015287 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Allocation Round 1 | Offshore Wind | Transmission | 4.2635 | 191.8387 | 0.8179 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2029/30 | Allocation Round 2 | Offshore Wind | Transmission | 9.6239 | 73.7529 | 0.70979 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2029/30 | Allocation Round 3 | Offshore Wind | Transmission | 18.9864 | 62.6494 | 1.1895 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2029/30 | Allocation Round 4 | Offshore Wind | Transmission | 14.8866 | 52.0413 | 0.77472 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Allocation Round 6 | Offshore Wind | Transmission | 8.9633 | 79.9608 | 0.71671 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Allocation Round 7 | Offshore Wind | Transmission | 5.7447 | 90.9138 | 0.52227 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Investment Contract | Offshore Wind | Transmission | 11.9899 | 144.8197 | 1.7364 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2029/30 | Allocation Round 5 | Tidal Stream | Transmission | 0.0489 | 275.8814 | 0.013491 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Allocation Round 4 | Tidal Stream | Distribution | 0.0425 | 248.767 | 0.010573 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Allocation Round 6 | Tidal Stream | Distribution | 0.0098 | 239.6545 | 0.0023486 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Allocation Round 5 | Tidal Stream | Distribution | 0.0538 | 275.8814 | 0.014842 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Allocation Round 6 | Tidal Stream | Transmission | 0.0328 | 239.6545 | 0.0078607 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2029/30 | Allocation Round 7 | Tidal Stream | Transmission | 0.0398 | 265 | 0.010547 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 6 | Tidal Stream | Transmission | 0.0328 | 239.6545 | 0.0078607 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 7 | Tidal Stream | Transmission | 0.0608 | 265 | 0.016112 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 5 | Tidal Stream | Distribution | 0.0538 | 275.8814 | 0.014842 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 4 | Tidal Stream | Distribution | 0.0425 | 248.767 | 0.010573 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 5 | Tidal Stream | Transmission | 0.0489 | 275.8814 | 0.013491 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 6 | Tidal Stream | Distribution | 0.0098 | 239.6545 | 0.0023486 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 7 | Tidal Stream | Distribution | 0.004 | 265 | 0.00106 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Investment Contract | Dedicated Biomass | Transmission | 1.9651 | 203.9414 | 0.40077 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2030/31 | Allocation Round 4 | Solar PV | Distribution | 1.7464 | 64.0797 | 0.11191 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 5 | Solar PV | Transmission | 0.3454 | 65.487 | 0.022619 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 6 | Solar PV | Distribution | 2.984 | 69.7645 | 0.20818 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 7 | Solar PV | Transmission | 0.8306 | 65.23 | 0.05418 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 7 | Solar PV | Distribution | 4.8871 | 65.23 | 0.31879 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 5 | Solar PV | Distribution | 1.5821 | 65.487 | 0.10361 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 6 | Solar PV | Transmission | 0.6418 | 69.7645 | 0.044775 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 4 | Solar PV | Transmission | 0.3384 | 64.0797 | 0.021685 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 1 | Solar PV | Distribution | 0.0265 | 13.2162 | 0.00035023 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2030/31 | Allocation Round 1 | Energy from Waste | Distribution | 0.1673 | 130.7763 | 0.021879 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2030/31 | Allocation Round 1 | Onshore Wind | Distribution | 0.8756 | 119.3594 | 0.10451 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2030/31 | Allocation Round 1 | Onshore Wind | Transmission | 0.7838 | 133.3124 | 0.10449 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2030/31 | Allocation Round 4 | Onshore Wind | Transmission | 1.4505 | 59.1752 | 0.085834 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 5 | Onshore Wind | Distribution | 0.6226 | 72.8578 | 0.045361 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 5 | Onshore Wind | Transmission | 2.6247 | 72.8578 | 0.19123 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 6 | Onshore Wind | Distribution | 0.6437 | 70.921 | 0.045652 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 6 | Onshore Wind | Transmission | 1.788 | 70.921 | 0.12681 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 7 | Onshore Wind | Distribution | 1.0224 | 72.24 | 0.073858 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 7 | Onshore Wind | Transmission | 2.2484 | 72.24 | 0.16242 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 3 | Remote Island Wind | Distribution | 0.0756 | 68.0196 | 0.0051423 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2030/31 | Allocation Round 3 | Remote Island Wind | Transmission | 0.125 | 60.9592 | 0.0076199 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2030/31 | Allocation Round 4 | Remote Island Wind | Distribution | 0.1012 | 64.6371 | 0.0065413 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 4 | Remote Island Wind | Transmission | 0.7487 | 64.6371 | 0.048394 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 5 | Remote Island Wind | Transmission | 0.7609 | 72.8578 | 0.055437 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 1 | Advanced Conversion Technology | Distribution | 0.0915 | 195.9882 | 0.017933 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2030/31 | Allocation Round 6 | Floating Offshore Wind | Transmission | 1.3612 | 194.9701 | 0.26539 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 7 | Floating Offshore Wind | Transmission | 0.2464 | 216.49 | 0.053343 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 1 | Offshore Wind | Transmission | 4.2635 | 191.8387 | 0.8179 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2030/31 | Allocation Round 2 | Offshore Wind | Transmission | 9.6239 | 73.7529 | 0.70979 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2030/31 | Allocation Round 3 | Offshore Wind | Transmission | 18.9864 | 62.6494 | 1.1895 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2030/31 | Allocation Round 4 | Offshore Wind | Transmission | 14.8866 | 52.0413 | 0.77472 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 6 | Offshore Wind | Transmission | 8.9633 | 79.9608 | 0.71671 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Allocation Round 7 | Offshore Wind | Transmission | 9.7187 | 90.9138 | 0.88356 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Investment Contract | Offshore Wind | Transmission | 11.9899 | 144.8197 | 1.7364 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2030/31 | Allocation Round 5 | Geothermal | Distribution | 0.0922 | 165.8075 | 0.015287 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2030/31 | Bespoke | Nuclear | Transmission | 9.8867 | 147.9704 | 1.4629 | nuclear | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2031/32 | Allocation Round 5 | Geothermal | Distribution | 0.0925 | 165.8075 | 0.015337 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Bespoke | Nuclear | Transmission | 21.833 | 147.9704 | 3.2306 | nuclear | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2031/32 | Allocation Round 1 | Offshore Wind | Transmission | 4.2759 | 191.8387 | 0.82028 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2031/32 | Allocation Round 2 | Offshore Wind | Transmission | 9.6522 | 73.7529 | 0.71188 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2031/32 | Allocation Round 3 | Offshore Wind | Transmission | 19.0399 | 62.6494 | 1.1928 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2031/32 | Allocation Round 4 | Offshore Wind | Transmission | 14.9286 | 52.0413 | 0.7769 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 6 | Offshore Wind | Transmission | 8.9885 | 79.9608 | 0.71873 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 7 | Offshore Wind | Transmission | 15.0069 | 90.9138 | 1.3643 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Investment Contract | Offshore Wind | Transmission | 12.0229 | 144.8197 | 1.7412 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2031/32 | Allocation Round 1 | Solar PV | Distribution | 0.0151 | 13.2162 | 0.00019957 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2031/32 | Allocation Round 4 | Solar PV | Transmission | 0.3389 | 64.0797 | 0.021717 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 6 | Solar PV | Transmission | 0.6428 | 69.7645 | 0.044845 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 5 | Solar PV | Distribution | 1.6215 | 65.487 | 0.10619 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 7 | Solar PV | Transmission | 0.832 | 65.23 | 0.054271 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 7 | Solar PV | Distribution | 4.8952 | 65.23 | 0.31931 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 6 | Solar PV | Distribution | 3.0185 | 69.7645 | 0.21058 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 5 | Solar PV | Transmission | 0.346 | 65.487 | 0.022658 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 4 | Solar PV | Distribution | 1.7493 | 64.0797 | 0.11209 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 7 | Tidal Stream | Transmission | 0.0609 | 265 | 0.016139 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 6 | Tidal Stream | Transmission | 0.0545 | 239.6545 | 0.013061 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 5 | Tidal Stream | Distribution | 0.0539 | 275.8814 | 0.01487 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 4 | Tidal Stream | Transmission | 0.027 | 248.767 | 0.0067167 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 5 | Tidal Stream | Transmission | 0.1016 | 275.8814 | 0.02803 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 4 | Tidal Stream | Distribution | 0.0426 | 248.767 | 0.010597 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 7 | Tidal Stream | Distribution | 0.0079 | 265 | 0.0020935 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 6 | Tidal Stream | Distribution | 0.0098 | 239.6545 | 0.0023486 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Investment Contract | Dedicated Biomass | Transmission | 1.9705 | 203.9414 | 0.40187 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2031/32 | Allocation Round 6 | Floating Offshore Wind | Transmission | 1.365 | 194.9701 | 0.26613 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 7 | Floating Offshore Wind | Transmission | 0.6671 | 216.49 | 0.14442 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 3 | Remote Island Wind | Distribution | 0.1744 | 68.0196 | 0.011863 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2031/32 | Allocation Round 3 | Remote Island Wind | Transmission | 0.1253 | 60.9592 | 0.0076382 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2031/32 | Allocation Round 4 | Remote Island Wind | Distribution | 0.1015 | 64.6371 | 0.0065607 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 4 | Remote Island Wind | Transmission | 0.7508 | 64.6371 | 0.04853 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 5 | Remote Island Wind | Transmission | 0.763 | 72.8578 | 0.05559 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 1 | Energy from Waste | Distribution | 0.1677 | 130.7763 | 0.021931 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2031/32 | Allocation Round 1 | Onshore Wind | Distribution | 0.878 | 119.3594 | 0.1048 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2031/32 | Allocation Round 1 | Onshore Wind | Transmission | 0.7861 | 133.3124 | 0.1048 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2031/32 | Allocation Round 4 | Onshore Wind | Transmission | 1.4547 | 59.1752 | 0.086082 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 5 | Onshore Wind | Distribution | 0.6243 | 72.8578 | 0.045485 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 5 | Onshore Wind | Transmission | 2.805 | 72.8578 | 0.20437 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 6 | Onshore Wind | Distribution | 0.6455 | 70.921 | 0.04578 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 6 | Onshore Wind | Transmission | 1.7931 | 70.921 | 0.12717 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 7 | Onshore Wind | Distribution | 1.0253 | 72.24 | 0.074068 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 7 | Onshore Wind | Transmission | 2.2548 | 72.24 | 0.16289 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2031/32 | Allocation Round 1 | Advanced Conversion Technology | Distribution | 0.0918 | 195.9882 | 0.017992 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2032/33 | Allocation Round 1 | Advanced Conversion Technology | Distribution | 0.0915 | 195.9882 | 0.017933 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2032/33 | Allocation Round 1 | Offshore Wind | Transmission | 4.2635 | 191.8387 | 0.8179 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2032/33 | Allocation Round 2 | Offshore Wind | Transmission | 9.6239 | 73.7529 | 0.70979 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2032/33 | Allocation Round 3 | Offshore Wind | Transmission | 18.9864 | 62.6494 | 1.1895 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2032/33 | Allocation Round 4 | Offshore Wind | Transmission | 14.8866 | 52.0413 | 0.77472 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 6 | Offshore Wind | Transmission | 8.9633 | 79.9608 | 0.71671 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 7 | Offshore Wind | Transmission | 24.9205 | 90.9138 | 2.2656 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Investment Contract | Offshore Wind | Transmission | 9.6499 | 144.7199 | 1.3965 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2032/33 | Allocation Round 5 | Geothermal | Distribution | 0.0922 | 165.8075 | 0.015287 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Bespoke | Nuclear | Transmission | 23.7617 | 147.9704 | 3.516 | nuclear | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2032/33 | Allocation Round 5 | Solar PV | Distribution | 1.6188 | 65.487 | 0.10601 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 4 | Solar PV | Distribution | 1.7464 | 64.0797 | 0.11191 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 7 | Solar PV | Transmission | 0.8306 | 65.23 | 0.05418 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 6 | Solar PV | Transmission | 0.6418 | 69.7645 | 0.044775 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 7 | Solar PV | Distribution | 4.8871 | 65.23 | 0.31879 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 6 | Solar PV | Distribution | 3.0135 | 69.7645 | 0.21024 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 4 | Solar PV | Transmission | 0.3384 | 64.0797 | 0.021685 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 5 | Solar PV | Transmission | 0.3454 | 65.487 | 0.022619 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Investment Contract | Dedicated Biomass | Transmission | 1.9651 | 203.9414 | 0.40077 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2032/33 | Allocation Round 7 | Tidal Stream | Transmission | 0.0608 | 265 | 0.016112 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 5 | Tidal Stream | Distribution | 0.0538 | 275.8814 | 0.014842 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 6 | Tidal Stream | Transmission | 0.0613 | 239.6545 | 0.014691 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 4 | Tidal Stream | Distribution | 0.0425 | 248.767 | 0.010573 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 5 | Tidal Stream | Transmission | 0.1184 | 275.8814 | 0.032664 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 6 | Tidal Stream | Distribution | 0.0098 | 239.6545 | 0.0023486 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 4 | Tidal Stream | Transmission | 0.0887 | 248.767 | 0.022066 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 7 | Tidal Stream | Distribution | 0.0078 | 265 | 0.002067 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 3 | Remote Island Wind | Distribution | 0.174 | 68.0196 | 0.011835 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2032/33 | Allocation Round 3 | Remote Island Wind | Transmission | 0.125 | 60.9592 | 0.0076199 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2032/33 | Allocation Round 4 | Remote Island Wind | Distribution | 0.1012 | 64.6371 | 0.0065413 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 4 | Remote Island Wind | Transmission | 0.7487 | 64.6371 | 0.048394 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 5 | Remote Island Wind | Transmission | 0.7609 | 72.8578 | 0.055437 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 6 | Floating Offshore Wind | Transmission | 1.3612 | 194.9701 | 0.26539 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 7 | Floating Offshore Wind | Transmission | 0.6652 | 216.49 | 0.14401 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 1 | Energy from Waste | Distribution | 0.1673 | 130.7763 | 0.021879 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2032/33 | Allocation Round 1 | Onshore Wind | Distribution | 0.8756 | 119.3594 | 0.10451 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2032/33 | Allocation Round 1 | Onshore Wind | Transmission | 0.7838 | 133.3124 | 0.10449 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2032/33 | Allocation Round 4 | Onshore Wind | Transmission | 1.4505 | 59.1752 | 0.085834 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 5 | Onshore Wind | Distribution | 0.6226 | 72.8578 | 0.045361 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 5 | Onshore Wind | Transmission | 2.797 | 72.8578 | 0.20378 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 6 | Onshore Wind | Distribution | 0.6437 | 70.921 | 0.045652 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 6 | Onshore Wind | Transmission | 1.788 | 70.921 | 0.12681 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 7 | Onshore Wind | Distribution | 1.0224 | 72.24 | 0.073858 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2032/33 | Allocation Round 7 | Onshore Wind | Transmission | 2.2484 | 72.24 | 0.16242 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 1 | Energy from Waste | Distribution | 0.1673 | 130.7763 | 0.021879 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2033/34 | Allocation Round 1 | Onshore Wind | Distribution | 0.8372 | 119.3296 | 0.099903 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2033/34 | Allocation Round 1 | Onshore Wind | Transmission | 0.6446 | 133.3124 | 0.085933 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2033/34 | Allocation Round 4 | Onshore Wind | Transmission | 1.4505 | 59.1752 | 0.085834 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 5 | Onshore Wind | Distribution | 0.6226 | 72.8578 | 0.045361 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 5 | Onshore Wind | Transmission | 2.797 | 72.8578 | 0.20378 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 6 | Onshore Wind | Distribution | 0.6437 | 70.921 | 0.045652 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 6 | Onshore Wind | Transmission | 1.788 | 70.921 | 0.12681 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 7 | Onshore Wind | Distribution | 1.0224 | 72.24 | 0.073858 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 7 | Onshore Wind | Transmission | 2.2484 | 72.24 | 0.16242 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 6 | Tidal Stream | Distribution | 0.0098 | 239.6545 | 0.0023486 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 5 | Tidal Stream | Transmission | 0.1184 | 275.8814 | 0.032664 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 7 | Tidal Stream | Distribution | 0.0078 | 265 | 0.002067 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 4 | Tidal Stream | Distribution | 0.0425 | 248.767 | 0.010573 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 7 | Tidal Stream | Transmission | 0.0608 | 265 | 0.016112 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 5 | Tidal Stream | Distribution | 0.0538 | 275.8814 | 0.014842 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 4 | Tidal Stream | Transmission | 0.0887 | 248.767 | 0.022066 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 6 | Tidal Stream | Transmission | 0.0613 | 239.6545 | 0.014691 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 1 | Advanced Conversion Technology | Distribution | 0.0689 | 195.9882 | 0.013504 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2033/34 | Investment Contract | Dedicated Biomass | Transmission | 1.9651 | 203.9414 | 0.40077 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2033/34 | Allocation Round 5 | Geothermal | Distribution | 0.0922 | 165.8075 | 0.015287 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Bespoke | Nuclear | Transmission | 24.1912 | 147.9704 | 3.5796 | nuclear | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2033/34 | Allocation Round 1 | Offshore Wind | Transmission | 4.2617 | 191.8404 | 0.81757 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2033/34 | Allocation Round 2 | Offshore Wind | Transmission | 9.6239 | 73.7529 | 0.70979 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2033/34 | Allocation Round 3 | Offshore Wind | Transmission | 18.9864 | 62.6494 | 1.1895 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2033/34 | Allocation Round 4 | Offshore Wind | Transmission | 14.8866 | 52.0413 | 0.77472 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 6 | Offshore Wind | Transmission | 8.9633 | 79.9608 | 0.71671 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 7 | Offshore Wind | Transmission | 27.7805 | 90.9138 | 2.5256 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Investment Contract | Offshore Wind | Transmission | 6.5963 | 144.8009 | 0.95515 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2033/34 | Allocation Round 4 | Solar PV | Transmission | 0.3384 | 64.0797 | 0.021685 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 7 | Solar PV | Distribution | 4.8871 | 65.23 | 0.31879 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 5 | Solar PV | Transmission | 0.3454 | 65.487 | 0.022619 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 6 | Solar PV | Distribution | 3.0135 | 69.7645 | 0.21024 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 4 | Solar PV | Distribution | 1.7464 | 64.0797 | 0.11191 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 7 | Solar PV | Transmission | 0.8306 | 65.23 | 0.05418 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 5 | Solar PV | Distribution | 1.6188 | 65.487 | 0.10601 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 6 | Solar PV | Transmission | 0.6418 | 69.7645 | 0.044775 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 6 | Floating Offshore Wind | Transmission | 1.3612 | 194.9701 | 0.26539 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 7 | Floating Offshore Wind | Transmission | 0.6652 | 216.49 | 0.14401 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 3 | Remote Island Wind | Distribution | 0.174 | 68.0196 | 0.011835 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2033/34 | Allocation Round 3 | Remote Island Wind | Transmission | 0.125 | 60.9592 | 0.0076199 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2033/34 | Allocation Round 4 | Remote Island Wind | Distribution | 0.1012 | 64.6371 | 0.0065413 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 4 | Remote Island Wind | Transmission | 0.7487 | 64.6371 | 0.048394 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2033/34 | Allocation Round 5 | Remote Island Wind | Transmission | 0.7609 | 72.8578 | 0.055437 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 1 | Offshore Wind | Transmission | 3.5989 | 191.8413 | 0.69042 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2034/35 | Allocation Round 2 | Offshore Wind | Transmission | 9.6239 | 73.7529 | 0.70979 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2034/35 | Allocation Round 3 | Offshore Wind | Transmission | 18.9864 | 62.6494 | 1.1895 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2034/35 | Allocation Round 4 | Offshore Wind | Transmission | 14.8866 | 52.0413 | 0.77472 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 6 | Offshore Wind | Transmission | 8.9633 | 79.9608 | 0.71671 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 7 | Offshore Wind | Transmission | 27.7805 | 90.9138 | 2.5256 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Investment Contract | Offshore Wind | Transmission | 3.4507 | 144.906 | 0.50003 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2034/35 | Allocation Round 5 | Geothermal | Distribution | 0.0922 | 165.8075 | 0.015287 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Bespoke | Nuclear | Transmission | 25.4852 | 147.9704 | 3.7711 | nuclear | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2034/35 | Allocation Round 1 | Energy from Waste | Distribution | 0.1182 | 130.7763 | 0.015458 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2034/35 | Allocation Round 1 | Onshore Wind | Distribution | 0.3734 | 119.386 | 0.044579 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2034/35 | Allocation Round 1 | Onshore Wind | Transmission | 0.0512 | 133.3124 | 0.0068256 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2034/35 | Allocation Round 4 | Onshore Wind | Transmission | 1.4505 | 59.1752 | 0.085834 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 5 | Onshore Wind | Distribution | 0.6226 | 72.8578 | 0.045361 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 5 | Onshore Wind | Transmission | 2.797 | 72.8578 | 0.20378 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 6 | Onshore Wind | Distribution | 0.6437 | 70.921 | 0.045652 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 6 | Onshore Wind | Transmission | 1.788 | 70.921 | 0.12681 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 7 | Onshore Wind | Distribution | 1.0224 | 72.24 | 0.073858 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 7 | Onshore Wind | Transmission | 2.2484 | 72.24 | 0.16242 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 6 | Tidal Stream | Distribution | 0.0098 | 239.6545 | 0.0023486 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 4 | Tidal Stream | Distribution | 0.0425 | 248.767 | 0.010573 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 5 | Tidal Stream | Transmission | 0.1184 | 275.8814 | 0.032664 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 7 | Tidal Stream | Distribution | 0.0078 | 265 | 0.002067 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 4 | Tidal Stream | Transmission | 0.0887 | 248.767 | 0.022066 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 6 | Tidal Stream | Transmission | 0.0613 | 239.6545 | 0.014691 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 7 | Tidal Stream | Transmission | 0.0608 | 265 | 0.016112 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 5 | Tidal Stream | Distribution | 0.0538 | 275.8814 | 0.014842 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Investment Contract | Dedicated Biomass | Transmission | 1.9651 | 203.9414 | 0.40077 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2034/35 | Allocation Round 3 | Remote Island Wind | Distribution | 0.174 | 68.0196 | 0.011835 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2034/35 | Allocation Round 3 | Remote Island Wind | Transmission | 0.125 | 60.9592 | 0.0076199 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2034/35 | Allocation Round 4 | Remote Island Wind | Distribution | 0.1012 | 64.6371 | 0.0065413 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 4 | Remote Island Wind | Transmission | 0.7487 | 64.6371 | 0.048394 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 5 | Remote Island Wind | Transmission | 0.7609 | 72.8578 | 0.055437 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 6 | Solar PV | Transmission | 0.6418 | 69.7645 | 0.044775 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 5 | Solar PV | Distribution | 1.6188 | 65.487 | 0.10601 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 7 | Solar PV | Transmission | 0.8306 | 65.23 | 0.05418 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 4 | Solar PV | Distribution | 1.7464 | 64.0797 | 0.11191 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 7 | Solar PV | Distribution | 4.8871 | 65.23 | 0.31879 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 4 | Solar PV | Transmission | 0.3384 | 64.0797 | 0.021685 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 6 | Solar PV | Distribution | 3.0135 | 69.7645 | 0.21024 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 5 | Solar PV | Transmission | 0.3454 | 65.487 | 0.022619 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 6 | Floating Offshore Wind | Transmission | 1.3612 | 194.9701 | 0.26539 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2034/35 | Allocation Round 7 | Floating Offshore Wind | Transmission | 0.6652 | 216.49 | 0.14401 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 5 | Geothermal | Distribution | 0.0925 | 165.8075 | 0.015337 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Bespoke | Nuclear | Transmission | 26.6294 | 147.9704 | 3.9404 | nuclear | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2035/36 | Allocation Round 1 | Offshore Wind | Transmission | 1.7091 | 191.8411 | 0.32788 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2035/36 | Allocation Round 2 | Offshore Wind | Transmission | 9.6522 | 73.7529 | 0.71188 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2035/36 | Allocation Round 3 | Offshore Wind | Transmission | 19.0399 | 62.6494 | 1.1928 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2035/36 | Allocation Round 4 | Offshore Wind | Transmission | 14.9286 | 52.0413 | 0.7769 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 6 | Offshore Wind | Transmission | 8.9885 | 79.9608 | 0.71873 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 7 | Offshore Wind | Transmission | 27.8588 | 90.9138 | 2.5327 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Investment Contract | Offshore Wind | Transmission | 1.603 | 144.8519 | 0.2322 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2035/36 | Investment Contract | Dedicated Biomass | Transmission | 1.3675 | 203.9414 | 0.27889 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2035/36 | Allocation Round 1 | Onshore Wind | Distribution | 0.0779 | 119.3594 | 0.0092981 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2035/36 | Allocation Round 1 | Onshore Wind | Transmission | 0.0319 | 133.3124 | 0.0042527 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2035/36 | Allocation Round 4 | Onshore Wind | Transmission | 1.4547 | 59.1752 | 0.086082 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 5 | Onshore Wind | Distribution | 0.6243 | 72.8578 | 0.045485 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 5 | Onshore Wind | Transmission | 2.805 | 72.8578 | 0.20437 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 6 | Onshore Wind | Distribution | 0.6455 | 70.921 | 0.04578 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 6 | Onshore Wind | Transmission | 1.7931 | 70.921 | 0.12717 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 7 | Onshore Wind | Distribution | 1.0253 | 72.24 | 0.074068 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 7 | Onshore Wind | Transmission | 2.2548 | 72.24 | 0.16289 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 7 | Tidal Stream | Transmission | 0.0609 | 265 | 0.016139 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 4 | Tidal Stream | Transmission | 0.0889 | 248.767 | 0.022115 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 5 | Tidal Stream | Transmission | 0.1187 | 275.8814 | 0.032747 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 6 | Tidal Stream | Transmission | 0.0615 | 239.6545 | 0.014739 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 5 | Tidal Stream | Distribution | 0.0539 | 275.8814 | 0.01487 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 6 | Tidal Stream | Distribution | 0.0098 | 239.6545 | 0.0023486 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 4 | Tidal Stream | Distribution | 0.0426 | 248.767 | 0.010597 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 7 | Tidal Stream | Distribution | 0.0079 | 265 | 0.0020935 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 6 | Floating Offshore Wind | Transmission | 1.365 | 194.9701 | 0.26613 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 7 | Floating Offshore Wind | Transmission | 0.6671 | 216.49 | 0.14442 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 3 | Remote Island Wind | Distribution | 0.1744 | 68.0196 | 0.011863 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2035/36 | Allocation Round 3 | Remote Island Wind | Transmission | 0.1253 | 60.9592 | 0.0076382 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2035/36 | Allocation Round 4 | Remote Island Wind | Distribution | 0.1015 | 64.6371 | 0.0065607 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 4 | Remote Island Wind | Transmission | 0.7508 | 64.6371 | 0.04853 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 5 | Remote Island Wind | Transmission | 0.763 | 72.8578 | 0.05559 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 6 | Solar PV | Distribution | 3.0185 | 69.7645 | 0.21058 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 4 | Solar PV | Transmission | 0.3389 | 64.0797 | 0.021717 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 7 | Solar PV | Distribution | 4.8952 | 65.23 | 0.31931 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 5 | Solar PV | Transmission | 0.346 | 65.487 | 0.022658 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 5 | Solar PV | Distribution | 1.6215 | 65.487 | 0.10619 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 7 | Solar PV | Transmission | 0.832 | 65.23 | 0.054271 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 4 | Solar PV | Distribution | 1.7493 | 64.0797 | 0.11209 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2035/36 | Allocation Round 6 | Solar PV | Transmission | 0.6428 | 69.7645 | 0.044845 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 7 | Solar PV | Distribution | 4.8871 | 65.23 | 0.31879 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 5 | Solar PV | Transmission | 0.3454 | 65.487 | 0.022619 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 6 | Solar PV | Distribution | 3.0135 | 69.7645 | 0.21024 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 4 | Solar PV | Transmission | 0.3384 | 64.0797 | 0.021685 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 6 | Solar PV | Transmission | 0.6418 | 69.7645 | 0.044775 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 7 | Solar PV | Transmission | 0.8306 | 65.23 | 0.05418 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 4 | Solar PV | Distribution | 1.7464 | 64.0797 | 0.11191 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 5 | Solar PV | Distribution | 1.6188 | 65.487 | 0.10601 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 1 | Onshore Wind | Distribution | 0.0776 | 119.3594 | 0.0092623 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2036/37 | Allocation Round 4 | Onshore Wind | Transmission | 1.4505 | 59.1752 | 0.085834 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 5 | Onshore Wind | Distribution | 0.6226 | 72.8578 | 0.045361 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 5 | Onshore Wind | Transmission | 2.797 | 72.8578 | 0.20378 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 6 | Onshore Wind | Distribution | 0.6437 | 70.921 | 0.045652 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 6 | Onshore Wind | Transmission | 1.788 | 70.921 | 0.12681 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 7 | Onshore Wind | Distribution | 1.0224 | 72.24 | 0.073858 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 7 | Onshore Wind | Transmission | 2.2484 | 72.24 | 0.16242 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 1 | Offshore Wind | Transmission | 1.5577 | 191.8387 | 0.29883 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2036/37 | Allocation Round 2 | Offshore Wind | Transmission | 8.5145 | 73.7372 | 0.62784 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2036/37 | Allocation Round 3 | Offshore Wind | Transmission | 18.9864 | 62.6494 | 1.1895 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2036/37 | Allocation Round 4 | Offshore Wind | Transmission | 14.8866 | 52.0413 | 0.77472 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 6 | Offshore Wind | Transmission | 8.9633 | 79.9608 | 0.71671 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 7 | Offshore Wind | Transmission | 27.7805 | 90.9138 | 2.5256 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 5 | Geothermal | Distribution | 0.0922 | 165.8075 | 0.015287 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Bespoke | Nuclear | Transmission | 26.7586 | 147.9704 | 3.9595 | nuclear | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2036/37 | Allocation Round 3 | Remote Island Wind | Distribution | 0.174 | 68.0196 | 0.011835 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2036/37 | Allocation Round 3 | Remote Island Wind | Transmission | 0.125 | 60.9592 | 0.0076199 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2036/37 | Allocation Round 4 | Remote Island Wind | Distribution | 0.1012 | 64.6371 | 0.0065413 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 4 | Remote Island Wind | Transmission | 0.7487 | 64.6371 | 0.048394 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 5 | Remote Island Wind | Transmission | 0.7609 | 72.8578 | 0.055437 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 5 | Tidal Stream | Transmission | 0.1184 | 275.8814 | 0.032664 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 4 | Tidal Stream | Distribution | 0.0425 | 248.767 | 0.010573 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 6 | Tidal Stream | Distribution | 0.0098 | 239.6545 | 0.0023486 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 7 | Tidal Stream | Distribution | 0.0078 | 265 | 0.002067 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 4 | Tidal Stream | Transmission | 0.0887 | 248.767 | 0.022066 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 6 | Tidal Stream | Transmission | 0.0613 | 239.6545 | 0.014691 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 5 | Tidal Stream | Distribution | 0.0538 | 275.8814 | 0.014842 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 7 | Tidal Stream | Transmission | 0.0608 | 265 | 0.016112 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 6 | Floating Offshore Wind | Transmission | 1.3612 | 194.9701 | 0.26539 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2036/37 | Allocation Round 7 | Floating Offshore Wind | Transmission | 0.6652 | 216.49 | 0.14401 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 5 | Solar PV | Transmission | 0.3454 | 65.487 | 0.022619 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 7 | Solar PV | Distribution | 4.8871 | 65.23 | 0.31879 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 6 | Solar PV | Transmission | 0.6418 | 69.7645 | 0.044775 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 4 | Solar PV | Transmission | 0.3384 | 64.0797 | 0.021685 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 4 | Solar PV | Distribution | 1.7464 | 64.0797 | 0.11191 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 6 | Solar PV | Distribution | 3.0135 | 69.7645 | 0.21024 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 7 | Solar PV | Transmission | 0.8306 | 65.23 | 0.05418 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 5 | Solar PV | Distribution | 1.6188 | 65.487 | 0.10601 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 1 | Onshore Wind | Distribution | 0.0776 | 119.3594 | 0.0092623 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2037/38 | Allocation Round 4 | Onshore Wind | Transmission | 1.4505 | 59.1752 | 0.085834 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 5 | Onshore Wind | Distribution | 0.6226 | 72.8578 | 0.045361 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 5 | Onshore Wind | Transmission | 2.797 | 72.8578 | 0.20378 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 6 | Onshore Wind | Distribution | 0.6437 | 70.921 | 0.045652 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 6 | Onshore Wind | Transmission | 1.788 | 70.921 | 0.12681 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 7 | Onshore Wind | Distribution | 1.0224 | 72.24 | 0.073858 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 7 | Onshore Wind | Transmission | 2.2484 | 72.24 | 0.16242 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 6 | Floating Offshore Wind | Transmission | 1.3612 | 194.9701 | 0.26539 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 7 | Floating Offshore Wind | Transmission | 0.6652 | 216.49 | 0.14401 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 3 | Remote Island Wind | Distribution | 0.174 | 68.0196 | 0.011835 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2037/38 | Allocation Round 3 | Remote Island Wind | Transmission | 0.125 | 60.9592 | 0.0076199 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2037/38 | Allocation Round 4 | Remote Island Wind | Distribution | 0.1012 | 64.6371 | 0.0065413 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 4 | Remote Island Wind | Transmission | 0.7487 | 64.6371 | 0.048394 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 5 | Remote Island Wind | Transmission | 0.7609 | 72.8578 | 0.055437 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 5 | Geothermal | Distribution | 0.0922 | 165.8075 | 0.015287 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Bespoke | Nuclear | Transmission | 26.639 | 147.9704 | 3.9418 | nuclear | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2037/38 | Allocation Round 1 | Offshore Wind | Transmission | 1.5577 | 191.8387 | 0.29883 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2037/38 | Allocation Round 2 | Offshore Wind | Transmission | 7.3806 | 73.7426 | 0.54426 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2037/38 | Allocation Round 3 | Offshore Wind | Transmission | 18.9864 | 62.6494 | 1.1895 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2037/38 | Allocation Round 4 | Offshore Wind | Transmission | 14.8866 | 52.0413 | 0.77472 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 6 | Offshore Wind | Transmission | 8.9633 | 79.9608 | 0.71671 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 7 | Offshore Wind | Transmission | 27.7805 | 90.9138 | 2.5256 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 7 | Tidal Stream | Transmission | 0.0608 | 265 | 0.016112 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 4 | Tidal Stream | Distribution | 0.0425 | 248.767 | 0.010573 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 5 | Tidal Stream | Distribution | 0.0538 | 275.8814 | 0.014842 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 6 | Tidal Stream | Transmission | 0.0613 | 239.6545 | 0.014691 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 5 | Tidal Stream | Transmission | 0.1184 | 275.8814 | 0.032664 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 4 | Tidal Stream | Transmission | 0.0887 | 248.767 | 0.022066 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 7 | Tidal Stream | Distribution | 0.0078 | 265 | 0.002067 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2037/38 | Allocation Round 6 | Tidal Stream | Distribution | 0.0098 | 239.6545 | 0.0023486 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 6 | Tidal Stream | Transmission | 0.0613 | 239.6545 | 0.014691 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 4 | Tidal Stream | Distribution | 0.0425 | 248.767 | 0.010573 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 7 | Tidal Stream | Transmission | 0.0608 | 265 | 0.016112 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 5 | Tidal Stream | Distribution | 0.0538 | 275.8814 | 0.014842 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 5 | Tidal Stream | Transmission | 0.1184 | 275.8814 | 0.032664 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 4 | Tidal Stream | Transmission | 0.0887 | 248.767 | 0.022066 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 7 | Tidal Stream | Distribution | 0.0078 | 265 | 0.002067 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 6 | Tidal Stream | Distribution | 0.0098 | 239.6545 | 0.0023486 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 7 | Solar PV | Transmission | 0.8306 | 65.23 | 0.05418 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 4 | Solar PV | Distribution | 1.744 | 64.0797 | 0.11176 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 6 | Solar PV | Distribution | 3.0135 | 69.7645 | 0.21024 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 5 | Solar PV | Distribution | 1.6188 | 65.487 | 0.10601 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 5 | Solar PV | Transmission | 0.3454 | 65.487 | 0.022619 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 6 | Solar PV | Transmission | 0.6418 | 69.7645 | 0.044775 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 4 | Solar PV | Transmission | 0.3384 | 64.0797 | 0.021685 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 7 | Solar PV | Distribution | 4.8871 | 65.23 | 0.31879 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 1 | Onshore Wind | Distribution | 0.0776 | 119.3594 | 0.0092623 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2038/39 | Allocation Round 4 | Onshore Wind | Transmission | 1.4505 | 59.1752 | 0.085834 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 5 | Onshore Wind | Distribution | 0.6226 | 72.8578 | 0.045361 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 5 | Onshore Wind | Transmission | 2.797 | 72.8578 | 0.20378 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 6 | Onshore Wind | Distribution | 0.6437 | 70.921 | 0.045652 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 6 | Onshore Wind | Transmission | 1.788 | 70.921 | 0.12681 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 7 | Onshore Wind | Distribution | 1.0224 | 72.24 | 0.073858 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 7 | Onshore Wind | Transmission | 2.2484 | 72.24 | 0.16242 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 3 | Remote Island Wind | Distribution | 0.174 | 68.0196 | 0.011835 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2038/39 | Allocation Round 3 | Remote Island Wind | Transmission | 0.125 | 60.9592 | 0.0076199 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2038/39 | Allocation Round 4 | Remote Island Wind | Distribution | 0.1012 | 64.6371 | 0.0065413 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 4 | Remote Island Wind | Transmission | 0.7487 | 64.6371 | 0.048394 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 5 | Remote Island Wind | Transmission | 0.7609 | 72.8578 | 0.055437 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 6 | Floating Offshore Wind | Transmission | 1.3612 | 194.9701 | 0.26539 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 7 | Floating Offshore Wind | Transmission | 0.6652 | 216.49 | 0.14401 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 1 | Offshore Wind | Transmission | 1.5577 | 191.8387 | 0.29883 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2038/39 | Allocation Round 2 | Offshore Wind | Transmission | 3.3388 | 73.7789 | 0.24633 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2038/39 | Allocation Round 3 | Offshore Wind | Transmission | 18.9864 | 62.6494 | 1.1895 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2038/39 | Allocation Round 4 | Offshore Wind | Transmission | 14.8866 | 52.0413 | 0.77472 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 6 | Offshore Wind | Transmission | 8.9633 | 79.9608 | 0.71671 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 7 | Offshore Wind | Transmission | 27.7805 | 90.9138 | 2.5256 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Allocation Round 5 | Geothermal | Distribution | 0.0922 | 165.8075 | 0.015287 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2038/39 | Bespoke | Nuclear | Transmission | 26.6455 | 147.9704 | 3.9427 | nuclear | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2039/40 | Allocation Round 5 | Geothermal | Distribution | 0.0925 | 165.8075 | 0.015337 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Bespoke | Nuclear | Transmission | 26.8289 | 147.9704 | 3.9699 | nuclear | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2039/40 | Allocation Round 1 | Offshore Wind | Transmission | 1.5621 | 191.832 | 0.29966 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2039/40 | Allocation Round 3 | Offshore Wind | Transmission | 18.4181 | 62.6483 | 1.1539 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2039/40 | Allocation Round 4 | Offshore Wind | Transmission | 14.9286 | 52.0413 | 0.7769 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 6 | Offshore Wind | Transmission | 8.9885 | 79.9608 | 0.71873 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 7 | Offshore Wind | Transmission | 27.8588 | 90.9138 | 2.5327 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 7 | Solar PV | Distribution | 4.8952 | 65.23 | 0.31931 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 6 | Solar PV | Distribution | 3.0185 | 69.7645 | 0.21058 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 5 | Solar PV | Transmission | 0.346 | 65.487 | 0.022658 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 4 | Solar PV | Distribution | 1.6923 | 64.0797 | 0.10844 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 6 | Solar PV | Transmission | 0.6428 | 69.7645 | 0.044845 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 4 | Solar PV | Transmission | 0.3184 | 64.0797 | 0.020403 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 5 | Solar PV | Distribution | 1.6215 | 65.487 | 0.10619 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 7 | Solar PV | Transmission | 0.832 | 65.23 | 0.054271 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 6 | Tidal Stream | Transmission | 0.0615 | 239.6545 | 0.014739 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 5 | Tidal Stream | Distribution | 0.0539 | 275.8814 | 0.01487 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 4 | Tidal Stream | Transmission | 0.0889 | 248.767 | 0.022115 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 7 | Tidal Stream | Transmission | 0.0609 | 265 | 0.016139 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 7 | Tidal Stream | Distribution | 0.0079 | 265 | 0.0020935 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 6 | Tidal Stream | Distribution | 0.0098 | 239.6545 | 0.0023486 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 4 | Tidal Stream | Distribution | 0.0426 | 248.767 | 0.010597 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 5 | Tidal Stream | Transmission | 0.1187 | 275.8814 | 0.032747 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 6 | Floating Offshore Wind | Transmission | 1.365 | 194.9701 | 0.26613 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 7 | Floating Offshore Wind | Transmission | 0.6671 | 216.49 | 0.14442 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 3 | Remote Island Wind | Distribution | 0.1744 | 68.0196 | 0.011863 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2039/40 | Allocation Round 3 | Remote Island Wind | Transmission | 0.1253 | 60.9592 | 0.0076382 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2039/40 | Allocation Round 4 | Remote Island Wind | Distribution | 0.1015 | 64.6371 | 0.0065607 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 4 | Remote Island Wind | Transmission | 0.7508 | 64.6371 | 0.04853 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 5 | Remote Island Wind | Transmission | 0.763 | 72.8578 | 0.05559 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 1 | Onshore Wind | Distribution | 0.0009 | 119.3627 | 0.00010743 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2039/40 | Allocation Round 4 | Onshore Wind | Transmission | 1.4547 | 59.1752 | 0.086082 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 5 | Onshore Wind | Distribution | 0.6243 | 72.8578 | 0.045485 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 5 | Onshore Wind | Transmission | 2.805 | 72.8578 | 0.20437 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 6 | Onshore Wind | Distribution | 0.6455 | 70.921 | 0.04578 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 6 | Onshore Wind | Transmission | 1.7931 | 70.921 | 0.12717 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 7 | Onshore Wind | Distribution | 1.0253 | 72.24 | 0.074068 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2039/40 | Allocation Round 7 | Onshore Wind | Transmission | 2.2548 | 72.24 | 0.16289 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 1 | Offshore Wind | Transmission | 0.0669 | 191.8387 | 0.012834 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2040/41 | Allocation Round 3 | Offshore Wind | Transmission | 14.4424 | 62.6497 | 0.90481 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2040/41 | Allocation Round 4 | Offshore Wind | Transmission | 14.8866 | 52.0413 | 0.77472 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 6 | Offshore Wind | Transmission | 8.9633 | 79.9608 | 0.71671 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 7 | Offshore Wind | Transmission | 27.7805 | 90.9138 | 2.5256 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 5 | Geothermal | Distribution | 0.0922 | 165.8075 | 0.015287 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Bespoke | Nuclear | Transmission | 24.6731 | 147.9704 | 3.6509 | nuclear | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2040/41 | Allocation Round 5 | Solar PV | Transmission | 0.3454 | 65.487 | 0.022619 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 6 | Solar PV | Distribution | 3.0135 | 69.7645 | 0.21024 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 7 | Solar PV | Distribution | 4.8871 | 65.23 | 0.31879 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 6 | Solar PV | Transmission | 0.6418 | 69.7645 | 0.044775 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 4 | Solar PV | Transmission | 0.2059 | 64.0797 | 0.013194 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 4 | Solar PV | Distribution | 0.919 | 64.0797 | 0.058889 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 7 | Solar PV | Transmission | 0.8306 | 65.23 | 0.05418 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 5 | Solar PV | Distribution | 1.5931 | 65.487 | 0.10433 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 6 | Tidal Stream | Distribution | 0.0098 | 239.6545 | 0.0023486 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 7 | Tidal Stream | Distribution | 0.0078 | 265 | 0.002067 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 5 | Tidal Stream | Transmission | 0.1184 | 275.8814 | 0.032664 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 4 | Tidal Stream | Distribution | 0.0425 | 248.767 | 0.010573 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 4 | Tidal Stream | Transmission | 0.0887 | 248.767 | 0.022066 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 5 | Tidal Stream | Distribution | 0.0538 | 275.8814 | 0.014842 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 6 | Tidal Stream | Transmission | 0.0613 | 239.6545 | 0.014691 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 7 | Tidal Stream | Transmission | 0.0608 | 265 | 0.016112 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 3 | Remote Island Wind | Distribution | 0.174 | 68.0196 | 0.011835 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2040/41 | Allocation Round 3 | Remote Island Wind | Transmission | 0.125 | 60.9592 | 0.0076199 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator
2040/41 | Allocation Round 4 | Remote Island Wind | Distribution | 0.1012 | 64.6371 | 0.0065413 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 4 | Remote Island Wind | Transmission | 0.7487 | 64.6371 | 0.048394 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 5 | Remote Island Wind | Transmission | 0.7609 | 72.8578 | 0.055437 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 6 | Floating Offshore Wind | Transmission | 1.3612 | 194.9701 | 0.26539 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 7 | Floating Offshore Wind | Transmission | 0.6652 | 216.49 | 0.14401 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 4 | Onshore Wind | Transmission | 1.4505 | 59.1752 | 0.085834 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 5 | Onshore Wind | Distribution | 0.6226 | 72.8578 | 0.045361 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 5 | Onshore Wind | Transmission | 2.797 | 72.8578 | 0.20378 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 6 | Onshore Wind | Distribution | 0.6437 | 70.921 | 0.045652 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 6 | Onshore Wind | Transmission | 1.788 | 70.921 | 0.12681 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 7 | Onshore Wind | Distribution | 1.0224 | 72.24 | 0.073858 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2040/41 | Allocation Round 7 | Onshore Wind | Transmission | 2.2484 | 72.24 | 0.16242 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 4 | Onshore Wind | Transmission | 0.4007 | 59.1752 | 0.023711 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 5 | Onshore Wind | Distribution | 0.5696 | 72.8578 | 0.0415 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 5 | Onshore Wind | Transmission | 2.6728 | 72.8578 | 0.19473 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 6 | Onshore Wind | Distribution | 0.5756 | 70.921 | 0.040822 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 6 | Onshore Wind | Transmission | 1.5518 | 70.921 | 0.11006 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 7 | Onshore Wind | Distribution | 1.0224 | 72.24 | 0.073858 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 7 | Onshore Wind | Transmission | 2.2484 | 72.24 | 0.16242 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 7 | Tidal Stream | Transmission | 0.0608 | 265 | 0.016112 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 6 | Tidal Stream | Transmission | 0.0613 | 239.6545 | 0.014691 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 5 | Tidal Stream | Distribution | 0.0524 | 275.8814 | 0.014456 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 4 | Tidal Stream | Distribution | 0.0416 | 248.767 | 0.010349 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 5 | Tidal Stream | Transmission | 0.1184 | 275.8814 | 0.032664 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 6 | Tidal Stream | Distribution | 0.0098 | 239.6545 | 0.0023486 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 4 | Tidal Stream | Transmission | 0.0887 | 248.767 | 0.022066 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 7 | Tidal Stream | Distribution | 0.0078 | 265 | 0.002067 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 5 | Geothermal | Distribution | 0.0688 | 165.8075 | 0.011408 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Bespoke | Nuclear | Transmission | 24.6764 | 147.9704 | 3.6514 | nuclear | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator; 2040/41 price held constant beyond published strike-price horizon
2041/42 | Allocation Round 3 | Offshore Wind | Transmission | 6.0574 | 62.6497 | 0.37949 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator; 2040/41 price held constant beyond published strike-price horizon
2041/42 | Allocation Round 4 | Offshore Wind | Transmission | 14.8866 | 52.0413 | 0.77472 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 6 | Offshore Wind | Transmission | 8.9633 | 79.9608 | 0.71671 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 7 | Offshore Wind | Transmission | 27.7805 | 90.9138 | 2.5256 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 7 | Solar PV | Distribution | 4.8871 | 65.23 | 0.31879 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 4 | Solar PV | Distribution | 0.1193 | 64.0797 | 0.0076447 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 6 | Solar PV | Distribution | 2.6222 | 69.7645 | 0.18294 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 5 | Solar PV | Transmission | 0.2641 | 65.487 | 0.017295 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 4 | Solar PV | Transmission | 0.1731 | 64.0797 | 0.011092 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 5 | Solar PV | Distribution | 1.3446 | 65.487 | 0.088054 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 7 | Solar PV | Transmission | 0.8306 | 65.23 | 0.05418 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 6 | Solar PV | Transmission | 0.6418 | 69.7645 | 0.044775 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 6 | Floating Offshore Wind | Transmission | 1.3612 | 194.9701 | 0.26539 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 7 | Floating Offshore Wind | Transmission | 0.6652 | 216.49 | 0.14401 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 3 | Remote Island Wind | Distribution | 0.174 | 68.0196 | 0.011835 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator; 2040/41 price held constant beyond published strike-price horizon
2041/42 | Allocation Round 3 | Remote Island Wind | Transmission | 0.125 | 60.9592 | 0.0076199 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator; 2040/41 price held constant beyond published strike-price horizon
2041/42 | Allocation Round 4 | Remote Island Wind | Distribution | 0.1012 | 64.6371 | 0.0065413 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 4 | Remote Island Wind | Transmission | 0.7487 | 64.6371 | 0.048394 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2041/42 | Allocation Round 5 | Remote Island Wind | Transmission | 0.7609 | 72.8578 | 0.055437 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 3 | Offshore Wind | Transmission | 0.7912 | 62.6497 | 0.049568 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator; 2040/41 price held constant beyond published strike-price horizon
2042/43 | Allocation Round 4 | Offshore Wind | Transmission | 11.7598 | 52.0413 | 0.61199 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 6 | Offshore Wind | Transmission | 6.5722 | 79.9608 | 0.52552 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 7 | Offshore Wind | Transmission | 27.7805 | 90.9138 | 2.5256 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 5 | Geothermal | Distribution | 0.0194 | 165.8075 | 0.0032167 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Bespoke | Nuclear | Transmission | 26.7553 | 147.9704 | 3.959 | nuclear | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator; 2040/41 price held constant beyond published strike-price horizon
2042/43 | Allocation Round 4 | Onshore Wind | Transmission | 0.1158 | 59.1752 | 0.0068525 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 5 | Onshore Wind | Distribution | 0.2647 | 72.8578 | 0.019285 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 5 | Onshore Wind | Transmission | 2.2811 | 72.8578 | 0.1662 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 6 | Onshore Wind | Distribution | 0.292 | 70.921 | 0.020709 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 6 | Onshore Wind | Transmission | 1.2973 | 70.921 | 0.092006 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 7 | Onshore Wind | Distribution | 1.0224 | 72.24 | 0.073858 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 7 | Onshore Wind | Transmission | 2.2484 | 72.24 | 0.16242 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 5 | Tidal Stream | Transmission | 0.1184 | 275.8814 | 0.032664 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 7 | Tidal Stream | Distribution | 0.0078 | 265 | 0.002067 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 6 | Tidal Stream | Transmission | 0.0613 | 239.6545 | 0.014691 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 4 | Tidal Stream | Transmission | 0.0887 | 248.767 | 0.022066 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 5 | Tidal Stream | Distribution | 0.0336 | 275.8814 | 0.0092696 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 7 | Tidal Stream | Transmission | 0.0608 | 265 | 0.016112 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 6 | Tidal Stream | Distribution | 0.0098 | 239.6545 | 0.0023486 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 4 | Tidal Stream | Distribution | 0.0001 | 248.767 | 2.4877e-05 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 3 | Remote Island Wind | Distribution | 0.174 | 68.0196 | 0.011835 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator; 2040/41 price held constant beyond published strike-price horizon
2042/43 | Allocation Round 3 | Remote Island Wind | Transmission | 0.125 | 60.9592 | 0.0076199 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator; 2040/41 price held constant beyond published strike-price horizon
2042/43 | Allocation Round 4 | Remote Island Wind | Distribution | 0.1012 | 64.6371 | 0.0065413 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 5 | Remote Island Wind | Transmission | 0.7609 | 72.8578 | 0.055437 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 6 | Solar PV | Transmission | 0.5862 | 69.7645 | 0.040896 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 5 | Solar PV | Distribution | 1.1196 | 65.487 | 0.073319 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 4 | Solar PV | Transmission | 0.1229 | 64.0797 | 0.0078754 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 6 | Solar PV | Distribution | 1.8128 | 69.7645 | 0.12647 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 7 | Solar PV | Transmission | 0.8306 | 65.23 | 0.05418 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 4 | Solar PV | Distribution | 0.0411 | 64.0797 | 0.0026337 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 5 | Solar PV | Transmission | 0.2029 | 65.487 | 0.013287 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 7 | Solar PV | Distribution | 4.8871 | 65.23 | 0.31879 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 6 | Floating Offshore Wind | Transmission | 1.3612 | 194.9701 | 0.26539 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2042/43 | Allocation Round 7 | Floating Offshore Wind | Transmission | 0.6652 | 216.49 | 0.14401 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2043/44 | Bespoke | Nuclear | Transmission | 26.7159 | 147.9704 | 3.9532 | nuclear | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator; 2040/41 price held constant beyond published strike-price horizon
2043/44 | Allocation Round 4 | Offshore Wind | Transmission | 4.7103 | 52.0413 | 0.24513 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2043/44 | Allocation Round 6 | Offshore Wind | Transmission | 2.4901 | 79.9608 | 0.19911 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2043/44 | Allocation Round 7 | Offshore Wind | Transmission | 27.8588 | 90.9138 | 2.5327 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2043/44 | Allocation Round 5 | Onshore Wind | Distribution | 0.0911 | 72.8578 | 0.0066373 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2043/44 | Allocation Round 5 | Onshore Wind | Transmission | 0.9495 | 72.8578 | 0.069178 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2043/44 | Allocation Round 6 | Onshore Wind | Distribution | 0.091 | 70.921 | 0.0064538 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2043/44 | Allocation Round 6 | Onshore Wind | Transmission | 0.5589 | 70.921 | 0.039638 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2043/44 | Allocation Round 7 | Onshore Wind | Distribution | 1.0253 | 72.24 | 0.074068 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2043/44 | Allocation Round 7 | Onshore Wind | Transmission | 2.2548 | 72.24 | 0.16289 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2043/44 | Allocation Round 6 | Tidal Stream | Distribution | 0.009 | 239.6545 | 0.0021569 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2043/44 | Allocation Round 5 | Tidal Stream | Transmission | 0.0697 | 275.8814 | 0.019229 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2043/44 | Allocation Round 7 | Tidal Stream | Transmission | 0.056 | 265 | 0.01484 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2043/44 | Allocation Round 6 | Tidal Stream | Transmission | 0.0315 | 239.6545 | 0.0075491 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2043/44 | Allocation Round 5 | Tidal Stream | Distribution | 0.0098 | 275.8814 | 0.0027036 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2043/44 | Allocation Round 7 | Tidal Stream | Distribution | 0.0079 | 265 | 0.0020935 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2043/44 | Allocation Round 4 | Tidal Stream | Transmission | 0.0889 | 248.767 | 0.022115 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2043/44 | Allocation Round 6 | Floating Offshore Wind | Transmission | 1.365 | 194.9701 | 0.26613 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2043/44 | Allocation Round 7 | Floating Offshore Wind | Transmission | 0.6671 | 216.49 | 0.14442 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2043/44 | Allocation Round 3 | Remote Island Wind | Distribution | 0.1744 | 68.0196 | 0.011863 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator; 2040/41 price held constant beyond published strike-price horizon
2043/44 | Allocation Round 3 | Remote Island Wind | Transmission | 0.03 | 60.9592 | 0.0018288 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator; 2040/41 price held constant beyond published strike-price horizon
2043/44 | Allocation Round 4 | Remote Island Wind | Distribution | 0.0407 | 64.6371 | 0.0026307 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2043/44 | Allocation Round 5 | Solar PV | Distribution | 0.092 | 65.487 | 0.0060248 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2043/44 | Allocation Round 4 | Solar PV | Distribution | 0.0005 | 64.0797 | 3.204e-05 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2043/44 | Allocation Round 7 | Solar PV | Transmission | 0.832 | 65.23 | 0.054271 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2043/44 | Allocation Round 6 | Solar PV | Transmission | 0.0991 | 69.7645 | 0.0069137 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2043/44 | Allocation Round 4 | Solar PV | Transmission | 0.1159 | 64.0797 | 0.0074268 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2043/44 | Allocation Round 7 | Solar PV | Distribution | 4.8952 | 65.23 | 0.31931 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2043/44 | Allocation Round 6 | Solar PV | Distribution | 0.132 | 69.7645 | 0.0092089 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2043/44 | Allocation Round 5 | Solar PV | Transmission | 0.0791 | 65.487 | 0.00518 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2044/45 | Allocation Round 7 | Solar PV | Transmission | 0.8306 | 65.23 | 0.05418 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2044/45 | Allocation Round 5 | Solar PV | Distribution | 0.0614 | 65.487 | 0.0040209 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2044/45 | Allocation Round 7 | Solar PV | Distribution | 4.8871 | 65.23 | 0.31879 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2044/45 | Allocation Round 4 | Solar PV | Transmission | 0.0531 | 64.0797 | 0.0034026 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2044/45 | Allocation Round 6 | Solar PV | Distribution | 0.0332 | 69.7645 | 0.0023162 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2044/45 | Allocation Round 5 | Onshore Wind | Transmission | 0.5644 | 72.8578 | 0.041121 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2044/45 | Allocation Round 7 | Onshore Wind | Distribution | 1.0224 | 72.24 | 0.073858 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2044/45 | Allocation Round 7 | Onshore Wind | Transmission | 2.2484 | 72.24 | 0.16242 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2044/45 | Allocation Round 7 | Offshore Wind | Transmission | 27.7805 | 90.9138 | 2.5256 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2044/45 | Bespoke | Nuclear | Transmission | 26.6455 | 147.9704 | 3.9427 | nuclear | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator; 2040/41 price held constant beyond published strike-price horizon
2044/45 | Allocation Round 3 | Remote Island Wind | Distribution | 0.174 | 68.0196 | 0.011835 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator; 2040/41 price held constant beyond published strike-price horizon
2044/45 | Allocation Round 7 | Tidal Stream | Transmission | 0.0211 | 265 | 0.0055915 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2044/45 | Allocation Round 5 | Tidal Stream | Transmission | 0.0695 | 275.8814 | 0.019174 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2044/45 | Allocation Round 4 | Tidal Stream | Transmission | 0.0887 | 248.767 | 0.022066 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2044/45 | Allocation Round 6 | Tidal Stream | Transmission | 0.0285 | 239.6545 | 0.0068302 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2044/45 | Allocation Round 7 | Tidal Stream | Distribution | 0.0078 | 265 | 0.002067 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2044/45 | Allocation Round 6 | Floating Offshore Wind | Transmission | 0.6511 | 194.9701 | 0.12695 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2044/45 | Allocation Round 7 | Floating Offshore Wind | Transmission | 0.6652 | 216.49 | 0.14401 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2045/46 | Allocation Round 5 | Solar PV | Distribution | 0.0368 | 65.487 | 0.0024099 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2045/46 | Allocation Round 7 | Solar PV | Transmission | 0.8306 | 65.23 | 0.05418 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2045/46 | Allocation Round 7 | Solar PV | Distribution | 4.8871 | 65.23 | 0.31879 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2045/46 | Allocation Round 5 | Onshore Wind | Transmission | 0.1734 | 72.8578 | 0.012634 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2045/46 | Allocation Round 7 | Onshore Wind | Distribution | 1.0224 | 72.24 | 0.073858 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2045/46 | Allocation Round 7 | Onshore Wind | Transmission | 2.2484 | 72.24 | 0.16242 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2045/46 | Allocation Round 7 | Floating Offshore Wind | Transmission | 0.6652 | 216.49 | 0.14401 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2045/46 | Allocation Round 3 | Remote Island Wind | Distribution | 0.0989 | 68.0196 | 0.0067271 | renewable_and_other_supported | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator; 2040/41 price held constant beyond published strike-price horizon
2045/46 | Bespoke | Nuclear | Transmission | 26.7553 | 147.9704 | 3.959 | nuclear | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator; 2040/41 price held constant beyond published strike-price horizon
2045/46 | Allocation Round 7 | Offshore Wind | Transmission | 27.7805 | 90.9138 | 2.5256 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2045/46 | Allocation Round 4 | Tidal Stream | Transmission | 0.0887 | 248.767 | 0.022066 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2045/46 | Allocation Round 7 | Tidal Stream | Distribution | 0.0039 | 265 | 0.0010335 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2045/46 | Allocation Round 5 | Tidal Stream | Transmission | 0.0695 | 275.8814 | 0.019174 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2045/46 | Allocation Round 6 | Tidal Stream | Transmission | 0.0285 | 239.6545 | 0.0068302 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2046/47 | Allocation Round 5 | Tidal Stream | Transmission | 0.0173 | 275.8814 | 0.0047727 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2046/47 | Allocation Round 4 | Tidal Stream | Transmission | 0.0622 | 248.767 | 0.015473 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2046/47 | Allocation Round 6 | Tidal Stream | Transmission | 0.0071 | 239.6545 | 0.0017015 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2046/47 | Allocation Round 7 | Solar PV | Distribution | 4.8781 | 65.23 | 0.3182 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2046/47 | Allocation Round 7 | Solar PV | Transmission | 0.8306 | 65.23 | 0.05418 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2046/47 | Allocation Round 7 | Onshore Wind | Distribution | 1.0224 | 72.24 | 0.073858 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2046/47 | Allocation Round 7 | Onshore Wind | Transmission | 2.1572 | 72.24 | 0.15584 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2046/47 | Allocation Round 7 | Floating Offshore Wind | Transmission | 0.6652 | 216.49 | 0.14401 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2046/47 | Allocation Round 7 | Offshore Wind | Transmission | 27.7805 | 90.9138 | 2.5256 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2046/47 | Bespoke | Nuclear | Transmission | 26.639 | 147.9704 | 3.9418 | nuclear | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator; 2040/41 price held constant beyond published strike-price horizon
2047/48 | Bespoke | Nuclear | Transmission | 26.7192 | 147.9704 | 3.9537 | nuclear | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator; 2040/41 price held constant beyond published strike-price horizon
2047/48 | Allocation Round 7 | Offshore Wind | Transmission | 27.8588 | 90.9138 | 2.5327 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2047/48 | Allocation Round 7 | Solar PV | Transmission | 0.8217 | 65.23 | 0.053599 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2047/48 | Allocation Round 7 | Solar PV | Distribution | 4.5633 | 65.23 | 0.29766 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2047/48 | Allocation Round 7 | Floating Offshore Wind | Transmission | 0.6671 | 216.49 | 0.14442 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2047/48 | Allocation Round 7 | Onshore Wind | Distribution | 0.9806 | 72.24 | 0.070839 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2047/48 | Allocation Round 7 | Onshore Wind | Transmission | 1.8756 | 72.24 | 0.13549 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2048/49 | Allocation Round 7 | Offshore Wind | Transmission | 26.9398 | 90.9138 | 2.4492 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2048/49 | Bespoke | Nuclear | Transmission | 26.7586 | 147.9704 | 3.9595 | nuclear | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator; 2040/41 price held constant beyond published strike-price horizon
2048/49 | Allocation Round 7 | Solar PV | Transmission | 0.7303 | 65.23 | 0.047637 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2048/49 | Allocation Round 7 | Solar PV | Distribution | 2.8947 | 65.23 | 0.18882 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2048/49 | Allocation Round 7 | Floating Offshore Wind | Transmission | 0.6652 | 216.49 | 0.14401 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2048/49 | Allocation Round 7 | Onshore Wind | Distribution | 0.603 | 72.24 | 0.043561 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2048/49 | Allocation Round 7 | Onshore Wind | Transmission | 1.2573 | 72.24 | 0.090827 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2049/50 | Allocation Round 7 | Onshore Wind | Distribution | 0.2001 | 72.24 | 0.014455 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2049/50 | Allocation Round 7 | Onshore Wind | Transmission | 0.4062 | 72.24 | 0.029344 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2049/50 | Allocation Round 7 | Solar PV | Transmission | 0.5395 | 65.23 | 0.035192 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2049/50 | Allocation Round 7 | Solar PV | Distribution | 0.8498 | 65.23 | 0.055432 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2049/50 | Bespoke | Nuclear | Transmission | 24.6698 | 147.9704 | 3.6504 | nuclear | LCCC round/technology/connection/year weighted price, 2020 real rebased by GDP deflator; 2040/41 price held constant beyond published strike-price horizon
2049/50 | Allocation Round 7 | Offshore Wind | Transmission | 22.0485 | 90.9138 | 2.0045 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort
2049/50 | Allocation Round 7 | Floating Offshore Wind | Transmission | 0.6652 | 216.49 | 0.14401 | renewable_and_other_supported | Capacity-weighted auction price by round/technology; proxy for output-weighted surviving cohort

## Checks
Independent checks and replay validation
PASS means the stated check passed on the audited release. It does not certify an assumption as true or establish grid engineering adequacy. Detailed test code and logs are retained under audit/ in the full model.
group | check | status | detail
Reference | Frozen pre-change and v1.28 evidence | PASS | All archived plan, evaluation and source reference hashes preserved.
Inputs | Existing fleet, demand, cost and weather inputs unchanged | PASS | New large-reactor capital is an explicit project-specific reference. Default SMR, gas, coal and renewables inputs are unchanged; electrolysis demand is separately rescheduled using explicit new flexibility settings.
Regression | ours_low: fresh evaluation and schedule/account reconciliation | PASS | Gas technology mix and dated orders change; our programme adds coal in 2037/38. Nuclear, renewable, storage, demand and finance inputs are preserved. Every previously passing connected screen still passes. Clean-target plans retain their original fleet and numerical results. Schedules, energy, inventory, accounts, coal stocks and costs reconcile.
Regression | ours_central: fresh evaluation and schedule/account reconciliation | PASS | Gas technology mix and dated orders change; our programme adds coal in 2037/38. Nuclear, renewable, storage, demand and finance inputs are preserved. Every previously passing connected screen still passes. Clean-target plans retain their original fleet and numerical results. Schedules, energy, inventory, accounts, coal stocks and costs reconcile.
Regression | ours_high: fresh evaluation and schedule/account reconciliation | PASS | Gas technology mix and dated orders change; our programme adds coal in 2037/38. Nuclear, renewable, storage, demand and finance inputs are preserved. Every previously passing connected screen still passes. Clean-target plans retain their original fleet and numerical results. Schedules, energy, inventory, accounts, coal stocks and costs reconcile.
Regression | target_low: fresh evaluation and schedule/account reconciliation | PASS | Gas technology mix and dated orders change; our programme adds coal in 2037/38. Nuclear, renewable, storage, demand and finance inputs are preserved. Every previously passing connected screen still passes. Clean-target plans retain their original fleet and numerical results. Schedules, energy, inventory, accounts, coal stocks and costs reconcile.
Regression | target_central: fresh evaluation and schedule/account reconciliation | PASS | Gas technology mix and dated orders change; our programme adds coal in 2037/38. Nuclear, renewable, storage, demand and finance inputs are preserved. Every previously passing connected screen still passes. Clean-target plans retain their original fleet and numerical results. Schedules, energy, inventory, accounts, coal stocks and costs reconcile.
Regression | target_high: fresh evaluation and schedule/account reconciliation | PASS | Gas technology mix and dated orders change; our programme adds coal in 2037/38. Nuclear, renewable, storage, demand and finance inputs are preserved. Every previously passing connected screen still passes. Clean-target plans retain their original fleet and numerical results. Schedules, energy, inventory, accounts, coal stocks and costs reconcile.
Regression | government_low: fresh evaluation and schedule/account reconciliation | PASS | Gas technology mix and dated orders change; our programme adds coal in 2037/38. Nuclear, renewable, storage, demand and finance inputs are preserved. Every previously passing connected screen still passes. Clean-target plans retain their original fleet and numerical results. Schedules, energy, inventory, accounts, coal stocks and costs reconcile.
Regression | government_central: fresh evaluation and schedule/account reconciliation | PASS | Gas technology mix and dated orders change; our programme adds coal in 2037/38. Nuclear, renewable, storage, demand and finance inputs are preserved. Every previously passing connected screen still passes. Clean-target plans retain their original fleet and numerical results. Schedules, energy, inventory, accounts, coal stocks and costs reconcile.
Regression | government_high: fresh evaluation and schedule/account reconciliation | PASS | Gas technology mix and dated orders change; our programme adds coal in 2037/38. Nuclear, renewable, storage, demand and finance inputs are preserved. Every previously passing connected screen still passes. Clean-target plans retain their original fleet and numerical results. Schedules, energy, inventory, accounts, coal stocks and costs reconcile.
Policy | Pilot-gated SMR and large-reactor arithmetic | PASS | Three inherited pilot units all online in 2035; first repeat order 2034 and output 2039; 2/4/6/8 ramp; four coal stations within delivery ceiling; one separately costed large reactor, with quantity/case/validation tests.
Dispatch | Unchanged CCGT-only target replay reuse | PASS | Zero peaker capacity preserves the historical thermal path. Six fresh normal/stress probes across three demands reproduce old outputs; 63 annual schedules and all 1,575 retained numerical replays are checked.
Interface | Browser/Python schedule parity | PASS | All nine plans and all years, including project-specific capital overrides.
Flexibility | Electrolysis fixed-mode equivalence and cost allowance | PASS | Six fixed-mode dispatch probes across all programmes reproduce the previous release. Capacity, per-block/annual energy, cyclic inventory, zero flexibility and allowance accounting verified independently.
Dispatch | Heterogeneous gas energy/fuel and operating-cost identities | PASS | CCGT, OCGT and engine availability, fuel, starts, inertia and costs remain distinct. No double-counting peakers as inherited CCGT; explicit shortages retained.
Procurement | Mixed-gas and two/four-coal candidates | PASS | Nine balanced candidates use dated CCGT/engine builds within explicit procurement envelopes. Independent two-coal controls preserve nuclear, renewables, storage and domestic coal supply; all formerly passing screens retained.
Procurement | Historical paired whole-station gas sizing | PASS | Fixed/flexible load use the same security screens. Whole 920 MW stations, four-year lead, no pre-2029 orders and combined eight-station annual commissioning limit. Annual counts and complete fixed schedules verified; full flexible schedules recalculated. Unavoidable early delivery gaps remain.

## Delivery study
Gas retention and delivery planning
26 saved delivery cases. Planning: five-year retention, constrained delivery. Workbook edits do not rerun dispatch.
Case | CCGT units | Engine sites | OCGT units | Coal units | New gas GW | 2030–50 cost £bn | All-screen pass years | 2050 cost £bn | Refurbishment cash £bn
Planning: Proposed / central | 30 | 252 | 48 | 4
Planning: Renewables / central | 34 | 285 | 55 | 0
Planning: Proposed / high | 34 | 300 | 57 | 4
Planning: Proposed / low | 33 | 172 | 34 | 4
Planning: Renewables / high | 34 | 300 | 57 | 0
Planning: Renewables / low | 34 | 190 | 38 | 0
Retention: Proposed / central | 30 | 234 | 45 | 4
Retention: Renewables / central | 34 | 270 | 54 | 0
Retention: Proposed / high | 34 | 300 | 57 | 4
Retention: Proposed / low | 33 | 132 | 26 | 4
Retention: Renewables / high | 34 | 300 | 57 | 0
Retention: Renewables / low | 34 | 182 | 36 | 0
Faster: Proposed / central | 40 | 316 | 0 | 4
Faster: Renewables / central | 55 | 274 | 0 | 0
Faster: Proposed / high | 54 | 449 | 0 | 4
Faster: Proposed / low | 33 | 219 | 0 | 4
Faster: Renewables / high | 67 | 335 | 0 | 0
Faster: Renewables / low | 43 | 239 | 0 | 0
Test: Proposed / central / ext0 / coal4 / fast | 40 | 332 | 0 | 4
Test: Proposed / central / ext0 / coal4 / slow | 34 | 255 | 48 | 4
Test: Proposed / central / ext10 / coal4 / slow | 34 | 234 | 45 | 4
Test: Proposed / central / ext5 / coal4 / slow | 34 | 252 | 48 | 4
Test: Proposed / central / ext5 / coal4 / slow50 | 20 | 285 | 54 | 4
Test: Proposed / central / ext5 / coal6 / slow | 34 | 240 | 45 | 6
Test: Proposed / central / ext5 / coal6 / slow / earlycoal | 34 | 240 | 45 | 6
Test: Renewables / central / ext0 / coal0 / slow | 34 | 300 | 57 | 0
Interpretation and inputs
CCGT unit GW | 0.92 | Existing model reference
Engine site GW | 0.1 | Five 20 MW modules per site
OCGT unit GW | 0.3 | Existing peaker reference
Five-year retention | 75% | Eligible named cohort fraction; analyst inspection-success estimate
Availability | 85% | Five-year case; ten-year sensitivity 80%
Full-load efficiency | 54% | Five-year case; ten-year sensitivity 52%
Refurbishment £/kW | 150 | Per five-year tranche; ten-year sensitivity £250/kW
Additional fixed O&M £/kW/year | 10 | Ten-year sensitivity £15/kW/year
Evidence | DESNZ/CEPA/GHD May2025 sections2.3–2.4: five-year refurbishment archetype£81/kW; transfer to ageing fleet is an estimate.
Source URL | https://www.gov.uk/government/publications/electricity-generation-cost-study-extending-the-life-of-existing-generation-assets
Capital treatment | Original inherited gas recovery is complete before estimated40year retirement. Extension charges refurbishment, existing plus extra O&M and fuel.
Coal roles | Up to4GW regular commitment through2044; remaining coal economically scheduled. Allreserve from2045. Six-coal case adds2039/2040.
Delivery | Slow case:2CCGT/year,5year lead;1.5GW engines/year;0.9GW OCGT/year;4.24GW shared ceiling. These are analyst scenarios.
Reliability | All-screen pass requires all7normal and2synthetic stress profiles. Failed cases are not equal-service cost comparisons.
Scope | Connected-security mode only. Gas supply remains unsecured. Some planned CCGTs are deferred beyond2050. No discretionary orders before2029.
Sizing | Bounded heuristic candidates, including lowerCCGT counts. No global cost minimum or engineering-certified life extension is claimed.

## Delivery annual
Connected hourly results by delivery case and year
Seven normal-weather profiles averaged for costs; worst normal percentage and two synthetic stresses reported separately.
Case | Year | Gas GW | Retained gas GW | CCGT GW | Engine GW | OCGT GW | Coal GW | Gas output TWh | Coal output TWh | Net cost £bn | Normal pass | Stress pass | Normal shortfall % | Stress shortage TWh | Peak gas TWh/day | Refurb cash £bn | New-build cash £bn | Refurb recovery £bn | Emissions Mt | All-screen pass
Retention: Proposed / low | 2030 | 34.4879 | 0 | 34.4879 | 0 | 0 | 0 | 82.6324 | 0 | 40.1393 | FALSE | FALSE | 0.025082 | 1.8917 | 1.2586 | 0 | 15.8728 | 0 | 34.6485
Retention: Proposed / low | 2031 | 34.6918 | 0 | 33.1918 | 1.5 | 0 | 0 | 81.3093 | 0 | 41.4207 | FALSE | FALSE | 0.033965 | 6.0263 | 1.3055 | 0.11606 | 12.8057 | 0 | 34.0642
Retention: Proposed / low | 2032 | 36.9191 | 0.46425 | 33.0191 | 3 | 0.9 | 0 | 78.9241 | 0 | 43.2008 | FALSE | FALSE | 0.02193 | 1.2264 | 1.3831 | 0.13406 | 7.9611 | 0.027026 | 33.1197
Retention: Proposed / low | 2033 | 39.0294 | 1.0005 | 32.7294 | 4.5 | 1.8 | 0 | 80.3005 | 0 | 43.3108 | FALSE | FALSE | 0.02063 | 1.0839 | 1.4951 | 0 | 8.9499 | 0.058244 | 33.6076
Retention: Proposed / low | 2034 | 42.99 | 1.0005 | 34.29 | 6 | 2.7 | 0 | 81.8492 | 0 | 43.6875 | FALSE | FALSE | 0.013895 | 3.7705 | 1.7012 | 0.27937 | 8.9499 | 0.058244 | 34.1603
Retention: Proposed / low | 2035 | 46.7409 | 2.118 | 35.6409 | 7.5 | 3.6 | 2 | 70.9571 | 14.9037 | 44.3088 | FALSE | FALSE | 5.9259e-16 | 1.9451 | 1.8628 | 0.396 | 7.9497 | 0.1233 | 42.3013
Retention: Proposed / low | 2036 | 50.3962 | 3.5859 | 36.8962 | 9 | 4.5 | 4 | 65.6136 | 29.8073 | 44.8341 | TRUE | FALSE | 5.991e-16 | 1.1179 | 2.0166 | 0.45262 | 9.1995 | 0.21551 | 52.704
Retention: Proposed / low | 2037 | 53.9848 | 4.9142 | 38.0848 | 10.5 | 5.4 | 6 | 58.1345 | 32.0288 | 45.703 | TRUE | FALSE | 5.2913e-16 | 0.37927 | 2.1199 | 0.56531 | 9.5345 | 0.29388 | 52.0485
Retention: Proposed / low | 2038 | 57.7516 | 6.7732 | 39.4516 | 12 | 6.3 | 8 | 53.6409 | 32.7759 | 46.5625 | TRUE | FALSE | 5.3479e-16 | 0.035825 | 2.2114 | 0.3135 | 12.1168 | 0.39431 | 50.8374
Retention: Proposed / low | 2039 | 60.6021 | 7.7479 | 40.4021 | 13 | 7.2 | 8 | 42.709 | 35.9432 | 47.2634 | TRUE | TRUE | 3.4732e-16 | 1.8474e-15 | 2.1914 | 0.735 | 13.7393 | 0.46731 | 49.5959
Retention: Proposed / low | 2040 | 62.5349 | 9.4537 | 41.7349 | 13 | 7.8 | 8 | 38.1934 | 36.1804 | 47.3228 | TRUE | TRUE | 3.5559e-16 | 1.9327e-15 | 2.248 | 0.47475 | 15.2543 | 0.5734 | 47.8679
Retention: Proposed / low | 2041 | 64.2581 | 9.8282 | 43.4581 | 13 | 7.8 | 8 | 30.5131 | 36.1269 | 47.6755 | TRUE | TRUE | 3.9474e-16 | 2.0819e-15 | 2.2582 | 0.48656 | 16.1543 | 0.59174 | 44.5771
Retention: Proposed / low | 2042 | 65.4291 | 9.8692 | 44.6291 | 13 | 7.8 | 8 | 19.8174 | 35.773 | 47.756 | TRUE | TRUE | 4.8332e-16 | 2.6503e-15 | 2.2233 | 0.43125 | 16.1543 | 0.59965 | 39.7633
Retention: Proposed / low | 2043 | 66.6725 | 9.4507 | 45.8725 | 13 | 7.8 | 8 | 13.6825 | 33.7863 | 47.6284 | TRUE | TRUE | 4.1664e-16 | 2.4727e-15 | 2.1746 | 0.49162 | 16.1543 | 0.56843 | 35.1096
Retention: Proposed / low | 2044 | 68.311 | 10.0211 | 47.511 | 13 | 7.8 | 8 | 12.8538 | 33.4898 | 48.4401 | TRUE | TRUE | 4.5903e-16 | 3.1335e-15 | 2.1717 | 0.45563 | 14.9343 | 0.60991 | 34.5088
Retention: Proposed / low | 2045 | 69.5074 | 9.2805 | 48.5074 | 13.2 | 7.8 | 8 | 22.0978 | 0 | 48.0316 | TRUE | TRUE | 5.0017e-16 | 3.6664e-15 | 2.2322 | 0.07875 | 11.435 | 0.54485 | 9.0642
Retention: Proposed / low | 2046 | 69.6921 | 7.6252 | 48.6921 | 13.2 | 7.8 | 8 | 19.3625 | 0 | 49.0634 | TRUE | TRUE | 3.9648e-16 | 2.8422e-15 | 2.187 | 0.15 | 8.735 | 0.45264 | 7.9681
Retention: Proposed / low | 2047 | 70.3359 | 6.429 | 49.3359 | 13.2 | 7.8 | 8 | 17.0834 | 0 | 49.7491 | TRUE | TRUE | 3.156e-16 | 2.1103e-15 | 2.2015 | 0 | 4.6965 | 0.37427 | 7.0601
Retention: Proposed / low | 2048 | 70.1044 | 4.5259 | 49.1044 | 13.2 | 7.8 | 8 | 16.7753 | 0 | 50.0173 | TRUE | TRUE | 2.946e-16 | 2.3164e-15 | 2.1902 | 0.3465 | 2.0079 | 0.27384 | 6.9376
Retention: Proposed / low | 2049 | 69.2206 | 4.1235 | 48.2206 | 13.2 | 7.8 | 8 | 19.0825 | 0 | 49.5509 | TRUE | TRUE | 3.4213e-16 | 2.7853e-15 | 2.1826 | 0.67181 | 1.3386 | 0.24005 | 7.8633
Retention: Proposed / low | 2050 | 69.0141 | 4.9882 | 48.0141 | 13.2 | 7.8 | 8 | 20.4016 | 0 | 49.6002 | TRUE | TRUE | 3.8659e-16 | 3.2188e-15 | 2.2093 | 0 | 0 | 0.29039 | 8.3939
Faster: Proposed / low | 2030 | 34.4879 | 0 | 34.4879 | 0 | 0 | 0 | 82.6324 | 0 | 40.1393 | FALSE | FALSE | 0.025082 | 1.8917 | 1.2586 | 0 | 17.8013 | 0 | 34.6485
Faster: Proposed / low | 2031 | 37.1918 | 0 | 33.1918 | 4 | 0 | 0 | 81.4072 | 0 | 41.5665 | FALSE | FALSE | 0.02305 | 4.8333 | 1.4159 | 0.069638 | 15.0377 | 0 | 34.1203
Faster: Proposed / low | 2032 | 41.0191 | 0.46425 | 33.0191 | 8 | 0 | 0 | 79.0338 | 0 | 43.4084 | FALSE | FALSE | 0.0083447 | 0.32769 | 1.5639 | 0.080437 | 10.664 | 0.016216 | 33.1867
Faster: Proposed / low | 2033 | 48.0094 | 1.0005 | 36.4094 | 11.6 | 0 | 0 | 80.5 | 0 | 43.8369 | TRUE | FALSE | 7.747e-16 | 0.028064 | 1.7466 | 0 | 11.2142 | 0.034947 | 33.7004
Faster: Proposed / low | 2034 | 55.01 | 1.0005 | 39.81 | 15.2 | 0 | 0 | 82.0234 | 0 | 44.4038 | TRUE | FALSE | 9.61e-16 | 0.48369 | 2.172 | 0.16762 | 11.2142 | 0.034947 | 34.2232
Faster: Proposed / low | 2035 | 61.8009 | 2.118 | 43.0009 | 18.8 | 0 | 2 | 71.0355 | 14.9037 | 45.1881 | TRUE | FALSE | 6.0211e-16 | 0.0012667 | 2.2772 | 0.2376 | 7.2893 | 0.07398 | 42.3156
Faster: Proposed / low | 2036 | 65.0123 | 3.702 | 46.2123 | 18.8 | 0 | 4 | 65.6486 | 29.8073 | 45.6547 | TRUE | TRUE | 5.917e-16 | 3.0802e-15 | 2.2585 | 0.20194 | 7.6619 | 0.12931 | 52.6947
Faster: Proposed / low | 2037 | 67.5946 | 4.584 | 48.7946 | 18.8 | 0 | 6 | 58.1471 | 32.0285 | 46.4403 | TRUE | TRUE | 5.3271e-16 | 1.9469e-15 | 2.1876 | 0.25875 | 7.4121 | 0.16011 | 52.0312
Faster: Proposed / low | 2038 | 68.2911 | 5.7728 | 49.4911 | 18.8 | 0 | 8 | 53.6458 | 32.7757 | 47.0556 | TRUE | TRUE | 5.2606e-16 | 1.8723e-15 | 2.115 | 0.1881 | 10.1696 | 0.20164 | 50.8118
Faster: Proposed / low | 2039 | 68.601 | 7.0268 | 49.801 | 18.8 | 0 | 8 | 42.7101 | 35.9432 | 47.5271 | TRUE | TRUE | 3.4054e-16 | 1.7764e-15 | 2.1051 | 0.27337 | 12.5772 | 0.24544 | 49.578
Faster: Proposed / low | 2040 | 68.9329 | 7.7317 | 50.1329 | 18.8 | 0 | 8 | 38.1943 | 36.1804 | 47.417 | TRUE | TRUE | 3.5723e-16 | 1.8829e-15 | 2.1512 | 0.04725 | 14.0848 | 0.27006 | 47.8435
Faster: Proposed / low | 2041 | 68.0926 | 6.4628 | 49.2926 | 18.8 | 0 | 8 | 30.5135 | 36.1269 | 47.5861 | TRUE | TRUE | 3.9158e-16 | 2.0677e-15 | 2.1816 | 0.09 | 14.9848 | 0.22574 | 44.5544
Faster: Proposed / low | 2042 | 66.6364 | 5.7165 | 47.8364 | 18.8 | 0 | 8 | 19.8179 | 35.773 | 47.465 | TRUE | TRUE | 4.9709e-16 | 2.7072e-15 | 2.1579 | 0 | 15.8619 | 0.19967 | 39.7445
Faster: Proposed / low | 2043 | 65.6532 | 3.9915 | 46.8532 | 18.8 | 0 | 8 | 14.2718 | 33.0571 | 47.2053 | TRUE | TRUE | 4.5235e-16 | 2.5437e-15 | 2.1119 | 0.10687 | 15.5696 | 0.13942 | 34.5836
Faster: Proposed / low | 2044 | 65.2599 | 3.45 | 46.4599 | 18.8 | 0 | 8 | 12.8538 | 33.4898 | 47.8435 | TRUE | TRUE | 4.5758e-16 | 3.1335e-15 | 2.0867 | 0 | 15.5522 | 0.12051 | 34.4948
Faster: Proposed / low | 2045 | 68.5944 | 1.6275 | 47.2944 | 21.3 | 0 | 8 | 22.0979 | 0 | 47.615 | TRUE | TRUE | 5.058e-16 | 3.6735e-15 | 2.1814 | 0 | 9.9 | 0.056847 | 9.0395
Faster: Proposed / low | 2046 | 68.2794 | 1.3125 | 46.9794 | 21.3 | 0 | 8 | 19.3624 | 0 | 48.6311 | TRUE | TRUE | 3.9372e-16 | 2.8422e-15 | 2.1315 | 0 | 7.2 | 0.045844 | 7.9543
Faster: Proposed / low | 2047 | 67.6794 | 0.7125 | 46.3794 | 21.3 | 0 | 8 | 17.0833 | 0 | 49.2564 | TRUE | TRUE | 3.156e-16 | 2.1245e-15 | 2.1079 | 0 | 4.1848 | 0.024887 | 7.0525
Faster: Proposed / low | 2048 | 67.511 | 0.7125 | 46.211 | 21.3 | 0 | 8 | 16.7752 | 0 | 49.5425 | TRUE | TRUE | 2.946e-16 | 2.3306e-15 | 2.095 | 0.10103 | 2.3248 | 0.024887 | 6.9324
Faster: Proposed / low | 2049 | 66.6706 | 0.6735 | 44.7706 | 21.9 | 0 | 8 | 19.0821 | 0 | 49.086 | TRUE | TRUE | 3.4472e-16 | 2.7711e-15 | 2.1283 | 0.40309 | 1.4848 | 0.023525 | 7.8559
Faster: Proposed / low | 2050 | 68.2866 | 3.3607 | 46.3866 | 21.9 | 0 | 8 | 20.4014 | 0 | 49.2243 | TRUE | TRUE | 3.8659e-16 | 3.2045e-15 | 2.1732 | 0 | 0 | 0.11739 | 8.3872
Retention: Proposed / high | 2030 | 34.4879 | 0 | 34.4879 | 0 | 0 | 0 | 84.8499 | 0 | 40.5162 | FALSE | FALSE | 0.043693 | 3.0869 | 1.264 | 0 | 15.8728 | 0 | 35.3569
Retention: Proposed / high | 2031 | 34.6918 | 0 | 33.1918 | 1.5 | 0 | 0 | 84.595 | 0 | 41.9481 | FALSE | FALSE | 0.070006 | 7.9541 | 1.3128 | 0.11606 | 12.8057 | 0 | 35.1197
Retention: Proposed / high | 2032 | 36.9191 | 0.46425 | 33.0191 | 3 | 0.9 | 0 | 83.4658 | 0 | 43.8809 | FALSE | FALSE | 0.05901 | 3.465 | 1.4051 | 0.13406 | 7.9611 | 0.027026 | 34.6122
Retention: Proposed / high | 2033 | 39.0294 | 1.0005 | 32.7294 | 4.5 | 1.8 | 0 | 87.3225 | 0 | 44.2513 | FALSE | FALSE | 0.081207 | 8.0613 | 1.5541 | 0 | 8.9499 | 0.058244 | 35.9563
Retention: Proposed / high | 2034 | 42.99 | 1.0005 | 34.29 | 6 | 2.7 | 0 | 92.3399 | 0 | 44.9568 | FALSE | FALSE | 0.070637 | 7.9744 | 1.7417 | 0.27937 | 8.9499 | 0.058244 | 37.7224
Retention: Proposed / high | 2035 | 46.7409 | 2.118 | 35.6409 | 7.5 | 3.6 | 2 | 84.5257 | 14.9037 | 45.9248 | FALSE | FALSE | 0.03032 | 6.6596 | 1.9001 | 0.396 | 7.9497 | 0.1233 | 47.0481
Retention: Proposed / high | 2036 | 50.3962 | 3.5859 | 36.8962 | 9 | 4.5 | 4 | 85.4824 | 29.8073 | 47.0563 | FALSE | FALSE | 0.032475 | 6.9545 | 2.0724 | 0.45262 | 9.1995 | 0.21551 | 59.7899
Retention: Proposed / high | 2037 | 53.9848 | 4.9142 | 38.0848 | 10.5 | 5.4 | 6 | 84.114 | 36.3056 | 48.8097 | FALSE | FALSE | 0.026604 | 6.9205 | 2.2474 | 0.56531 | 9.5345 | 0.29388 | 65.0838
Retention: Proposed / high | 2038 | 57.7516 | 6.7732 | 39.4516 | 12 | 6.3 | 8 | 82.4363 | 44.3864 | 50.4205 | FALSE | FALSE | 0.021988 | 6.4098 | 2.414 | 0.3135 | 12.5843 | 0.39431 | 71.5995
Retention: Proposed / high | 2039 | 61.1021 | 7.7479 | 40.4021 | 13.5 | 7.2 | 8 | 81.8189 | 45.0531 | 51.8129 | FALSE | FALSE | 0.021411 | 6.2758 | 2.5658 | 0.735 | 15.2843 | 0.46731 | 71.7439
Retention: Proposed / high | 2040 | 64.8349 | 9.4537 | 41.7349 | 15 | 8.1 | 8 | 94.8451 | 39.4851 | 52.9306 | FALSE | FALSE | 0.024798 | 6.6536 | 2.741 | 0.47475 | 17.0843 | 0.5734 | 71.3066
Retention: Proposed / high | 2041 | 68.9581 | 9.8282 | 43.4581 | 16.5 | 9 | 8 | 95.6098 | 39.8583 | 54.0954 | FALSE | FALSE | 0.018066 | 5.945 | 2.9247 | 0.48656 | 17.9843 | 0.59174 | 71.6616
Retention: Proposed / high | 2042 | 72.5291 | 9.8692 | 44.6291 | 18 | 9.9 | 8 | 91.2256 | 42.6606 | 55.0341 | FALSE | FALSE | 0.011315 | 5.5471 | 3.0918 | 0.43125 | 17.9843 | 0.59965 | 72.1659
Retention: Proposed / high | 2043 | 76.1725 | 9.4507 | 45.8725 | 19.5 | 10.8 | 8 | 88.5785 | 42.6461 | 55.5009 | FALSE | FALSE | 0.0071333 | 4.7161 | 3.265 | 0.49162 | 17.9843 | 0.56843 | 70.9508
Retention: Proposed / high | 2044 | 80.211 | 10.0211 | 47.511 | 21 | 11.7 | 8 | 84.0627 | 44.8989 | 56.3988 | FALSE | FALSE | 0.0023386 | 3.6595 | 3.4093 | 0.45563 | 17.9843 | 0.60991 | 71.3457
Retention: Proposed / high | 2045 | 83.6074 | 9.2805 | 48.5074 | 22.5 | 12.6 | 8 | 115.2728 | 0.22699 | 56.9373 | FALSE | FALSE | 3.6045e-15 | 3.1511 | 3.4411 | 0.07875 | 17.9843 | 0.54485 | 44.2572
Retention: Proposed / high | 2046 | 86.1921 | 7.6252 | 48.6921 | 24 | 13.5 | 8 | 107.7605 | 0.12204 | 57.8709 | TRUE | FALSE | 3.0986e-15 | 2.2375 | 3.5048 | 0.15 | 17.9843 | 0.45264 | 41.3136
Retention: Proposed / high | 2047 | 89.2359 | 6.429 | 49.3359 | 25.5 | 14.4 | 8 | 102.5711 | 0.057338 | 58.6064 | TRUE | FALSE | 2.7815e-15 | 1.4077 | 3.5959 | 0 | 14.3843 | 0.37427 | 39.2531
Retention: Proposed / high | 2048 | 91.4044 | 4.5259 | 49.1044 | 27 | 15.3 | 8 | 97.1472 | 0.021821 | 59.2621 | TRUE | FALSE | 2.6561e-15 | 0.80228 | 3.6579 | 0.3465 | 10.7843 | 0.27384 | 37.1281
Retention: Proposed / high | 2049 | 93.8406 | 4.1235 | 49.1406 | 28.5 | 16.2 | 8 | 90.774 | 0.0029314 | 59.6375 | TRUE | FALSE | 2.3782e-15 | 0.34629 | 3.702 | 0.67181 | 6.7568 | 0.24005 | 34.7868
Retention: Proposed / high | 2050 | 96.0341 | 4.9882 | 48.9341 | 30 | 17.1 | 8 | 81.9137 | 0 | 60.1524 | TRUE | FALSE | 2.1486e-15 | 0.13848 | 3.7283 | 0 | 1.7543 | 0.29039 | 31.5728
Faster: Proposed / high | 2030 | 34.4879 | 0 | 34.4879 | 0 | 0 | 0 | 84.8499 | 0 | 40.5162 | FALSE | FALSE | 0.043693 | 3.0869 | 1.264 | 0 | 17.8013 | 0 | 35.3569
Faster: Proposed / high | 2031 | 37.1918 | 0 | 33.1918 | 4 | 0 | 0 | 84.7766 | 0 | 42.0977 | FALSE | FALSE | 0.038348 | 6.659 | 1.4386 | 0.069638 | 15.0377 | 0 | 35.2122
Faster: Proposed / high | 2032 | 41.0191 | 0.46425 | 33.0191 | 8 | 0 | 0 | 83.664 | 0 | 44.0937 | FALSE | FALSE | 0.020424 | 1.65 | 1.589 | 0.080437 | 10.664 | 0.016216 | 34.7216
Faster: Proposed / high | 2033 | 48.0094 | 1.0005 | 36.4094 | 11.6 | 0 | 0 | 87.7233 | 0 | 44.7852 | FALSE | FALSE | 0.011131 | 3.8997 | 1.9118 | 0 | 11.2142 | 0.034947 | 36.1428
Faster: Proposed / high | 2034 | 55.01 | 1.0005 | 39.81 | 15.2 | 0 | 0 | 92.7689 | 0 | 45.6759 | FALSE | FALSE | 0.0030931 | 2.7418 | 2.211 | 0.16762 | 11.2142 | 0.034947 | 37.8924
Faster: Proposed / high | 2035 | 61.8009 | 2.118 | 43.0009 | 18.8 | 0 | 2 | 84.8565 | 14.9037 | 46.795 | TRUE | FALSE | 1.7263e-15 | 1.1585 | 2.4849 | 0.2376 | 10.214 | 0.07398 | 47.1352
Faster: Proposed / high | 2036 | 68.6123 | 3.702 | 46.2123 | 22.4 | 0 | 4 | 85.8399 | 29.8073 | 48.0694 | TRUE | FALSE | 2.2335e-15 | 0.8477 | 2.7611 | 0.20194 | 11.4639 | 0.12931 | 59.8328
Faster: Proposed / high | 2037 | 74.7946 | 4.584 | 48.7946 | 26 | 0 | 6 | 84.4787 | 36.3056 | 49.9393 | TRUE | FALSE | 1.8758e-15 | 0.51994 | 2.9879 | 0.25875 | 11.7988 | 0.16011 | 65.0762
Faster: Proposed / high | 2038 | 80.9311 | 5.7728 | 51.3311 | 29.6 | 0 | 8 | 82.7985 | 44.3862 | 51.6477 | TRUE | FALSE | 2.6448e-15 | 0.24458 | 3.1719 | 0.1881 | 14.8487 | 0.20164 | 71.5385
Faster: Proposed / high | 2039 | 87.601 | 7.0268 | 54.401 | 33.2 | 0 | 8 | 82.1739 | 45.053 | 53.1943 | TRUE | FALSE | 2.9067e-15 | 0.080162 | 3.3742 | 0.27337 | 17.5487 | 0.24544 | 71.6113
Faster: Proposed / high | 2040 | 93.3729 | 7.7317 | 56.5729 | 36.8 | 0 | 8 | 88.3241 | 46.4598 | 54.2769 | TRUE | FALSE | 2.7433e-15 | 0.064952 | 3.5866 | 0.04725 | 19.3487 | 0.27006 | 74.7793
Faster: Proposed / high | 2041 | 98.8926 | 6.4628 | 58.4926 | 40.4 | 0 | 8 | 88.5838 | 47.1493 | 55.5025 | TRUE | FALSE | 2.9479e-15 | 0.0019733 | 3.7063 | 0.09 | 20.2487 | 0.22574 | 75.1291
Faster: Proposed / high | 2042 | 104.7164 | 5.7165 | 60.7164 | 44 | 0 | 8 | 86.3925 | 47.6506 | 56.6047 | TRUE | FALSE | 3.0306e-15 | 2.1846e-13 | 3.9663 | 0 | 18.4937 | 0.19967 | 74.3665
Faster: Proposed / high | 2043 | 107.3932 | 3.9915 | 62.4932 | 44.9 | 0 | 8 | 83.9406 | 47.6631 | 57.0656 | TRUE | TRUE | 2.9825e-15 | 2.0022e-13 | 3.9039 | 0.10687 | 17.0315 | 0.13942 | 73.2739
Faster: Proposed / high | 2044 | 109.7599 | 3.45 | 64.8599 | 44.9 | 0 | 8 | 81.8287 | 47.3612 | 57.8927 | TRUE | TRUE | 3.4853e-15 | 1.4008e-13 | 3.8767 | 0 | 15.8619 | 0.12051 | 72.3295
Faster: Proposed / high | 2045 | 111.5144 | 1.6275 | 66.6144 | 44.9 | 0 | 8 | 115.5417 | 0 | 58.4046 | TRUE | TRUE | 3.5211e-15 | 4.8331e-14 | 3.9011 | 0 | 14.6924 | 0.056847 | 43.5201
Faster: Proposed / high | 2046 | 112.1194 | 1.3125 | 67.2194 | 44.9 | 0 | 8 | 107.9196 | 0 | 59.2519 | TRUE | TRUE | 3.1043e-15 | 3.9613e-14 | 3.8734 | 0 | 14.4 | 0.045844 | 40.7661
Faster: Proposed / high | 2047 | 111.5194 | 0.7125 | 66.6194 | 44.9 | 0 | 8 | 102.6594 | 0 | 59.7814 | TRUE | TRUE | 2.7834e-15 | 3.8078e-14 | 3.8421 | 0 | 11.0924 | 0.024887 | 38.8364
Faster: Proposed / high | 2048 | 111.351 | 0.7125 | 66.451 | 44.9 | 0 | 8 | 97.1995 | 0 | 60.3089 | TRUE | TRUE | 2.6542e-15 | 2.9495e-14 | 3.8175 | 0.10103 | 7.4924 | 0.024887 | 36.8102
Faster: Proposed / high | 2049 | 109.9106 | 0.6735 | 65.0106 | 44.9 | 0 | 8 | 90.8079 | 0 | 60.4368 | TRUE | TRUE | 2.38e-15 | 2.8926e-14 | 3.755 | 0.40309 | 3.8924 | 0.023525 | 34.5232
Faster: Proposed / high | 2050 | 110.6066 | 3.3607 | 65.7066 | 44.9 | 0 | 8 | 81.9464 | 0 | 60.8174 | TRUE | TRUE | 2.1541e-15 | 2.1934e-14 | 3.7361 | 0 | 0 | 0.11739 | 31.3355
Retention: Renewables / low | 2030 | 34.4879 | 0 | 34.4879 | 0 | 0 | 0 | 82.6324 | 0 | 40.1393 | FALSE | FALSE | 0.025082 | 1.8917 | 1.2586 | 0 | 15.2373 | 0 | 34.6485
Retention: Renewables / low | 2031 | 34.6918 | 0 | 33.1918 | 1.5 | 0 | 0 | 81.1294 | 0 | 41.5355 | FALSE | FALSE | 0.033109 | 5.9904 | 1.3055 | 0.11606 | 16.62 | 0 | 34.0054
Retention: Renewables / low | 2032 | 36.9191 | 0.46425 | 33.0191 | 3 | 0.9 | 0 | 78.6117 | 0 | 43.4383 | FALSE | FALSE | 0.021405 | 1.2002 | 1.3828 | 0.13406 | 14.6657 | 0.027026 | 33.0167
Retention: Renewables / low | 2033 | 39.0294 | 1.0005 | 32.7294 | 4.5 | 1.8 | 0 | 79.7557 | 0 | 43.6658 | FALSE | FALSE | 0.019834 | 1.0571 | 1.4913 | 0 | 16.9524 | 0.058244 | 33.4262
Retention: Renewables / low | 2034 | 42.99 | 1.0005 | 34.29 | 6 | 2.7 | 0 | 79.9946 | 0 | 45.3368 | FALSE | FALSE | 0.011452 | 0.48608 | 1.6628 | 0.27937 | 13.4048 | 0.058244 | 33.5373
Retention: Renewables / low | 2035 | 46.7409 | 2.118 | 35.6409 | 7.5 | 3.6 | 0 | 75.2554 | 0 | 46.5957 | FALSE | FALSE | 0.0018835 | 0.093179 | 1.7913 | 0.396 | 12.8577 | 0.1233 | 31.5674
Retention: Renewables / low | 2036 | 50.3962 | 3.5859 | 36.8962 | 9 | 4.5 | 0 | 76.0754 | 0 | 47.4589 | TRUE | FALSE | 6.518e-16 | 0.042297 | 1.8927 | 0.45262 | 14.0231 | 0.21551 | 31.8697
Retention: Renewables / low | 2037 | 53.9848 | 4.9142 | 38.0848 | 10.5 | 5.4 | 0 | 76.9092 | 0 | 48.2705 | TRUE | FALSE | 7.3629e-16 | 0.022976 | 2.0223 | 0.56531 | 13.9739 | 0.29388 | 32.1742
Retention: Renewables / low | 2038 | 57.0516 | 6.7732 | 39.4516 | 11.3 | 6.3 | 0 | 71.7772 | 0 | 49.7323 | TRUE | TRUE | 5.9498e-16 | 3.1761e-15 | 2.0944 | 0.3135 | 13.4035 | 0.39431 | 30.0476
Retention: Renewables / low | 2039 | 58.0021 | 7.7479 | 40.4021 | 11.3 | 6.3 | 0 | 66.7295 | 0 | 50.8986 | TRUE | TRUE | 4.6252e-16 | 2.931e-15 | 2.1029 | 0.735 | 15.7896 | 0.46731 | 27.9292
Retention: Renewables / low | 2040 | 60.1349 | 9.4537 | 41.7349 | 11.5 | 6.9 | 0 | 68.1534 | 0 | 51.6989 | TRUE | TRUE | 4.7357e-16 | 2.8813e-15 | 2.2266 | 0.47475 | 17.403 | 0.5734 | 28.4617
Retention: Renewables / low | 2041 | 63.4581 | 9.8282 | 43.4581 | 12.5 | 7.5 | 0 | 69.5062 | 0 | 52.9831 | TRUE | TRUE | 5.2974e-16 | 3.0909e-15 | 2.3409 | 0.48656 | 16.4013 | 0.59174 | 28.9623
Retention: Renewables / low | 2042 | 65.7291 | 9.8692 | 44.6291 | 13.3 | 7.8 | 0 | 70.9987 | 0 | 53.7441 | TRUE | TRUE | 5.5521e-16 | 3.3538e-15 | 2.456 | 0.43125 | 21.614 | 0.59965 | 29.5199
Retention: Renewables / low | 2043 | 66.9725 | 9.4507 | 45.8725 | 13.3 | 7.8 | 0 | 71.8896 | 0 | 54.7858 | TRUE | TRUE | 5.9817e-16 | 3.2578e-15 | 2.5423 | 0.49162 | 12.8852 | 0.56843 | 29.8519
Retention: Renewables / low | 2044 | 69.911 | 10.0211 | 47.511 | 14 | 8.4 | 0 | 74.1544 | 0 | 55.2691 | TRUE | TRUE | 6.7913e-16 | 3.8227e-15 | 2.662 | 0.45563 | 22.5609 | 0.60991 | 30.681
Retention: Renewables / low | 2045 | 70.9074 | 9.2805 | 48.5074 | 14 | 8.4 | 0 | 75.4375 | 0 | 56.2139 | TRUE | TRUE | 7.5659e-16 | 4.1567e-15 | 2.7493 | 0.07875 | 12.678 | 0.54485 | 31.141
Retention: Renewables / low | 2046 | 72.2921 | 7.6252 | 48.6921 | 14.9 | 8.7 | 0 | 76.9269 | 0 | 56.8751 | TRUE | TRUE | 8.4527e-16 | 4.3698e-15 | 2.8287 | 0.15 | 14.6079 | 0.45264 | 31.6678
Retention: Renewables / low | 2047 | 73.6359 | 6.429 | 49.3359 | 15.3 | 9 | 0 | 77.9134 | 0 | 57.5746 | TRUE | TRUE | 9.4005e-16 | 4.6612e-15 | 2.8891 | 0 | 14.2407 | 0.37427 | 32.0194
Retention: Renewables / low | 2048 | 74.9044 | 4.5259 | 49.1044 | 16.2 | 9.6 | 0 | 79.0281 | 0 | 58.1212 | TRUE | TRUE | 9.1947e-16 | 4.6469e-15 | 2.9624 | 0.3465 | 11.637 | 0.27384 | 32.4178
Retention: Renewables / low | 2049 | 76.4406 | 4.1235 | 49.1406 | 17.1 | 10.2 | 0 | 79.7675 | 0 | 58.617 | TRUE | TRUE | 9.4087e-16 | 4.8814e-15 | 3.0364 | 0.67181 | 9.1136 | 0.24005 | 32.6965
Retention: Renewables / low | 2050 | 77.9341 | 4.9882 | 48.9341 | 18.2 | 10.8 | 0 | 80.59 | 0 | 59.1553 | TRUE | TRUE | 9.2704e-16 | 4.8956e-15 | 3.1195 | 0 | 1.7543 | 0.29039 | 33.0228
Faster: Renewables / low | 2030 | 34.4879 | 0 | 34.4879 | 0 | 0 | 0 | 82.6324 | 0 | 40.1393 | FALSE | FALSE | 0.025082 | 1.8917 | 1.2586 | 0 | 17.1657 | 0 | 34.6485
Faster: Renewables / low | 2031 | 37.1918 | 0 | 33.1918 | 4 | 0 | 0 | 81.2263 | 0 | 41.6813 | FALSE | FALSE | 0.022781 | 4.8075 | 1.4158 | 0.069638 | 18.852 | 0 | 34.0605
Faster: Renewables / low | 2032 | 41.0191 | 0.46425 | 33.0191 | 8 | 0 | 0 | 78.7137 | 0 | 43.6456 | FALSE | FALSE | 0.0078407 | 0.31461 | 1.5638 | 0.080437 | 17.3686 | 0.016216 | 33.0799
Faster: Renewables / low | 2033 | 48.0094 | 1.0005 | 36.4094 | 11.6 | 0 | 0 | 79.9439 | 0 | 44.1919 | TRUE | FALSE | 6.9894e-16 | 0.026981 | 1.74 | 0 | 17.5593 | 0.034947 | 33.5134
Faster: Renewables / low | 2034 | 52.91 | 1.0005 | 39.81 | 13.1 | 0 | 0 | 80.1316 | 0 | 45.9322 | TRUE | TRUE | 6.7172e-16 | 3.5207e-15 | 1.8809 | 0.16762 | 12.7443 | 0.034947 | 33.5831
Faster: Renewables / low | 2035 | 56.1009 | 2.118 | 43.0009 | 13.1 | 0 | 0 | 75.3316 | 0 | 47.1445 | TRUE | TRUE | 5.783e-16 | 3.2117e-15 | 1.887 | 0.2376 | 11.9049 | 0.07398 | 31.5807
Faster: Renewables / low | 2036 | 58.3923 | 3.702 | 45.2923 | 13.1 | 0 | 0 | 76.1262 | 0 | 47.8772 | TRUE | TRUE | 6.5735e-16 | 3.5705e-15 | 1.956 | 0.20194 | 12.7779 | 0.12931 | 31.8634
Faster: Renewables / low | 2037 | 60.0546 | 4.584 | 46.9546 | 13.1 | 0 | 0 | 76.9421 | 0 | 48.5338 | TRUE | TRUE | 7.4347e-16 | 3.8973e-15 | 2.0202 | 0.25875 | 13.9036 | 0.16011 | 32.1519
Faster: Renewables / low | 2038 | 61.6711 | 5.7728 | 48.5711 | 13.1 | 0 | 0 | 71.7938 | 0 | 49.8635 | TRUE | TRUE | 5.8626e-16 | 3.0838e-15 | 2.0264 | 0.1881 | 13.4109 | 0.20164 | 30.0167
Faster: Renewables / low | 2039 | 62.901 | 7.0268 | 49.801 | 13.1 | 0 | 0 | 66.7435 | 0 | 50.9972 | TRUE | TRUE | 4.6422e-16 | 2.8102e-15 | 2.0429 | 0.27337 | 15.6744 | 0.24544 | 27.8987
Faster: Renewables / low | 2040 | 65.0729 | 7.7317 | 51.9729 | 13.1 | 0 | 0 | 68.1716 | 0 | 51.7569 | TRUE | TRUE | 4.7193e-16 | 2.8173e-15 | 2.1383 | 0.04725 | 15.7407 | 0.27006 | 28.4171
Faster: Renewables / low | 2041 | 64.2326 | 6.4628 | 51.1326 | 13.1 | 0 | 0 | 69.5146 | 0 | 52.7525 | TRUE | TRUE | 5.2658e-16 | 3.0269e-15 | 2.227 | 0.09 | 15.7388 | 0.22574 | 28.9066
Faster: Renewables / low | 2042 | 65.5364 | 5.7165 | 52.4364 | 13.1 | 0 | 0 | 71.0055 | 0 | 53.453 | TRUE | TRUE | 5.4909e-16 | 3.3538e-15 | 2.3239 | 0 | 22.0118 | 0.19967 | 29.4525
Faster: Renewables / low | 2043 | 66.0332 | 3.9915 | 50.5332 | 15.5 | 0 | 0 | 71.8936 | 0 | 54.427 | TRUE | TRUE | 5.952e-16 | 3.2578e-15 | 2.4275 | 0.10687 | 12.7629 | 0.13942 | 29.7824
Faster: Renewables / low | 2044 | 68.8799 | 3.45 | 51.9799 | 16.9 | 0 | 0 | 74.1574 | 0 | 54.8748 | TRUE | TRUE | 6.6755e-16 | 3.8796e-15 | 2.5412 | 0 | 22.8738 | 0.12051 | 30.5998
Faster: Renewables / low | 2045 | 69.4544 | 1.6275 | 50.0544 | 19.4 | 0 | 0 | 75.4373 | 0 | 55.8003 | TRUE | TRUE | 7.5096e-16 | 4.1425e-15 | 2.6444 | 0 | 11.5482 | 0.056847 | 31.0612
Faster: Renewables / low | 2046 | 71.4794 | 1.3125 | 51.5794 | 19.9 | 0 | 0 | 76.9309 | 0 | 56.5405 | TRUE | TRUE | 8.3976e-16 | 4.4054e-15 | 2.7226 | 0 | 14.4083 | 0.045844 | 31.5928
Faster: Renewables / low | 2047 | 72.9794 | 0.7125 | 50.9794 | 22 | 0 | 0 | 77.9165 | 0 | 57.2552 | TRUE | TRUE | 9.1307e-16 | 4.4693e-15 | 2.8001 | 0 | 13.3781 | 0.024887 | 31.9522
Faster: Renewables / low | 2048 | 74.651 | 0.7125 | 52.651 | 22 | 0 | 0 | 79.0353 | 0 | 57.8642 | TRUE | TRUE | 9.089e-16 | 4.6541e-15 | 2.8622 | 0.10103 | 11.4246 | 0.024887 | 32.3553
Faster: Renewables / low | 2049 | 76.0306 | 0.6735 | 52.1306 | 23.9 | 0 | 0 | 79.7725 | 0 | 58.3463 | TRUE | TRUE | 9.4346e-16 | 4.9312e-15 | 2.9344 | 0.40309 | 7.5289 | 0.023525 | 32.6323
Faster: Renewables / low | 2050 | 79.4866 | 3.3607 | 55.5866 | 23.9 | 0 | 0 | 80.6114 | 0 | 59.0047 | TRUE | TRUE | 1.0339e-15 | 1.8066e-14 | 2.9939 | 0 | 0 | 0.11739 | 32.9516
Retention: Renewables / central | 2030 | 34.4879 | 0 | 34.4879 | 0 | 0 | 0 | 83.8047 | 0 | 40.4038 | FALSE | FALSE | 0.026374 | 2.5779 | 1.2636 | 0 | 24.5961 | 0 | 35.007
Retention: Renewables / central | 2031 | 34.6918 | 0 | 33.1918 | 1.5 | 0 | 0 | 82.6055 | 0 | 42.1323 | FALSE | FALSE | 0.035357 | 2.5891 | 1.2838 | 0.11606 | 26.1298 | 0 | 34.4671
Retention: Renewables / central | 2032 | 36.9191 | 0.46425 | 33.0191 | 3 | 0.9 | 0 | 80.6639 | 0 | 44.3628 | FALSE | FALSE | 0.020593 | 2.5403 | 1.3999 | 0.13406 | 26.6919 | 0.027026 | 33.673
Retention: Renewables / central | 2033 | 39.0294 | 1.0005 | 32.7294 | 4.5 | 1.8 | 0 | 81.4797 | 0 | 46.308 | FALSE | FALSE | 0.019138 | 2.6272 | 1.519 | 0 | 24.2932 | 0.058244 | 33.9812
Retention: Renewables / central | 2034 | 42.99 | 1.0005 | 34.29 | 6 | 2.7 | 0 | 82.4663 | 0 | 48.4094 | FALSE | FALSE | 0.013682 | 1.9783 | 1.6948 | 0.27937 | 23.6736 | 0.058244 | 34.3521
Retention: Renewables / central | 2035 | 46.7409 | 2.118 | 35.6409 | 7.5 | 3.6 | 0 | 78.1726 | 0 | 50.6429 | FALSE | FALSE | 0.0057914 | 1.1584 | 1.8637 | 0.396 | 23.4464 | 0.1233 | 32.5503
Retention: Renewables / central | 2036 | 50.3962 | 3.5859 | 36.8962 | 9 | 4.5 | 0 | 80.2545 | 0 | 52.634 | FALSE | FALSE | 0.0061059 | 1.2389 | 2.0374 | 0.45262 | 23.4243 | 0.21551 | 33.3051
Retention: Renewables / central | 2037 | 53.9848 | 4.9142 | 38.0848 | 10.5 | 5.4 | 0 | 82.3738 | 0 | 54.5351 | FALSE | FALSE | 0.0062824 | 1.2925 | 2.208 | 0.56531 | 24.097 | 0.29388 | 34.0797
Retention: Renewables / central | 2038 | 57.7516 | 6.7732 | 39.4516 | 12 | 6.3 | 0 | 78.2267 | 0 | 56.8917 | FALSE | FALSE | 0.0026186 | 0.87078 | 2.3766 | 0.3135 | 21.884 | 0.39431 | 32.3298
Retention: Renewables / central | 2039 | 61.1021 | 7.7479 | 40.4021 | 13.5 | 7.2 | 0 | 73.9484 | 0 | 58.9838 | FALSE | FALSE | 4.8548e-05 | 0.52885 | 2.5191 | 0.735 | 23.5366 | 0.46731 | 30.5179
Retention: Renewables / central | 2040 | 64.8349 | 9.4537 | 41.7349 | 15 | 8.1 | 0 | 76.4111 | 0 | 60.9145 | FALSE | FALSE | 0.00024202 | 0.64002 | 2.7049 | 0.47475 | 20.2299 | 0.5734 | 31.4244
Retention: Renewables / central | 2041 | 68.9581 | 9.8282 | 43.4581 | 16.5 | 9 | 0 | 78.3479 | 0 | 62.3174 | TRUE | FALSE | 9.0958e-16 | 0.40182 | 2.8794 | 0.48656 | 20.9914 | 0.59174 | 32.1307
Retention: Renewables / central | 2042 | 72.5291 | 9.8692 | 44.6291 | 18 | 9.9 | 0 | 80.3952 | 0 | 63.4931 | TRUE | FALSE | 9.7318e-16 | 0.30685 | 3.0397 | 0.43125 | 25.9254 | 0.59965 | 32.8679
Retention: Renewables / central | 2043 | 76.1725 | 9.4507 | 45.8725 | 19.5 | 10.8 | 0 | 81.7775 | 0 | 65.036 | TRUE | FALSE | 9.1753e-16 | 0.19082 | 3.1954 | 0.49162 | 15.8726 | 0.56843 | 33.3552
Retention: Renewables / central | 2044 | 80.211 | 10.0211 | 47.511 | 21 | 11.7 | 0 | 84.4095 | 0 | 65.8262 | TRUE | FALSE | 1.0846e-15 | 0.091461 | 3.3598 | 0.45563 | 26.8044 | 0.60991 | 34.301
Retention: Renewables / central | 2045 | 83.6074 | 9.2805 | 48.5074 | 22.5 | 12.6 | 0 | 86.4203 | 0 | 67.1307 | TRUE | FALSE | 1.2478e-15 | 0.0305 | 3.5071 | 0.07875 | 15.2868 | 0.54485 | 34.977
Retention: Renewables / central | 2046 | 86.1921 | 7.6252 | 48.6921 | 24 | 13.5 | 0 | 88.2869 | 0 | 68.1707 | TRUE | FALSE | 1.2827e-15 | 0.0062247 | 3.6199 | 0.15 | 15.8229 | 0.45264 | 35.5995
Retention: Renewables / central | 2047 | 88.3359 | 6.429 | 49.3359 | 24.6 | 14.4 | 0 | 89.3767 | 0 | 68.9207 | TRUE | TRUE | 1.2641e-15 | 1.6279e-14 | 3.6968 | 0 | 13.9653 | 0.37427 | 35.9614
Retention: Renewables / central | 2048 | 89.5044 | 4.5259 | 49.1044 | 25.4 | 15 | 0 | 90.4044 | 0 | 69.4213 | TRUE | TRUE | 1.2359e-15 | 2.0471e-14 | 3.7608 | 0.3465 | 10.508 | 0.27384 | 36.3117
Retention: Renewables / central | 2049 | 90.9406 | 4.1235 | 49.1406 | 26.2 | 15.6 | 0 | 91.0446 | 0 | 69.8739 | TRUE | TRUE | 1.2046e-15 | 2.8137e-14 | 3.8332 | 0.67181 | 7.7856 | 0.24005 | 36.5401
Retention: Renewables / central | 2050 | 92.1341 | 4.9882 | 48.9341 | 27 | 16.2 | 0 | 91.3756 | 0 | 70.0342 | TRUE | TRUE | 1.2544e-15 | 3.2891e-14 | 3.8976 | 0 | 1.7543 | 0.29039 | 36.7088
Faster: Renewables / central | 2030 | 34.4879 | 0 | 34.4879 | 0 | 0 | 0 | 83.8047 | 0 | 40.4038 | FALSE | FALSE | 0.026374 | 2.5779 | 1.2636 | 0 | 26.5246 | 0 | 35.007
Faster: Renewables / central | 2031 | 37.1918 | 0 | 33.1918 | 4 | 0 | 0 | 82.7109 | 0 | 42.2787 | FALSE | FALSE | 0.020503 | 1.5526 | 1.3966 | 0.069638 | 28.3617 | 0 | 34.5261
Faster: Renewables / central | 2032 | 41.0191 | 0.46425 | 33.0191 | 8 | 0 | 0 | 80.7774 | 0 | 44.5714 | FALSE | FALSE | 0.0080696 | 0.99472 | 1.5853 | 0.080437 | 29.3948 | 0.016216 | 33.7444
Faster: Renewables / central | 2033 | 48.0094 | 1.0005 | 36.4094 | 11.6 | 0 | 0 | 81.6843 | 0 | 46.8343 | TRUE | FALSE | 9.3389e-16 | 0.1561 | 1.8546 | 0 | 26.5575 | 0.034947 | 34.0774
Faster: Renewables / central | 2034 | 55.01 | 1.0005 | 39.81 | 15.2 | 0 | 0 | 82.6608 | 0 | 49.1261 | TRUE | FALSE | 1.0048e-15 | 0.0055388 | 2.0841 | 0.16762 | 23.5979 | 0.034947 | 34.4246
Faster: Renewables / central | 2035 | 58.2009 | 2.118 | 43.0009 | 15.2 | 0 | 0 | 78.3019 | 0 | 51.3115 | TRUE | TRUE | 9.4182e-16 | 4.8246e-15 | 2.1494 | 0.2376 | 23.4358 | 0.07398 | 32.5784
Faster: Renewables / central | 2036 | 61.5123 | 3.702 | 46.2123 | 15.3 | 0 | 0 | 80.3823 | 0 | 53.2476 | TRUE | TRUE | 1.1087e-15 | 5.5849e-15 | 2.3239 | 0.20194 | 24.2586 | 0.12931 | 33.3125
Faster: Renewables / central | 2037 | 65.4946 | 4.584 | 48.7946 | 16.7 | 0 | 0 | 82.5019 | 0 | 55.1434 | TRUE | TRUE | 1.2439e-15 | 6.5583e-15 | 2.4928 | 0.25875 | 24.0213 | 0.16011 | 34.0614
Faster: Renewables / central | 2038 | 68.0311 | 5.7728 | 51.3311 | 16.7 | 0 | 0 | 78.3198 | 0 | 57.3964 | TRUE | TRUE | 1.0897e-15 | 6.132e-15 | 2.5812 | 0.1881 | 21.8083 | 0.20164 | 32.2785
Faster: Renewables / central | 2039 | 71.101 | 7.0268 | 54.401 | 16.7 | 0 | 0 | 74.0247 | 0 | 59.4407 | TRUE | TRUE | 1.0412e-15 | 5.7767e-15 | 2.6419 | 0.27337 | 23.656 | 0.24544 | 30.4486
Faster: Renewables / central | 2040 | 73.5729 | 7.7317 | 56.5729 | 17 | 0 | 0 | 76.4845 | 0 | 61.2471 | TRUE | TRUE | 8.7569e-16 | 5.0377e-15 | 2.8246 | 0.04725 | 20.5769 | 0.27006 | 31.3168
Faster: Renewables / central | 2041 | 76.5926 | 6.4628 | 58.4926 | 18.1 | 0 | 0 | 78.4069 | 0 | 62.5849 | TRUE | TRUE | 9.1445e-16 | 5.3362e-15 | 2.9481 | 0.09 | 20.6559 | 0.22574 | 32.0029
Faster: Renewables / central | 2042 | 79.3164 | 5.7165 | 60.7164 | 18.6 | 0 | 0 | 80.4486 | 0 | 63.7131 | TRUE | TRUE | 9.4369e-16 | 2.1682e-14 | 3.056 | 0 | 24.4854 | 0.19967 | 32.7216
Faster: Renewables / central | 2043 | 80.7732 | 3.9915 | 61.5732 | 19.2 | 0 | 0 | 81.8163 | 0 | 65.1404 | TRUE | TRUE | 9.8847e-16 | 3.2813e-14 | 3.1177 | 0.10687 | 14.5952 | 0.13942 | 33.1986
Faster: Renewables / central | 2044 | 83.5199 | 3.45 | 63.0199 | 20.5 | 0 | 0 | 84.4378 | 0 | 65.8191 | TRUE | TRUE | 1.2434e-15 | 5.1401e-14 | 3.2344 | 0 | 25.3648 | 0.12051 | 34.1225
Faster: Renewables / central | 2045 | 83.9944 | 1.6275 | 61.0944 | 22.9 | 0 | 0 | 86.4376 | 0 | 66.943 | TRUE | TRUE | 1.7028e-15 | 6.7544e-14 | 3.278 | 0 | 13.327 | 0.056847 | 34.7964
Faster: Renewables / central | 2046 | 86.2194 | 1.3125 | 62.6194 | 23.6 | 0 | 0 | 88.3002 | 0 | 67.9928 | TRUE | TRUE | 1.9707e-15 | 8.0881e-14 | 3.3686 | 0 | 15.2083 | 0.045844 | 35.4212
Faster: Renewables / central | 2047 | 87.7194 | 0.7125 | 62.0194 | 25.7 | 0 | 0 | 89.3884 | 0 | 68.7016 | TRUE | TRUE | 2.0767e-15 | 9.2754e-14 | 3.4476 | 0 | 13.1677 | 0.024887 | 35.796
Faster: Renewables / central | 2048 | 89.391 | 0.7125 | 63.691 | 25.7 | 0 | 0 | 90.418 | 0 | 69.2701 | TRUE | TRUE | 2.2693e-15 | 1.0288e-13 | 3.5099 | 0.10103 | 10.2306 | 0.024887 | 36.151
Faster: Renewables / central | 2049 | 90.5706 | 0.6735 | 63.1706 | 27.4 | 0 | 0 | 91.0581 | 0 | 69.7028 | TRUE | TRUE | 2.4022e-15 | 1.1491e-13 | 3.5728 | 0.40309 | 6.3958 | 0.023525 | 36.3754
Faster: Renewables / central | 2050 | 94.0266 | 3.3607 | 66.6266 | 27.4 | 0 | 0 | 91.3967 | 0 | 69.9985 | TRUE | TRUE | 2.7415e-15 | 1.0569e-13 | 3.7029 | 0 | 0 | 0.11739 | 36.5215
Retention: Renewables / high | 2030 | 34.4879 | 0 | 34.4879 | 0 | 0 | 0 | 84.8499 | 0 | 40.5162 | FALSE | FALSE | 0.043693 | 3.0869 | 1.264 | 0 | 28.4467 | 0 | 35.3569
Retention: Renewables / high | 2031 | 34.6918 | 0 | 33.1918 | 1.5 | 0 | 0 | 83.6356 | 0 | 42.4293 | FALSE | FALSE | 0.058857 | 7.8106 | 1.3128 | 0.11606 | 28.984 | 0 | 34.8127
Retention: Renewables / high | 2032 | 36.9191 | 0.46425 | 33.0191 | 3 | 0.9 | 0 | 81.9116 | 0 | 44.7085 | FALSE | FALSE | 0.042021 | 3.2827 | 1.4034 | 0.13406 | 30.3094 | 0.027026 | 34.1072
Retention: Renewables / high | 2033 | 39.0294 | 1.0005 | 32.7294 | 4.5 | 1.8 | 0 | 82.7051 | 0 | 47.0973 | FALSE | FALSE | 0.043702 | 3.5164 | 1.5207 | 0 | 27.4316 | 0.058244 | 34.426
Retention: Renewables / high | 2034 | 42.99 | 1.0005 | 34.29 | 6 | 2.7 | 0 | 84.0539 | 0 | 49.5026 | FALSE | FALSE | 0.027082 | 3.0172 | 1.6965 | 0.27937 | 28.2682 | 0.058244 | 34.9372
Retention: Renewables / high | 2035 | 46.7409 | 2.118 | 35.6409 | 7.5 | 3.6 | 0 | 80.0456 | 0 | 52.1066 | FALSE | FALSE | 0.020627 | 2.2319 | 1.8646 | 0.396 | 28.6593 | 0.1233 | 33.2623
Retention: Renewables / high | 2036 | 50.3962 | 3.5859 | 36.8962 | 9 | 4.5 | 0 | 82.7954 | 0 | 54.4619 | FALSE | FALSE | 0.022638 | 2.6328 | 2.0379 | 0.45262 | 31.2824 | 0.21551 | 34.292
Retention: Renewables / high | 2037 | 53.9848 | 4.9142 | 38.0848 | 10.5 | 5.4 | 0 | 85.8755 | 0 | 57.2346 | FALSE | FALSE | 0.024794 | 3.4293 | 2.2298 | 0.56531 | 27.9273 | 0.29388 | 35.4088
Retention: Renewables / high | 2038 | 57.7516 | 6.7732 | 39.4516 | 12 | 6.3 | 0 | 82.3126 | 0 | 60.2001 | FALSE | FALSE | 0.022448 | 3.0397 | 2.4012 | 0.3135 | 26.1066 | 0.39431 | 33.9025
Retention: Renewables / high | 2039 | 61.1021 | 7.7479 | 40.4021 | 13.5 | 7.2 | 0 | 78.6179 | 0 | 62.7299 | FALSE | FALSE | 0.020447 | 2.6439 | 2.5531 | 0.735 | 26.6751 | 0.46731 | 32.3411
Retention: Renewables / high | 2040 | 64.8349 | 9.4537 | 41.7349 | 15 | 8.1 | 0 | 81.9931 | 0 | 64.7816 | FALSE | FALSE | 0.022615 | 3.0439 | 2.7385 | 0.47475 | 25.1243 | 0.5734 | 33.631
Retention: Renewables / high | 2041 | 68.9581 | 9.8282 | 43.4581 | 16.5 | 9 | 0 | 84.6489 | 0 | 66.8173 | FALSE | FALSE | 0.021948 | 2.8881 | 2.9289 | 0.48656 | 25.0191 | 0.59174 | 34.6121
Retention: Renewables / high | 2042 | 72.5291 | 9.8692 | 44.6291 | 18 | 9.9 | 0 | 87.5573 | 0 | 68.5013 | FALSE | FALSE | 0.020463 | 2.9177 | 3.1035 | 0.43125 | 27.3971 | 0.59965 | 35.6766
Retention: Renewables / high | 2043 | 76.1725 | 9.4507 | 45.8725 | 19.5 | 10.8 | 0 | 89.4419 | 0 | 70.353 | FALSE | FALSE | 0.017202 | 2.6616 | 3.2724 | 0.49162 | 15.0928 | 0.56843 | 36.3616
Retention: Renewables / high | 2044 | 80.211 | 10.0211 | 47.511 | 21 | 11.7 | 0 | 92.7367 | 0 | 71.1865 | FALSE | FALSE | 0.016211 | 2.2448 | 3.446 | 0.45563 | 26.1124 | 0.60991 | 37.5956
Retention: Renewables / high | 2045 | 83.6074 | 9.2805 | 48.5074 | 22.5 | 12.6 | 0 | 94.7051 | 0 | 72.4161 | FALSE | FALSE | 0.011716 | 1.8367 | 3.5991 | 0.07875 | 16.4588 | 0.54485 | 38.3063
Retention: Renewables / high | 2046 | 86.1921 | 7.6252 | 48.6921 | 24 | 13.5 | 0 | 97.0215 | 0 | 73.2256 | FALSE | FALSE | 0.010919 | 1.625 | 3.7318 | 0.15 | 18.9091 | 0.45264 | 39.1371
Retention: Renewables / high | 2047 | 89.2359 | 6.429 | 49.3359 | 25.5 | 14.4 | 0 | 98.4333 | 0 | 74.3294 | FALSE | FALSE | 0.0090711 | 1.3651 | 3.8726 | 0 | 16.2306 | 0.37427 | 39.6263
Retention: Renewables / high | 2048 | 91.4044 | 4.5259 | 49.1044 | 27 | 15.3 | 0 | 99.8581 | 0 | 75.2027 | FALSE | FALSE | 0.0077798 | 1.2363 | 3.9903 | 0.3465 | 11.248 | 0.27384 | 40.1172
Retention: Renewables / high | 2049 | 93.8406 | 4.1235 | 49.1406 | 28.5 | 16.2 | 0 | 100.7344 | 0 | 75.7383 | FALSE | FALSE | 0.0066311 | 0.99404 | 4.1111 | 0.67181 | 10.0521 | 0.24005 | 40.461
Retention: Renewables / high | 2050 | 96.0341 | 4.9882 | 48.9341 | 30 | 17.1 | 0 | 101.8258 | 0 | 76.0949 | FALSE | FALSE | 0.0057937 | 0.8364 | 4.2244 | 0 | 1.7543 | 0.29039 | 40.9317
Faster: Renewables / high | 2030 | 34.4879 | 0 | 34.4879 | 0 | 0 | 0 | 84.8499 | 0 | 40.5162 | FALSE | FALSE | 0.043693 | 3.0869 | 1.264 | 0 | 30.3752 | 0 | 35.3569
Faster: Renewables / high | 2031 | 37.1918 | 0 | 33.1918 | 4 | 0 | 0 | 83.7925 | 0 | 42.5782 | FALSE | FALSE | 0.032676 | 6.5225 | 1.4384 | 0.069638 | 31.2159 | 0 | 34.896
Faster: Renewables / high | 2032 | 41.0191 | 0.46425 | 33.0191 | 8 | 0 | 0 | 82.066 | 0 | 44.9197 | FALSE | FALSE | 0.017573 | 1.5281 | 1.5858 | 0.080437 | 33.0123 | 0.016216 | 34.1994
Faster: Renewables / high | 2033 | 48.0094 | 1.0005 | 36.4094 | 11.6 | 0 | 0 | 82.9708 | 0 | 47.6278 | FALSE | FALSE | 0.0053274 | 0.47067 | 1.8746 | 0 | 29.6959 | 0.034947 | 34.5582
Faster: Renewables / high | 2034 | 55.01 | 1.0005 | 39.81 | 15.2 | 0 | 0 | 84.3148 | 0 | 50.2213 | TRUE | FALSE | 1.0447e-15 | 0.06521 | 2.126 | 0.16762 | 30.5326 | 0.034947 | 35.0464
Faster: Renewables / high | 2035 | 61.8009 | 2.118 | 43.0009 | 18.8 | 0 | 0 | 80.28 | 0 | 52.9829 | TRUE | FALSE | 9.9143e-16 | 0.0054194 | 2.3215 | 0.2376 | 30.5986 | 0.07398 | 33.3373
Faster: Renewables / high | 2036 | 68.1123 | 3.702 | 46.2123 | 21.9 | 0 | 0 | 83.0548 | 0 | 55.4558 | TRUE | TRUE | 1.0976e-15 | 5.9401e-15 | 2.5608 | 0.20194 | 32.9617 | 0.12931 | 34.3438
Faster: Renewables / high | 2037 | 73.3946 | 4.584 | 48.7946 | 24.6 | 0 | 0 | 86.1516 | 0 | 58.297 | TRUE | TRUE | 1.3982e-15 | 7.2262e-15 | 2.8344 | 0.25875 | 28.5017 | 0.16011 | 35.4257
Faster: Renewables / high | 2038 | 76.9311 | 5.7728 | 51.3311 | 25.6 | 0 | 0 | 82.5562 | 0 | 61.2141 | TRUE | TRUE | 1.2279e-15 | 6.3878e-15 | 2.9739 | 0.1881 | 26.0309 | 0.20164 | 33.8675
Faster: Renewables / high | 2039 | 80.001 | 7.0268 | 54.401 | 25.6 | 0 | 0 | 78.8476 | 0 | 63.6943 | TRUE | TRUE | 1.1447e-15 | 1.733e-14 | 3.0814 | 0.27337 | 28.4194 | 0.24544 | 32.2707
Faster: Renewables / high | 2040 | 84.9729 | 7.7317 | 56.5729 | 28.4 | 0 | 0 | 82.2418 | 0 | 65.7636 | TRUE | TRUE | 1.2242e-15 | 3.9702e-14 | 3.3231 | 0.04725 | 26.6086 | 0.27006 | 33.5043
Faster: Renewables / high | 2041 | 89.2926 | 6.4628 | 58.4926 | 30.8 | 0 | 0 | 84.8813 | 0 | 67.8067 | TRUE | TRUE | 1.4629e-15 | 5.5437e-14 | 3.5066 | 0.09 | 25.7884 | 0.22574 | 34.4437
Faster: Renewables / high | 2042 | 92.8164 | 5.7165 | 60.7164 | 32.1 | 0 | 0 | 87.7872 | 0 | 69.487 | TRUE | TRUE | 1.6564e-15 | 6.9512e-14 | 3.673 | 0 | 27.5814 | 0.19967 | 35.4675
Faster: Renewables / high | 2043 | 94.9932 | 3.9915 | 62.4932 | 32.5 | 0 | 0 | 89.6586 | 0 | 71.2814 | TRUE | TRUE | 2.6899e-15 | 1.0449e-13 | 3.7917 | 0.10687 | 15.6671 | 0.13942 | 36.129
Faster: Renewables / high | 2044 | 98.3599 | 3.45 | 64.8599 | 33.5 | 0 | 0 | 92.9459 | 0 | 72.0548 | TRUE | TRUE | 3.1749e-15 | 1.2019e-13 | 3.9261 | 0 | 26.0367 | 0.12051 | 37.3213
Faster: Renewables / high | 2045 | 100.1144 | 1.6275 | 66.6144 | 33.5 | 0 | 0 | 94.9083 | 0 | 73.2476 | TRUE | TRUE | 3.3593e-15 | 1.5334e-13 | 3.9969 | 0 | 15.506 | 0.056847 | 38.0177
Faster: Renewables / high | 2046 | 103.4794 | 1.3125 | 69.9794 | 33.5 | 0 | 0 | 97.224 | 0 | 74.1679 | TRUE | TRUE | 3.9161e-15 | 1.3296e-13 | 4.102 | 0 | 17.3715 | 0.045844 | 38.8391
Faster: Renewables / high | 2047 | 106.5594 | 0.7125 | 73.0594 | 33.5 | 0 | 0 | 98.6187 | 0 | 75.3391 | TRUE | TRUE | 3.964e-15 | 1.1346e-13 | 4.1874 | 0 | 14.693 | 0.024887 | 39.3232
Faster: Renewables / high | 2048 | 107.311 | 0.7125 | 73.811 | 33.5 | 0 | 0 | 100.0319 | 0 | 76.1457 | TRUE | TRUE | 3.9892e-15 | 1.3851e-13 | 4.2593 | 0.10103 | 9.418 | 0.024887 | 39.8107
Faster: Renewables / high | 2049 | 107.7106 | 0.6735 | 74.2106 | 33.5 | 0 | 0 | 100.8968 | 0 | 76.5696 | TRUE | TRUE | 4.0203e-15 | 1.7874e-13 | 4.2793 | 0.40309 | 8.0649 | 0.023525 | 40.1367
Faster: Renewables / high | 2050 | 111.1666 | 3.3607 | 77.6666 | 33.5 | 0 | 0 | 101.9936 | 0 | 76.9955 | TRUE | TRUE | 3.7604e-15 | 1.1418e-13 | 4.3871 | 0 | 0 | 0.11739 | 40.5586
Planning: Proposed / low | 2030 | 34.4879 | 0 | 34.4879 | 0 | 0 | 0 | 82.6324 | 0 | 40.1393 | FALSE | FALSE | 0.025082 | 1.8917 | 1.2586 | 0 | 15.8728 | 0 | 34.6485
Planning: Proposed / low | 2031 | 34.6918 | 0 | 33.1918 | 1.5 | 0 | 0 | 81.3093 | 0 | 41.4207 | FALSE | FALSE | 0.033965 | 6.0263 | 1.3055 | 0.069638 | 12.8057 | 0 | 34.0642
Planning: Proposed / low | 2032 | 36.9191 | 0.46425 | 33.0191 | 3 | 0.9 | 0 | 78.9252 | 0 | 43.1876 | FALSE | FALSE | 0.021835 | 1.2184 | 1.3834 | 0.080437 | 7.9611 | 0.016216 | 33.1196
Planning: Proposed / low | 2033 | 39.0294 | 1.0005 | 32.7294 | 4.5 | 1.8 | 0 | 80.3024 | 0 | 43.2823 | FALSE | FALSE | 0.020431 | 1.0705 | 1.4954 | 0 | 8.9499 | 0.034947 | 33.6067
Planning: Proposed / low | 2034 | 42.99 | 1.0005 | 34.29 | 6 | 2.7 | 0 | 81.8508 | 0 | 43.6589 | FALSE | FALSE | 0.013812 | 3.7485 | 1.702 | 0.16762 | 8.9499 | 0.034947 | 34.1592
Planning: Proposed / low | 2035 | 46.7409 | 2.118 | 35.6409 | 7.5 | 3.6 | 2 | 70.959 | 14.9037 | 44.2484 | FALSE | FALSE | 6.0021e-16 | 1.9102 | 1.862 | 0.2376 | 7.9497 | 0.07398 | 42.2988
Planning: Proposed / low | 2036 | 50.5123 | 3.702 | 37.0123 | 9 | 4.5 | 4 | 65.6162 | 29.8073 | 44.7307 | TRUE | FALSE | 6.065e-16 | 1.0619 | 2.0241 | 0.20194 | 9.1995 | 0.12931 | 52.6996
Planning: Proposed / low | 2037 | 53.6546 | 4.584 | 37.7546 | 10.5 | 5.4 | 6 | 58.1344 | 32.0288 | 45.5322 | TRUE | FALSE | 5.2913e-16 | 0.38336 | 2.1127 | 0.25875 | 9.5345 | 0.16011 | 52.0419
Planning: Proposed / low | 2038 | 56.7511 | 5.7728 | 38.4511 | 12 | 6.3 | 8 | 53.6396 | 32.7761 | 46.306 | TRUE | FALSE | 5.1734e-16 | 0.054847 | 2.1922 | 0.1881 | 12.3893 | 0.20164 | 50.8282
Planning: Proposed / low | 2039 | 60.081 | 7.0268 | 39.681 | 13.2 | 7.2 | 8 | 42.7089 | 35.9432 | 46.9886 | TRUE | TRUE | 3.3546e-16 | 1.755e-15 | 2.1833 | 0.27337 | 14.4143 | 0.24544 | 49.5886
Planning: Proposed / low | 2040 | 61.9129 | 7.7317 | 40.0129 | 13.8 | 8.1 | 8 | 38.1931 | 36.1804 | 46.9846 | TRUE | TRUE | 3.605e-16 | 1.9327e-15 | 2.2438 | 0.04725 | 15.8518 | 0.27006 | 47.8574
Planning: Proposed / low | 2041 | 62.9926 | 6.4628 | 40.0926 | 14.5 | 8.4 | 8 | 30.5122 | 36.1269 | 47.2899 | TRUE | TRUE | 3.9947e-16 | 2.1032e-15 | 2.2661 | 0.09 | 16.2968 | 0.22574 | 44.5657
Planning: Proposed / low | 2042 | 63.3764 | 5.7165 | 40.4764 | 14.5 | 8.4 | 8 | 19.8165 | 35.773 | 47.3125 | TRUE | TRUE | 4.9709e-16 | 2.7072e-15 | 2.229 | 0 | 16.5818 | 0.19967 | 39.7528
Planning: Proposed / low | 2043 | 63.6132 | 3.9915 | 40.4132 | 14.5 | 8.7 | 8 | 14.2701 | 33.0571 | 47.1487 | TRUE | TRUE | 4.4937e-16 | 2.5011e-15 | 2.168 | 0.10687 | 17.6468 | 0.13942 | 34.5913
Planning: Proposed / low | 2044 | 65.9399 | 3.45 | 40.9399 | 15.7 | 9.3 | 8 | 12.8524 | 33.4898 | 47.9753 | TRUE | TRUE | 4.5758e-16 | 3.1193e-15 | 2.1685 | 0 | 16.2068 | 0.12051 | 34.4996
Planning: Proposed / low | 2045 | 68.2544 | 1.6275 | 40.8544 | 17.2 | 10.2 | 8 | 22.0951 | 0 | 47.6891 | TRUE | TRUE | 5.0439e-16 | 3.709e-15 | 2.2538 | 0 | 11.435 | 0.056847 | 9.0499
Planning: Proposed / low | 2046 | 69.7794 | 1.3125 | 42.3794 | 17.2 | 10.2 | 8 | 19.3611 | 0 | 48.849 | TRUE | TRUE | 3.9648e-16 | 2.8564e-15 | 2.2389 | 0 | 8.735 | 0.045844 | 7.9588
Planning: Proposed / low | 2047 | 71.0194 | 0.7125 | 43.6194 | 17.2 | 10.2 | 8 | 17.0829 | 0 | 49.6183 | TRUE | TRUE | 3.129e-16 | 2.1245e-15 | 2.2722 | 0 | 4.6965 | 0.024887 | 7.0545
Planning: Proposed / low | 2048 | 72.691 | 0.7125 | 45.291 | 17.2 | 10.2 | 8 | 16.7751 | 0 | 50.0486 | TRUE | TRUE | 2.946e-16 | 2.3306e-15 | 2.2929 | 0.10103 | 2.0079 | 0.024887 | 6.9344
Planning: Proposed / low | 2049 | 72.1706 | 0.6735 | 44.7706 | 17.2 | 10.2 | 8 | 19.0821 | 0 | 49.6295 | TRUE | TRUE | 3.4213e-16 | 2.7711e-15 | 2.3094 | 0.40309 | 1.3386 | 0.023525 | 7.8594
Planning: Proposed / low | 2050 | 73.7866 | 3.3607 | 46.3866 | 17.2 | 10.2 | 8 | 20.4014 | 0 | 49.7702 | TRUE | TRUE | 3.8659e-16 | 3.2045e-15 | 2.3553 | 0 | 0 | 0.11739 | 8.3904
Test: Proposed / central / ext5 / coal4 / slow | 2030 | 34.4879 | 0 | 34.4879 | 0 | 0 | 0 | 83.8047 | 0 | 40.4038 | FALSE | FALSE | 0.026374 | 2.5779 | 1.2636 | 0 | 15.8728 | 0 | 35.007
Test: Proposed / central / ext5 / coal4 / slow | 2031 | 34.6918 | 0 | 33.1918 | 1.5 | 0 | 0 | 83.2492 | 0 | 41.8078 | FALSE | FALSE | 0.038244 | 2.659 | 1.2843 | 0.069638 | 12.8057 | 0 | 34.6719
Test: Proposed / central / ext5 / coal4 / slow | 2032 | 36.9191 | 0.46425 | 33.0191 | 3 | 0.9 | 0 | 81.7835 | 0 | 43.6968 | FALSE | FALSE | 0.023456 | 2.6497 | 1.4014 | 0.080437 | 7.9611 | 0.016216 | 34.0356
Test: Proposed / central / ext5 / coal4 / slow | 2033 | 39.0294 | 1.0005 | 32.7294 | 4.5 | 1.8 | 0 | 84.8255 | 0 | 43.9875 | FALSE | FALSE | 0.025186 | 2.9222 | 1.5237 | 0 | 8.9499 | 0.034947 | 35.0784
Test: Proposed / central / ext5 / coal4 / slow | 2034 | 42.99 | 1.0005 | 34.29 | 6 | 2.7 | 0 | 88.4763 | 0 | 44.5796 | FALSE | FALSE | 0.019416 | 2.3874 | 1.6972 | 0.16762 | 8.9499 | 0.034947 | 36.3417
Test: Proposed / central / ext5 / coal4 / slow | 2035 | 46.7409 | 2.118 | 35.6409 | 7.5 | 3.6 | 2 | 79.3062 | 14.9037 | 45.4006 | FALSE | FALSE | 0.0088534 | 0.99526 | 1.8589 | 0.2376 | 7.9497 | 0.07398 | 45.1223
Test: Proposed / central / ext5 / coal4 / slow | 2036 | 50.5123 | 3.702 | 37.0123 | 9 | 4.5 | 4 | 77.8626 | 29.8073 | 46.286 | FALSE | FALSE | 0.0073504 | 3.9989 | 2.0661 | 0.20194 | 9.1995 | 0.12931 | 56.9262
Test: Proposed / central / ext5 / coal4 / slow | 2037 | 53.6546 | 4.584 | 37.7546 | 10.5 | 5.4 | 6 | 72.1451 | 35.2625 | 47.5065 | FALSE | FALSE | 0.0026476 | 3.2307 | 2.2089 | 0.25875 | 9.5345 | 0.16011 | 59.7697
Test: Proposed / central / ext5 / coal4 / slow | 2038 | 56.7511 | 5.7728 | 38.4511 | 12 | 6.3 | 8 | 67.2509 | 41.7721 | 48.6884 | FALSE | FALSE | 1.6636e-15 | 2.5239 | 2.3595 | 0.1881 | 12.5843 | 0.20164 | 63.72
Test: Proposed / central / ext5 / coal4 / slow | 2039 | 60.381 | 7.0268 | 39.681 | 13.5 | 7.2 | 8 | 62.979 | 42.0988 | 49.7571 | TRUE | FALSE | 1.9116e-15 | 1.9666 | 2.5253 | 0.27337 | 15.2843 | 0.24544 | 62.1098
Test: Proposed / central / ext5 / coal4 / slow | 2040 | 63.1129 | 7.7317 | 40.0129 | 15 | 8.1 | 8 | 64.4407 | 43.18 | 50.3478 | TRUE | FALSE | 1.8396e-15 | 2.1984 | 2.6649 | 0.04725 | 17.0843 | 0.27006 | 63.261
Test: Proposed / central / ext5 / coal4 / slow | 2041 | 65.5926 | 6.4628 | 40.0926 | 16.5 | 9 | 8 | 59.2229 | 43.3022 | 50.9537 | TRUE | FALSE | 1.8411e-15 | 1.7498 | 2.7857 | 0.09 | 17.9843 | 0.22574 | 61.1527
Test: Proposed / central / ext5 / coal4 / slow | 2042 | 68.3764 | 5.7165 | 40.4764 | 18 | 9.9 | 8 | 51.061 | 43.2608 | 51.3948 | TRUE | FALSE | 1.8697e-15 | 1.1419 | 2.9154 | 0 | 17.9843 | 0.19967 | 57.7202
Test: Proposed / central / ext5 / coal4 / slow | 2043 | 70.7132 | 3.9915 | 40.4132 | 19.5 | 10.8 | 8 | 45.2858 | 42.9352 | 51.5377 | TRUE | FALSE | 1.763e-15 | 0.85795 | 2.9675 | 0.10687 | 17.9843 | 0.13942 | 54.9799
Test: Proposed / central / ext5 / coal4 / slow | 2044 | 73.6399 | 3.45 | 40.9399 | 21 | 11.7 | 8 | 42.9533 | 42.5233 | 52.3257 | TRUE | FALSE | 2.0932e-15 | 0.41596 | 3.0119 | 0 | 17.9843 | 0.12051 | 53.7322
Test: Proposed / central / ext5 / coal4 / slow | 2045 | 75.9544 | 1.6275 | 40.8544 | 22.5 | 12.6 | 8 | 68.7957 | 0.0083632 | 52.6799 | TRUE | FALSE | 2.4738e-15 | 0.32224 | 3.1364 | 0 | 17.9843 | 0.056847 | 26.155
Test: Proposed / central / ext5 / coal4 / slow | 2046 | 79.8794 | 1.3125 | 42.3794 | 24 | 13.5 | 8 | 63.2403 | 0 | 53.8606 | TRUE | FALSE | 2.0841e-15 | 0.029033 | 3.2426 | 0 | 17.3618 | 0.045844 | 23.9807
Test: Proposed / central / ext5 / coal4 / slow | 2047 | 83.2194 | 0.7125 | 43.6194 | 25.2 | 14.4 | 8 | 57.1107 | 0 | 54.5497 | TRUE | TRUE | 1.649e-15 | 1.4161e-14 | 3.1721 | 0 | 12.5543 | 0.024887 | 21.6904
Test: Proposed / central / ext5 / coal4 / slow | 2048 | 84.891 | 0.7125 | 45.291 | 25.2 | 14.4 | 8 | 50.9266 | 0 | 55.0909 | TRUE | TRUE | 1.4704e-15 | 1.3543e-14 | 3.1177 | 0.10103 | 8.9543 | 0.024887 | 19.3925
Test: Proposed / central / ext5 / coal4 / slow | 2049 | 85.2906 | 0.6735 | 45.6906 | 25.2 | 14.4 | 8 | 45.513 | 0 | 55.3673 | TRUE | TRUE | 1.2381e-15 | 1.1106e-14 | 3.09 | 0.40309 | 5.3543 | 0.023525 | 17.3888
Test: Proposed / central / ext5 / coal4 / slow | 2050 | 86.9066 | 3.3607 | 47.3066 | 25.2 | 14.4 | 8 | 37.9115 | 0 | 55.7956 | TRUE | TRUE | 9.6523e-16 | 9.3863e-15 | 3.0883 | 0 | 1.3157 | 0.11739 | 14.6132
Planning: Proposed / high | 2030 | 34.4879 | 0 | 34.4879 | 0 | 0 | 0 | 84.8499 | 0 | 40.5162 | FALSE | FALSE | 0.043693 | 3.0869 | 1.264 | 0 | 15.8728 | 0 | 35.3569
Planning: Proposed / high | 2031 | 34.6918 | 0 | 33.1918 | 1.5 | 0 | 0 | 84.595 | 0 | 41.9481 | FALSE | FALSE | 0.070006 | 7.9541 | 1.3128 | 0.069638 | 12.8057 | 0 | 35.1197
Planning: Proposed / high | 2032 | 36.9191 | 0.46425 | 33.0191 | 3 | 0.9 | 0 | 83.4676 | 0 | 43.8677 | FALSE | FALSE | 0.05854 | 3.4527 | 1.4052 | 0.080437 | 7.9611 | 0.016216 | 34.6119
Planning: Proposed / high | 2033 | 39.0294 | 1.0005 | 32.7294 | 4.5 | 1.8 | 0 | 87.3273 | 0 | 44.2227 | FALSE | FALSE | 0.080191 | 8.0331 | 1.555 | 0 | 8.9499 | 0.034947 | 35.9549
Planning: Proposed / high | 2034 | 42.99 | 1.0005 | 34.29 | 6 | 2.7 | 0 | 92.3447 | 0 | 44.9281 | FALSE | FALSE | 0.069675 | 7.9479 | 1.7425 | 0.16762 | 8.9499 | 0.034947 | 37.7203
Planning: Proposed / high | 2035 | 46.7409 | 2.118 | 35.6409 | 7.5 | 3.6 | 2 | 84.5315 | 14.9037 | 45.8637 | FALSE | FALSE | 0.029258 | 6.603 | 1.901 | 0.2376 | 7.9497 | 0.07398 | 47.0419
Planning: Proposed / high | 2036 | 50.5123 | 3.702 | 37.0123 | 9 | 4.5 | 4 | 85.4966 | 29.8073 | 46.9513 | FALSE | FALSE | 0.030379 | 6.8179 | 2.0769 | 0.20194 | 9.1995 | 0.12931 | 59.7768
Planning: Proposed / high | 2037 | 53.6546 | 4.584 | 37.7546 | 10.5 | 5.4 | 6 | 84.1123 | 36.3056 | 48.6356 | FALSE | FALSE | 0.026796 | 6.9375 | 2.2396 | 0.25875 | 9.5345 | 0.16011 | 65.0541
Planning: Proposed / high | 2038 | 56.7511 | 5.7728 | 38.4511 | 12 | 6.3 | 8 | 82.4134 | 44.3864 | 50.1593 | FALSE | FALSE | 0.024481 | 6.6445 | 2.3855 | 0.1881 | 12.5843 | 0.20164 | 71.5494
Planning: Proposed / high | 2039 | 60.381 | 7.0268 | 39.681 | 13.5 | 7.2 | 8 | 81.8089 | 45.0531 | 51.5195 | FALSE | FALSE | 0.022489 | 6.3715 | 2.5481 | 0.27337 | 15.2843 | 0.24544 | 71.6862
Planning: Proposed / high | 2040 | 63.1129 | 7.7317 | 40.0129 | 15 | 8.1 | 8 | 97.011 | 37.2185 | 52.5391 | FALSE | FALSE | 0.029579 | 7.102 | 2.6954 | 0.04725 | 17.0843 | 0.27006 | 69.9751
Planning: Proposed / high | 2041 | 65.5926 | 6.4628 | 40.0926 | 16.5 | 9 | 8 | 95.4896 | 39.8962 | 53.5667 | FALSE | FALSE | 0.028062 | 6.982 | 2.8142 | 0.09 | 17.9843 | 0.22574 | 71.5579
Planning: Proposed / high | 2042 | 68.3764 | 5.7165 | 40.4764 | 18 | 9.9 | 8 | 91.1318 | 42.6232 | 54.4525 | FALSE | FALSE | 0.020251 | 6.8292 | 2.9578 | 0 | 17.9843 | 0.19967 | 72.0638
Planning: Proposed / high | 2043 | 70.7132 | 3.9915 | 40.4132 | 19.5 | 10.8 | 8 | 88.4802 | 42.6559 | 54.8639 | FALSE | FALSE | 0.016445 | 6.2402 | 3.0735 | 0.10687 | 17.9843 | 0.13942 | 70.9174
Planning: Proposed / high | 2044 | 73.6399 | 3.45 | 40.9399 | 21 | 11.7 | 8 | 86.3024 | 42.4417 | 55.6984 | FALSE | FALSE | 0.0098078 | 5.307 | 3.2131 | 0 | 17.9843 | 0.12051 | 70.0025
Planning: Proposed / high | 2045 | 75.9544 | 1.6275 | 40.8544 | 22.5 | 12.6 | 8 | 114.803 | 0.62813 | 56.1787 | FALSE | FALSE | 0.0062193 | 5.0169 | 3.2764 | 0 | 17.9843 | 0.056847 | 44.5562
Planning: Proposed / high | 2046 | 79.8794 | 1.3125 | 42.3794 | 24 | 13.5 | 8 | 107.5638 | 0.28555 | 57.2412 | FALSE | FALSE | 0.00089868 | 3.6046 | 3.3624 | 0 | 17.9843 | 0.045844 | 41.4583
Planning: Proposed / high | 2047 | 83.5194 | 0.7125 | 43.6194 | 25.5 | 14.4 | 8 | 102.4646 | 0.13581 | 58.0591 | TRUE | FALSE | 2.7702e-15 | 2.45 | 3.4507 | 0 | 14.3843 | 0.024887 | 39.3278
Planning: Proposed / high | 2048 | 87.591 | 0.7125 | 45.291 | 27 | 15.3 | 8 | 97.1049 | 0.050465 | 58.8764 | TRUE | FALSE | 2.6338e-15 | 1.3381 | 3.5693 | 0.10103 | 10.7843 | 0.024887 | 37.1547
Planning: Proposed / high | 2049 | 90.3906 | 0.6735 | 45.6906 | 28.5 | 16.2 | 8 | 90.748 | 0.016963 | 59.2993 | TRUE | FALSE | 2.3635e-15 | 0.66824 | 3.6289 | 0.40309 | 6.7568 | 0.023525 | 34.8003
Planning: Proposed / high | 2050 | 94.4066 | 3.3607 | 47.3066 | 30 | 17.1 | 8 | 81.909 | 0 | 59.9041 | TRUE | FALSE | 2.1523e-15 | 0.19647 | 3.697 | 0 | 1.7543 | 0.11739 | 31.5539
Planning: Renewables / low | 2030 | 34.4879 | 0 | 34.4879 | 0 | 0 | 0 | 82.6324 | 0 | 40.1393 | FALSE | FALSE | 0.025082 | 1.8917 | 1.2586 | 0 | 15.2373 | 0 | 34.6485
Planning: Renewables / low | 2031 | 34.6918 | 0 | 33.1918 | 1.5 | 0 | 0 | 81.1294 | 0 | 41.5355 | FALSE | FALSE | 0.033109 | 5.9904 | 1.3055 | 0.069638 | 16.62 | 0 | 34.0054
Planning: Renewables / low | 2032 | 36.9191 | 0.46425 | 33.0191 | 3 | 0.9 | 0 | 78.6125 | 0 | 43.4251 | FALSE | FALSE | 0.02131 | 1.1924 | 1.3832 | 0.080437 | 14.6657 | 0.016216 | 33.0166
Planning: Renewables / low | 2033 | 39.0294 | 1.0005 | 32.7294 | 4.5 | 1.8 | 0 | 79.7573 | 0 | 43.6373 | FALSE | FALSE | 0.019635 | 1.044 | 1.491 | 0 | 16.9524 | 0.034947 | 33.4254
Planning: Renewables / low | 2034 | 42.99 | 1.0005 | 34.29 | 6 | 2.7 | 0 | 79.9961 | 0 | 45.3082 | FALSE | FALSE | 0.011259 | 0.47745 | 1.6637 | 0.16762 | 13.4048 | 0.034947 | 33.5364
Planning: Renewables / low | 2035 | 46.7409 | 2.118 | 35.6409 | 7.5 | 3.6 | 0 | 75.2575 | 0 | 46.5354 | FALSE | FALSE | 0.0015143 | 0.086613 | 1.7909 | 0.2376 | 12.8577 | 0.07398 | 31.5655
Planning: Renewables / low | 2036 | 50.5123 | 3.702 | 37.0123 | 9 | 4.5 | 0 | 76.0791 | 0 | 47.3555 | TRUE | FALSE | 6.592e-16 | 0.038683 | 1.8893 | 0.20194 | 14.0231 | 0.12931 | 31.8659
Planning: Renewables / low | 2037 | 53.6546 | 4.584 | 37.7546 | 10.5 | 5.4 | 0 | 76.9088 | 0 | 48.0996 | TRUE | FALSE | 7.3629e-16 | 0.02343 | 2.0151 | 0.25875 | 14.5064 | 0.16011 | 32.1662
Planning: Renewables / low | 2038 | 56.6511 | 5.7728 | 38.4511 | 11.9 | 6.3 | 0 | 71.7767 | 0 | 49.5104 | TRUE | TRUE | 5.8103e-16 | 3.1051e-15 | 2.0889 | 0.1881 | 13.6885 | 0.20164 | 30.0377
Planning: Renewables / low | 2039 | 58.181 | 7.0268 | 39.681 | 11.9 | 6.6 | 0 | 66.7313 | 0 | 50.6693 | TRUE | TRUE | 4.6422e-16 | 3.002e-15 | 2.0945 | 0.27337 | 16.3346 | 0.24544 | 27.9193
Planning: Renewables / low | 2040 | 60.0129 | 7.7317 | 40.0129 | 12.5 | 7.5 | 0 | 68.1538 | 0 | 51.3945 | TRUE | TRUE | 4.834e-16 | 2.9665e-15 | 2.2216 | 0.04725 | 18.013 | 0.27006 | 28.4477
Planning: Renewables / low | 2041 | 62.4926 | 6.4628 | 40.0926 | 14 | 8.4 | 0 | 69.5022 | 0 | 52.6195 | TRUE | TRUE | 5.3526e-16 | 3.1477e-15 | 2.354 | 0.09 | 17.2838 | 0.22574 | 28.9468
Planning: Renewables / low | 2042 | 64.9764 | 5.7165 | 40.4764 | 15.5 | 9 | 0 | 70.9936 | 0 | 53.3852 | TRUE | TRUE | 5.6745e-16 | 3.5101e-15 | 2.4733 | 0 | 22.3665 | 0.19967 | 29.503
Planning: Renewables / low | 2043 | 66.0132 | 3.9915 | 40.4132 | 16 | 9.6 | 0 | 71.8802 | 0 | 54.439 | TRUE | TRUE | 5.9668e-16 | 3.2365e-15 | 2.5772 | 0.10687 | 13.6902 | 0.13942 | 29.8369
Planning: Renewables / low | 2044 | 68.9399 | 3.45 | 40.9399 | 17.5 | 10.5 | 0 | 74.1428 | 0 | 54.8935 | TRUE | TRUE | 6.9651e-16 | 3.9364e-15 | 2.7049 | 0 | 22.8859 | 0.12051 | 30.6639
Planning: Renewables / low | 2045 | 69.6544 | 1.6275 | 40.8544 | 18 | 10.8 | 0 | 75.4195 | 0 | 55.8699 | TRUE | TRUE | 7.4532e-16 | 4.0359e-15 | 2.8066 | 0 | 12.003 | 0.056847 | 31.1264
Planning: Renewables / low | 2046 | 71.4794 | 1.3125 | 42.3794 | 18.3 | 10.8 | 0 | 76.913 | 0 | 56.6009 | TRUE | TRUE | 8.5215e-16 | 4.4409e-15 | 2.8768 | 0 | 14.0504 | 0.045844 | 31.6567
Planning: Renewables / low | 2047 | 72.9194 | 0.7125 | 43.6194 | 18.5 | 10.8 | 0 | 77.901 | 0 | 57.3492 | TRUE | TRUE | 9.0228e-16 | 4.4125e-15 | 2.9323 | 0 | 13.3707 | 0.024887 | 32.0106
Planning: Renewables / low | 2048 | 74.591 | 0.7125 | 45.291 | 18.5 | 10.8 | 0 | 79.0215 | 0 | 57.9606 | TRUE | TRUE | 9.1022e-16 | 4.5972e-15 | 2.994 | 0.10103 | 11.092 | 0.024887 | 32.412
Planning: Renewables / low | 2049 | 76.0906 | 0.6735 | 45.6906 | 19 | 11.4 | 0 | 79.7603 | 0 | 58.4807 | TRUE | TRUE | 9.3179e-16 | 4.8885e-15 | 3.0657 | 0.40309 | 8.1136 | 0.023525 | 32.6907
Planning: Renewables / low | 2050 | 77.7066 | 3.3607 | 47.3066 | 19 | 11.4 | 0 | 80.5875 | 0 | 59.0008 | TRUE | TRUE | 9.2704e-16 | 4.9383e-15 | 3.1271 | 0 | 1.7543 | 0.11739 | 33.0125
Planning: Renewables / central | 2030 | 34.4879 | 0 | 34.4879 | 0 | 0 | 0 | 83.8047 | 0 | 40.4038 | FALSE | FALSE | 0.026374 | 2.5779 | 1.2636 | 0 | 24.5961 | 0 | 35.007
Planning: Renewables / central | 2031 | 34.6918 | 0 | 33.1918 | 1.5 | 0 | 0 | 82.6055 | 0 | 42.1323 | FALSE | FALSE | 0.035357 | 2.5891 | 1.2838 | 0.069638 | 26.1298 | 0 | 34.4671
Planning: Renewables / central | 2032 | 36.9191 | 0.46425 | 33.0191 | 3 | 0.9 | 0 | 80.665 | 0 | 44.3495 | FALSE | FALSE | 0.020499 | 2.5295 | 1.4 | 0.080437 | 26.6919 | 0.016216 | 33.6727
Planning: Renewables / central | 2033 | 39.0294 | 1.0005 | 32.7294 | 4.5 | 1.8 | 0 | 81.481 | 0 | 46.2793 | FALSE | FALSE | 0.018947 | 2.6068 | 1.5192 | 0 | 24.2932 | 0.034947 | 33.9798
Planning: Renewables / central | 2034 | 42.99 | 1.0005 | 34.29 | 6 | 2.7 | 0 | 82.4679 | 0 | 48.3808 | FALSE | FALSE | 0.013609 | 1.957 | 1.6957 | 0.16762 | 23.6736 | 0.034947 | 34.351
Planning: Renewables / central | 2035 | 46.7409 | 2.118 | 35.6409 | 7.5 | 3.6 | 0 | 78.1756 | 0 | 50.5824 | FALSE | FALSE | 0.0056936 | 1.1233 | 1.8634 | 0.2376 | 23.4464 | 0.07398 | 32.5479
Planning: Renewables / central | 2036 | 50.5123 | 3.702 | 37.0123 | 9 | 4.5 | 0 | 80.2616 | 0 | 52.5303 | FALSE | FALSE | 0.0057072 | 1.1499 | 2.0442 | 0.20194 | 23.4243 | 0.12931 | 33.3004
Planning: Renewables / central | 2037 | 53.6546 | 4.584 | 37.7546 | 10.5 | 5.4 | 0 | 82.373 | 0 | 54.3633 | FALSE | FALSE | 0.006311 | 1.3043 | 2.1997 | 0.25875 | 24.097 | 0.16011 | 34.0659
Planning: Renewables / central | 2038 | 56.7511 | 5.7728 | 38.4511 | 12 | 6.3 | 0 | 78.2175 | 0 | 56.6337 | FALSE | FALSE | 0.0034457 | 0.99041 | 2.3454 | 0.1881 | 21.884 | 0.20164 | 32.3078
Planning: Renewables / central | 2039 | 60.381 | 7.0268 | 39.681 | 13.5 | 7.2 | 0 | 73.9448 | 0 | 58.6952 | FALSE | FALSE | 0.00030486 | 0.58188 | 2.5032 | 0.27337 | 23.5366 | 0.24544 | 30.4956
Planning: Renewables / central | 2040 | 63.1129 | 7.7317 | 40.0129 | 15 | 8.1 | 0 | 76.3958 | 0 | 60.5041 | FALSE | FALSE | 0.0015834 | 0.85723 | 2.6574 | 0.04725 | 20.2299 | 0.27006 | 31.3902
Planning: Renewables / central | 2041 | 65.5926 | 6.4628 | 40.0926 | 16.5 | 9 | 0 | 78.3117 | 0 | 61.7961 | FALSE | FALSE | 0.0025726 | 0.88623 | 2.7859 | 0.09 | 20.9914 | 0.22574 | 32.0919
Planning: Renewables / central | 2042 | 68.3764 | 5.7165 | 40.4764 | 18 | 9.9 | 0 | 80.3534 | 0 | 62.9137 | FALSE | FALSE | 0.0019291 | 0.85985 | 2.9265 | 0 | 25.9254 | 0.19967 | 32.8294
Planning: Renewables / central | 2043 | 70.7132 | 3.9915 | 40.4132 | 19.5 | 10.8 | 0 | 81.7255 | 0 | 64.3948 | FALSE | FALSE | 0.00075029 | 0.86665 | 3.0494 | 0.10687 | 15.8726 | 0.13942 | 33.3223
Planning: Renewables / central | 2044 | 73.6399 | 3.45 | 40.9399 | 21 | 11.7 | 0 | 84.3492 | 0 | 65.0881 | FALSE | FALSE | 0.00031798 | 0.77184 | 3.1926 | 0 | 26.8044 | 0.12051 | 34.2711
Planning: Renewables / central | 2045 | 75.9544 | 1.6275 | 40.8544 | 22.5 | 12.6 | 0 | 86.357 | 0 | 66.3745 | TRUE | FALSE | 1.1783e-15 | 0.75228 | 3.3174 | 0 | 15.2868 | 0.056847 | 34.9625
Planning: Renewables / central | 2046 | 79.8794 | 1.3125 | 42.3794 | 24 | 13.5 | 0 | 88.246 | 0 | 67.5424 | TRUE | FALSE | 1.2689e-15 | 0.40258 | 3.4901 | 0 | 16.5504 | 0.045844 | 35.5958
Planning: Renewables / central | 2047 | 83.5194 | 0.7125 | 43.6194 | 25.5 | 14.4 | 0 | 89.3502 | 0 | 68.4276 | TRUE | FALSE | 1.2558e-15 | 0.19947 | 3.6358 | 0 | 14.7053 | 0.024887 | 35.9643
Planning: Renewables / central | 2048 | 87.591 | 0.7125 | 45.291 | 27 | 15.3 | 0 | 90.3938 | 0 | 69.1532 | TRUE | FALSE | 1.2277e-15 | 0.031766 | 3.7699 | 0.10103 | 10.963 | 0.024887 | 36.3156
Planning: Renewables / central | 2049 | 90.3906 | 0.6735 | 45.6906 | 28.5 | 16.2 | 0 | 91.0376 | 0 | 69.7169 | TRUE | FALSE | 1.2128e-15 | 2.04e-14 | 3.8506 | 0.40309 | 7.1231 | 0.023525 | 36.5446
Planning: Renewables / central | 2050 | 92.3066 | 3.3607 | 47.3066 | 28.5 | 16.5 | 0 | 91.3737 | 0 | 69.8975 | TRUE | TRUE | 1.2645e-15 | 3.1399e-14 | 3.9289 | 0 | 1.7543 | 0.11739 | 36.6978
Planning: Renewables / high | 2030 | 34.4879 | 0 | 34.4879 | 0 | 0 | 0 | 84.8499 | 0 | 40.5162 | FALSE | FALSE | 0.043693 | 3.0869 | 1.264 | 0 | 28.4467 | 0 | 35.3569
Planning: Renewables / high | 2031 | 34.6918 | 0 | 33.1918 | 1.5 | 0 | 0 | 83.6356 | 0 | 42.4293 | FALSE | FALSE | 0.058857 | 7.8106 | 1.3128 | 0.069638 | 28.984 | 0 | 34.8127
Planning: Renewables / high | 2032 | 36.9191 | 0.46425 | 33.0191 | 3 | 0.9 | 0 | 81.9133 | 0 | 44.6952 | FALSE | FALSE | 0.041518 | 3.2704 | 1.4035 | 0.080437 | 30.3094 | 0.016216 | 34.107
Planning: Renewables / high | 2033 | 39.0294 | 1.0005 | 32.7294 | 4.5 | 1.8 | 0 | 82.7079 | 0 | 47.0687 | FALSE | FALSE | 0.043062 | 3.4903 | 1.5209 | 0 | 27.4316 | 0.034947 | 34.4246
Planning: Renewables / high | 2034 | 42.99 | 1.0005 | 34.29 | 6 | 2.7 | 0 | 84.0558 | 0 | 49.474 | FALSE | FALSE | 0.026976 | 2.9921 | 1.6971 | 0.16762 | 28.2682 | 0.034947 | 34.9355
Planning: Renewables / high | 2035 | 46.7409 | 2.118 | 35.6409 | 7.5 | 3.6 | 0 | 80.0479 | 0 | 52.0459 | FALSE | FALSE | 0.020298 | 2.1823 | 1.8664 | 0.2376 | 28.6593 | 0.07398 | 33.2582
Planning: Renewables / high | 2036 | 50.5123 | 3.702 | 37.0123 | 9 | 4.5 | 0 | 82.8045 | 0 | 54.3578 | FALSE | FALSE | 0.02197 | 2.5089 | 2.0453 | 0.20194 | 31.2824 | 0.12931 | 34.284
Planning: Renewables / high | 2037 | 53.6546 | 4.584 | 37.7546 | 10.5 | 5.4 | 0 | 85.8745 | 0 | 57.0619 | FALSE | FALSE | 0.024894 | 3.4463 | 2.2219 | 0.25875 | 27.9273 | 0.16011 | 35.3888
Planning: Renewables / high | 2038 | 56.7511 | 5.7728 | 38.4511 | 12 | 6.3 | 0 | 82.2967 | 0 | 59.9405 | FALSE | FALSE | 0.023632 | 3.2754 | 2.372 | 0.1881 | 26.1066 | 0.20164 | 33.8679
Planning: Renewables / high | 2039 | 60.381 | 7.0268 | 39.681 | 13.5 | 7.2 | 0 | 78.6133 | 0 | 62.4396 | FALSE | FALSE | 0.021025 | 2.7423 | 2.5342 | 0.27337 | 26.6751 | 0.24544 | 32.3064
Planning: Renewables / high | 2040 | 63.1129 | 7.7317 | 40.0129 | 15 | 8.1 | 0 | 81.965 | 0 | 64.3685 | FALSE | FALSE | 0.024513 | 3.4756 | 2.6862 | 0.04725 | 25.1243 | 0.27006 | 33.5758
Planning: Renewables / high | 2041 | 65.5926 | 6.4628 | 40.0926 | 16.5 | 9 | 0 | 84.5831 | 0 | 66.2932 | FALSE | FALSE | 0.028221 | 3.93 | 2.8266 | 0.09 | 25.0191 | 0.22574 | 34.5498
Planning: Renewables / high | 2042 | 68.3764 | 5.7165 | 40.4764 | 18 | 9.9 | 0 | 87.477 | 0 | 67.9195 | FALSE | FALSE | 0.029089 | 4.2418 | 2.9746 | 0 | 27.3971 | 0.19967 | 35.6165
Planning: Renewables / high | 2043 | 70.7132 | 3.9915 | 40.4132 | 19.5 | 10.8 | 0 | 89.3385 | 0 | 69.7106 | FALSE | FALSE | 0.028718 | 4.4168 | 3.1008 | 0.10687 | 15.0928 | 0.13942 | 36.3114
Planning: Renewables / high | 2044 | 73.6399 | 3.45 | 40.9399 | 21 | 11.7 | 0 | 92.6094 | 0 | 70.4473 | FALSE | FALSE | 0.028545 | 4.2903 | 3.2457 | 0 | 26.1124 | 0.12051 | 37.5457
Planning: Renewables / high | 2045 | 75.9544 | 1.6275 | 40.8544 | 22.5 | 12.6 | 0 | 94.5636 | 0 | 71.6607 | FALSE | FALSE | 0.025064 | 4.1375 | 3.3636 | 0 | 16.4588 | 0.056847 | 38.2782
Planning: Renewables / high | 2046 | 79.8794 | 1.3125 | 42.3794 | 24 | 13.5 | 0 | 96.9122 | 0 | 72.5984 | FALSE | FALSE | 0.020166 | 3.3674 | 3.5335 | 0 | 18.9091 | 0.045844 | 39.1215
Planning: Renewables / high | 2047 | 83.5194 | 0.7125 | 43.6194 | 25.5 | 14.4 | 0 | 98.3401 | 0 | 73.7863 | FALSE | FALSE | 0.017149 | 2.736 | 3.6936 | 0 | 16.2306 | 0.024887 | 39.6218
Planning: Renewables / high | 2048 | 87.591 | 0.7125 | 45.291 | 27 | 15.3 | 0 | 99.7984 | 0 | 74.8202 | FALSE | FALSE | 0.013144 | 2.0157 | 3.8718 | 0.10103 | 11.248 | 0.024887 | 40.1146
Planning: Renewables / high | 2049 | 90.3906 | 0.6735 | 45.6906 | 28.5 | 16.2 | 0 | 100.6806 | 0 | 75.4029 | FALSE | FALSE | 0.011265 | 1.6505 | 4.0025 | 0.40309 | 10.0521 | 0.023525 | 40.4603
Planning: Renewables / high | 2050 | 94.4066 | 3.3607 | 47.3066 | 30 | 17.1 | 0 | 101.8026 | 0 | 75.8474 | FALSE | FALSE | 0.0078168 | 1.0849 | 4.1766 | 0 | 1.7543 | 0.11739 | 40.9108
Test: Proposed / central / ext0 / coal4 / slow | 2030 | 34.4879 | 0 | 34.4879 | 0 | 0 | 0 | 83.8047 | 0 | 40.4038 | FALSE | FALSE | 0.026374 | 2.5779 | 1.2636 | 0 | 15.8728 | 0 | 35.007
Test: Proposed / central / ext0 / coal4 / slow | 2031 | 34.8079 | 0 | 33.3079 | 1.5 | 0 | 0 | 83.2558 | 0 | 41.8237 | FALSE | FALSE | 0.037408 | 2.6094 | 1.2878 | 0 | 12.8057 | 0 | 34.6745
Test: Proposed / central / ext0 / coal4 / slow | 2032 | 36.5889 | 0 | 32.6889 | 3 | 0.9 | 0 | 81.7714 | 0 | 43.6852 | FALSE | FALSE | 0.025281 | 2.7819 | 1.392 | 0 | 7.9611 | 0 | 34.0272
Test: Proposed / central / ext0 / coal4 / slow | 2033 | 38.0289 | 0 | 31.7289 | 4.5 | 1.8 | 0 | 84.7758 | 0 | 43.922 | FALSE | FALSE | 0.037792 | 3.3488 | 1.4912 | 0 | 8.9499 | 0 | 35.0502
Test: Proposed / central / ext0 / coal4 / slow | 2034 | 42.2689 | 0 | 33.5689 | 6 | 2.7 | 0 | 88.4519 | 0 | 44.5536 | FALSE | FALSE | 0.021599 | 2.6662 | 1.6733 | 0 | 8.9499 | 0 | 36.3261
Test: Proposed / central / ext0 / coal4 / slow | 2035 | 45.0189 | 0 | 33.9189 | 7.5 | 3.6 | 2 | 79.2615 | 14.9037 | 45.3193 | FALSE | FALSE | 0.012928 | 1.4818 | 1.8013 | 0 | 7.9497 | 0 | 45.0934
Test: Proposed / central / ext0 / coal4 / slow | 2036 | 47.1469 | 0 | 33.6469 | 9 | 4.5 | 4 | 77.7748 | 29.8073 | 46.0962 | FALSE | FALSE | 0.014239 | 5.2971 | 1.9591 | 0 | 9.1995 | 0 | 56.8806
Test: Proposed / central / ext0 / coal4 / slow | 2037 | 49.5019 | 0 | 33.6019 | 10.5 | 5.4 | 6 | 72.0419 | 35.2625 | 47.2756 | FALSE | FALSE | 0.010983 | 4.7403 | 2.0713 | 0 | 9.5345 | 0 | 59.7271
Test: Proposed / central / ext0 / coal4 / slow | 2038 | 51.2919 | 0 | 32.9919 | 12 | 6.3 | 8 | 67.1106 | 41.7721 | 48.3667 | FALSE | FALSE | 0.0089237 | 4.4089 | 2.1695 | 0 | 12.5843 | 0 | 63.6676
Test: Proposed / central / ext0 / coal4 / slow | 2039 | 53.8099 | 0 | 33.1099 | 13.5 | 7.2 | 8 | 62.8352 | 42.0988 | 49.3751 | FALSE | FALSE | 0.0074583 | 4.0731 | 2.2905 | 0 | 15.2843 | 0 | 62.0608
Test: Proposed / central / ext0 / coal4 / slow | 2040 | 55.4599 | 0 | 32.3599 | 15 | 8.1 | 8 | 66.072 | 41.3622 | 49.8951 | FALSE | FALSE | 0.0094759 | 4.7163 | 2.4007 | 0 | 17.0843 | 0 | 62.2244
Test: Proposed / central / ext0 / coal4 / slow | 2041 | 59.2799 | 0 | 33.7799 | 16.5 | 9 | 8 | 61.0048 | 41.458 | 50.5935 | FALSE | FALSE | 0.0044686 | 3.5707 | 2.5655 | 0 | 17.9843 | 0 | 60.1449
Test: Proposed / central / ext0 / coal4 / slow | 2042 | 62.6599 | 0 | 34.7599 | 18 | 9.9 | 8 | 51.0104 | 43.2608 | 51.033 | TRUE | FALSE | 1.8296e-15 | 2.4257 | 2.7187 | 0 | 17.9843 | 0 | 57.722
Test: Proposed / central / ext0 / coal4 / slow | 2043 | 66.8999 | 0 | 36.5999 | 19.5 | 10.8 | 8 | 45.2655 | 42.9352 | 51.3088 | TRUE | FALSE | 1.7493e-15 | 1.4929 | 2.9019 | 0 | 17.9843 | 0 | 54.9831
Test: Proposed / central / ext0 / coal4 / slow | 2044 | 70.1899 | 0 | 37.4899 | 21 | 11.7 | 8 | 42.9413 | 42.5233 | 52.1064 | TRUE | FALSE | 2.0753e-15 | 0.84688 | 2.97 | 0 | 17.9843 | 0 | 53.7376
Test: Proposed / central / ext0 / coal4 / slow | 2045 | 74.3269 | 0 | 39.2269 | 22.5 | 12.6 | 8 | 68.7837 | 0.017447 | 52.5768 | TRUE | FALSE | 2.4727e-15 | 0.48986 | 3.0934 | 0 | 17.9843 | 0 | 26.1715
Test: Proposed / central / ext0 / coal4 / slow | 2046 | 78.5669 | 0 | 41.0669 | 24 | 13.5 | 8 | 63.2385 | 0 | 53.7776 | TRUE | FALSE | 2.082e-15 | 0.067218 | 3.22 | 0 | 17.5568 | 0 | 23.9872
Test: Proposed / central / ext0 / coal4 / slow | 2047 | 82.8069 | 0 | 42.9069 | 25.5 | 14.4 | 8 | 57.1098 | 0 | 54.5218 | TRUE | FALSE | 1.6428e-15 | 1.4232e-14 | 3.1691 | 0 | 12.5543 | 0 | 21.6926
Test: Proposed / central / ext0 / coal4 / slow | 2048 | 84.6469 | 0 | 44.7469 | 25.5 | 14.4 | 8 | 50.9261 | 0 | 55.086 | TRUE | TRUE | 1.4642e-15 | 1.3486e-14 | 3.1149 | 0 | 8.9543 | 0 | 19.3925
Test: Proposed / central / ext0 / coal4 / slow | 2049 | 85.5889 | 0 | 45.6889 | 25.5 | 14.4 | 8 | 45.5131 | 0 | 55.4338 | TRUE | TRUE | 1.2401e-15 | 1.1063e-14 | 3.1021 | 0 | 5.3543 | 0 | 17.3864
Test: Proposed / central / ext0 / coal4 / slow | 2050 | 83.8459 | 0 | 43.9459 | 25.5 | 14.4 | 8 | 37.9096 | 0 | 55.5989 | TRUE | TRUE | 9.6523e-16 | 9.4147e-15 | 3.0076 | 0 | 1.3157 | 0 | 14.6139
Test: Renewables / central / ext0 / coal0 / slow | 2030 | 34.4879 | 0 | 34.4879 | 0 | 0 | 0 | 83.8047 | 0 | 40.4038 | FALSE | FALSE | 0.026374 | 2.5779 | 1.2636 | 0 | 24.5961 | 0 | 35.007
Test: Renewables / central / ext0 / coal0 / slow | 2031 | 34.8079 | 0 | 33.3079 | 1.5 | 0 | 0 | 82.6114 | 0 | 42.1483 | FALSE | FALSE | 0.034177 | 2.5406 | 1.2871 | 0 | 26.1298 | 0 | 34.4696
Test: Renewables / central / ext0 / coal0 / slow | 2032 | 36.5889 | 0 | 32.6889 | 3 | 0.9 | 0 | 80.6527 | 0 | 44.338 | FALSE | FALSE | 0.021599 | 2.6532 | 1.3907 | 0 | 26.6919 | 0 | 33.6644
Test: Renewables / central / ext0 / coal0 / slow | 2033 | 38.0289 | 0 | 31.7289 | 4.5 | 1.8 | 0 | 81.4456 | 0 | 46.2145 | FALSE | FALSE | 0.021796 | 2.9976 | 1.4897 | 0 | 24.2932 | 0 | 33.9579
Test: Renewables / central / ext0 / coal0 / slow | 2034 | 42.2689 | 0 | 33.5689 | 6 | 2.7 | 0 | 82.4499 | 0 | 48.355 | FALSE | FALSE | 0.015259 | 2.2165 | 1.6702 | 0 | 23.6736 | 0 | 34.339
Test: Renewables / central / ext0 / coal0 / slow | 2035 | 45.0189 | 0 | 33.9189 | 7.5 | 3.6 | 0 | 78.1391 | 0 | 50.5021 | FALSE | FALSE | 0.0096431 | 1.6437 | 1.8035 | 0 | 23.4464 | 0 | 32.528
Test: Renewables / central / ext0 / coal0 / slow | 2036 | 47.1469 | 0 | 33.6469 | 9 | 4.5 | 0 | 80.1894 | 0 | 52.3404 | FALSE | FALSE | 0.013176 | 2.2229 | 1.9297 | 0 | 23.4243 | 0 | 33.2634
Test: Renewables / central / ext0 / coal0 / slow | 2037 | 49.5019 | 0 | 33.6019 | 10.5 | 5.4 | 0 | 82.2845 | 0 | 54.1297 | FALSE | FALSE | 0.01527 | 2.6761 | 2.0679 | 0 | 24.097 | 0 | 34.0242
Test: Renewables / central / ext0 / coal0 / slow | 2038 | 51.2919 | 0 | 32.9919 | 12 | 6.3 | 0 | 78.1086 | 0 | 56.3088 | FALSE | FALSE | 0.014625 | 2.6224 | 2.1722 | 0 | 21.884 | 0 | 32.2643
Test: Renewables / central / ext0 / coal0 / slow | 2039 | 53.8099 | 0 | 33.1099 | 13.5 | 7.2 | 0 | 73.8296 | 0 | 58.3105 | FALSE | FALSE | 0.01246 | 2.2382 | 2.2932 | 0 | 23.5366 | 0 | 30.4567
Test: Renewables / central / ext0 / coal0 / slow | 2040 | 55.4599 | 0 | 32.3599 | 15 | 8.1 | 0 | 76.2588 | 0 | 60.0243 | FALSE | FALSE | 0.016132 | 3.0585 | 2.4132 | 0 | 20.2299 | 0 | 31.3614
Test: Renewables / central / ext0 / coal0 / slow | 2041 | 59.2799 | 0 | 33.7799 | 16.5 | 9 | 0 | 78.2037 | 0 | 61.407 | FALSE | FALSE | 0.013846 | 2.6134 | 2.5851 | 0 | 20.9914 | 0 | 32.0755
Test: Renewables / central / ext0 / coal0 / slow | 2042 | 62.6599 | 0 | 34.7599 | 18 | 9.9 | 0 | 80.2563 | 0 | 62.5526 | FALSE | FALSE | 0.011929 | 2.3509 | 2.7415 | 0 | 25.9254 | 0 | 32.8256
Test: Renewables / central / ext0 / coal0 / slow | 2043 | 66.8999 | 0 | 36.5999 | 19.5 | 10.8 | 0 | 81.6624 | 0 | 64.1673 | FALSE | FALSE | 0.0065589 | 1.7328 | 2.9254 | 0 | 15.8726 | 0 | 33.3226
Test: Renewables / central / ext0 / coal0 / slow | 2044 | 70.1899 | 0 | 37.4899 | 21 | 11.7 | 0 | 84.2935 | 0 | 64.8709 | FALSE | FALSE | 0.0051773 | 1.489 | 3.0774 | 0 | 26.8044 | 0 | 34.2781
Test: Renewables / central / ext0 / coal0 / slow | 2045 | 74.3269 | 0 | 39.2269 | 22.5 | 12.6 | 0 | 86.3333 | 0 | 66.2723 | TRUE | FALSE | 1.1663e-15 | 1.081 | 3.266 | 0 | 15.2868 | 0 | 34.9682
Test: Renewables / central / ext0 / coal0 / slow | 2046 | 78.5669 | 0 | 41.0669 | 24 | 13.5 | 0 | 88.233 | 0 | 67.4602 | TRUE | FALSE | 1.2668e-15 | 0.61317 | 3.4507 | 0 | 16.5504 | 0 | 35.6031
Test: Renewables / central / ext0 / coal0 / slow | 2047 | 82.8069 | 0 | 42.9069 | 25.5 | 14.4 | 0 | 89.3438 | 0 | 68.3829 | TRUE | FALSE | 1.2422e-15 | 0.25598 | 3.6193 | 0 | 14.7053 | 0 | 35.968
Test: Renewables / central / ext0 / coal0 / slow | 2048 | 87.0469 | 0 | 44.7469 | 27 | 15.3 | 0 | 90.3906 | 0 | 69.1312 | TRUE | FALSE | 1.2431e-15 | 0.050117 | 3.761 | 0 | 11.248 | 0 | 36.317
Test: Renewables / central / ext0 / coal0 / slow | 2049 | 90.3889 | 0 | 45.6889 | 28.5 | 16.2 | 0 | 91.0378 | 0 | 69.7656 | TRUE | TRUE | 1.2046e-15 | 2.2531e-14 | 3.8504 | 0 | 8.3831 | 0 | 36.5389
Test: Renewables / central / ext0 / coal0 / slow | 2050 | 91.0459 | 0 | 43.9459 | 30 | 17.1 | 0 | 91.3629 | 0 | 69.8189 | TRUE | FALSE | 1.2363e-15 | 2.2368e-14 | 3.9072 | 0 | 1.7543 | 0 | 36.7208
Test: Proposed / central / ext10 / coal4 / slow | 2030 | 34.4879 | 0 | 34.4879 | 0 | 0 | 0 | 83.8047 | 0 | 40.4038 | FALSE | FALSE | 0.026374 | 2.5779 | 1.2636 | 0 | 15.8728 | 0 | 35.007
Test: Proposed / central / ext10 / coal4 / slow | 2031 | 34.6918 | 0 | 33.1918 | 1.5 | 0 | 0 | 83.2492 | 0 | 41.8078 | FALSE | FALSE | 0.038244 | 2.659 | 1.2843 | 0.11606 | 12.8057 | 0 | 34.6719
Test: Proposed / central / ext10 / coal4 / slow | 2032 | 36.9191 | 0.46425 | 33.0191 | 3 | 0.9 | 0 | 81.7826 | 0 | 43.71 | FALSE | FALSE | 0.023585 | 2.6606 | 1.4013 | 0.13406 | 7.9611 | 0.027026 | 34.036
Test: Proposed / central / ext10 / coal4 / slow | 2033 | 39.0294 | 1.0005 | 32.7294 | 4.5 | 1.8 | 0 | 84.823 | 0 | 44.0162 | FALSE | FALSE | 0.025657 | 2.9453 | 1.5234 | 0 | 8.9499 | 0.058244 | 35.0798
Test: Proposed / central / ext10 / coal4 / slow | 2034 | 42.99 | 1.0005 | 34.29 | 6 | 2.7 | 0 | 88.4738 | 0 | 44.6083 | FALSE | FALSE | 0.019598 | 2.4102 | 1.6965 | 0.27937 | 8.9499 | 0.058244 | 36.3436
Test: Proposed / central / ext10 / coal4 / slow | 2035 | 46.7409 | 2.118 | 35.6409 | 7.5 | 3.6 | 2 | 79.3027 | 14.9037 | 45.4613 | FALSE | FALSE | 0.0091955 | 1.0286 | 1.8571 | 0.396 | 7.9497 | 0.1233 | 45.1263
Test: Proposed / central / ext10 / coal4 / slow | 2036 | 50.3962 | 3.5859 | 36.8962 | 9 | 4.5 | 4 | 77.8564 | 29.8073 | 46.3903 | FALSE | FALSE | 0.0078696 | 4.1261 | 2.06 | 0.45262 | 9.1995 | 0.21551 | 56.9344
Test: Proposed / central / ext10 / coal4 / slow | 2037 | 53.9848 | 4.9142 | 38.0848 | 10.5 | 5.4 | 6 | 72.1461 | 35.2625 | 47.6785 | FALSE | FALSE | 0.0025475 | 3.2157 | 2.2171 | 0.56531 | 9.5345 | 0.29388 | 59.7853
Test: Proposed / central / ext10 / coal4 / slow | 2038 | 57.7516 | 6.7732 | 39.4516 | 12 | 6.3 | 8 | 67.2611 | 41.7721 | 48.9465 | TRUE | FALSE | 1.6871e-15 | 2.3369 | 2.3888 | 0.3135 | 12.5843 | 0.39431 | 63.7447
Test: Proposed / central / ext10 / coal4 / slow | 2039 | 61.1021 | 7.7479 | 40.4021 | 13.5 | 7.2 | 8 | 62.9819 | 42.0988 | 50.0462 | TRUE | FALSE | 1.9182e-15 | 1.8902 | 2.5459 | 0.735 | 15.2843 | 0.46731 | 62.1361
Test: Proposed / central / ext10 / coal4 / slow | 2040 | 64.8349 | 9.4537 | 41.7349 | 15 | 8.1 | 8 | 64.4521 | 43.18 | 50.7587 | TRUE | FALSE | 1.8131e-15 | 1.88 | 2.7219 | 0.47475 | 17.0843 | 0.5734 | 63.2996
Test: Proposed / central / ext10 / coal4 / slow | 2041 | 68.9581 | 9.8282 | 43.4581 | 16.5 | 9 | 8 | 59.2451 | 43.3022 | 51.475 | TRUE | FALSE | 1.8423e-15 | 1.1834 | 2.8923 | 0.48656 | 17.9843 | 0.59174 | 61.1919
Test: Proposed / central / ext10 / coal4 / slow | 2042 | 72.5291 | 9.8692 | 44.6291 | 18 | 9.9 | 8 | 51.0775 | 43.2608 | 51.9741 | TRUE | FALSE | 1.8732e-15 | 0.60136 | 2.9987 | 0.43125 | 17.9843 | 0.59965 | 57.7523
Test: Proposed / central / ext10 / coal4 / slow | 2043 | 76.1725 | 9.4507 | 45.8725 | 19.5 | 10.8 | 8 | 45.299 | 42.9352 | 52.1793 | TRUE | FALSE | 1.7653e-15 | 0.29692 | 3.1018 | 0.49162 | 17.9843 | 0.56843 | 55.0036
Test: Proposed / central / ext10 / coal4 / slow | 2044 | 80.211 | 10.0211 | 47.511 | 21 | 11.7 | 8 | 42.9603 | 42.5233 | 53.0648 | TRUE | FALSE | 2.0775e-15 | 0.047771 | 3.1617 | 0.45563 | 17.9843 | 0.60991 | 53.7513
Test: Proposed / central / ext10 / coal4 / slow | 2045 | 83.6074 | 9.2805 | 48.5074 | 22.5 | 12.6 | 8 | 68.8117 | 0 | 53.4387 | TRUE | FALSE | 2.5042e-15 | 0.0082263 | 3.2735 | 0.07875 | 17.1668 | 0.54485 | 26.153
Test: Proposed / central / ext10 / coal4 / slow | 2046 | 85.5921 | 7.6252 | 48.6921 | 23.4 | 13.5 | 8 | 63.2453 | 0 | 54.4566 | TRUE | TRUE | 2.0565e-15 | 1.8268e-14 | 3.226 | 0.15 | 16.1543 | 0.45264 | 23.985
Test: Proposed / central / ext10 / coal4 / slow | 2047 | 86.2359 | 6.429 | 49.3359 | 23.4 | 13.5 | 8 | 57.1148 | 0 | 54.9241 | TRUE | TRUE | 1.6469e-15 | 1.4317e-14 | 3.156 | 0 | 12.5543 | 0.37427 | 21.6952
Test: Proposed / central / ext10 / coal4 / slow | 2048 | 86.0044 | 4.5259 | 49.1044 | 23.4 | 13.5 | 8 | 50.929 | 0 | 55.3028 | TRUE | TRUE | 1.4642e-15 | 1.3586e-14 | 3.1141 | 0.3465 | 8.9543 | 0.27384 | 19.397
Test: Proposed / central / ext10 / coal4 / slow | 2049 | 86.0406 | 4.1235 | 49.1406 | 23.4 | 13.5 | 8 | 45.5146 | 0 | 55.5313 | TRUE | TRUE | 1.2401e-15 | 1.1021e-14 | 3.0836 | 0.67181 | 5.3543 | 0.24005 | 17.3931
Test: Proposed / central / ext10 / coal4 / slow | 2050 | 85.8341 | 4.9882 | 48.9341 | 23.4 | 13.5 | 8 | 37.9123 | 0 | 55.8681 | TRUE | TRUE | 9.6523e-16 | 9.3863e-15 | 3.029 | 0 | 1.3157 | 0.29039 | 14.6192
Test: Proposed / central / ext5 / coal6 / slow | 2030 | 34.4879 | 0 | 34.4879 | 0 | 0 | 0 | 83.8047 | 0 | 40.4038 | FALSE | FALSE | 0.026374 | 2.5779 | 1.2636 | 0 | 15.8728 | 0 | 35.007
Test: Proposed / central / ext5 / coal6 / slow | 2031 | 34.6918 | 0 | 33.1918 | 1.5 | 0 | 0 | 83.2492 | 0 | 41.8078 | FALSE | FALSE | 0.038244 | 2.659 | 1.2843 | 0.069638 | 12.8057 | 0 | 34.6719
Test: Proposed / central / ext5 / coal6 / slow | 2032 | 36.9191 | 0.46425 | 33.0191 | 3 | 0.9 | 0 | 81.7835 | 0 | 43.6968 | FALSE | FALSE | 0.023456 | 2.6497 | 1.4014 | 0.080437 | 7.9611 | 0.016216 | 34.0356
Test: Proposed / central / ext5 / coal6 / slow | 2033 | 39.0294 | 1.0005 | 32.7294 | 4.5 | 1.8 | 0 | 84.8255 | 0 | 43.9875 | FALSE | FALSE | 0.025186 | 2.9222 | 1.5237 | 0 | 8.9499 | 0.034947 | 35.0784
Test: Proposed / central / ext5 / coal6 / slow | 2034 | 42.99 | 1.0005 | 34.29 | 6 | 2.7 | 0 | 88.4763 | 0 | 44.5796 | FALSE | FALSE | 0.019416 | 2.3874 | 1.6972 | 0.16762 | 9.5 | 0.034947 | 36.3417
Test: Proposed / central / ext5 / coal6 / slow | 2035 | 46.7409 | 2.118 | 35.6409 | 7.5 | 3.6 | 2 | 79.3062 | 14.9037 | 45.4006 | FALSE | FALSE | 0.0088534 | 0.99526 | 1.8589 | 0.2376 | 9.05 | 0.07398 | 45.1223
Test: Proposed / central / ext5 / coal6 / slow | 2036 | 50.5123 | 3.702 | 37.0123 | 9 | 4.5 | 4 | 77.8626 | 29.8073 | 46.286 | FALSE | FALSE | 0.0073504 | 3.9989 | 2.0661 | 0.20194 | 10.2999 | 0.12931 | 56.9262
Test: Proposed / central / ext5 / coal6 / slow | 2037 | 53.6546 | 4.584 | 37.7546 | 10.5 | 5.4 | 6 | 72.1451 | 35.2625 | 47.5065 | FALSE | FALSE | 0.0026476 | 3.2307 | 2.2089 | 0.25875 | 10.6348 | 0.16011 | 59.7697
Test: Proposed / central / ext5 / coal6 / slow | 2038 | 56.7511 | 5.7728 | 38.4511 | 12 | 6.3 | 8 | 67.2509 | 41.7721 | 48.6884 | FALSE | FALSE | 1.6636e-15 | 2.5239 | 2.3595 | 0.1881 | 13.6846 | 0.20164 | 63.72
Test: Proposed / central / ext5 / coal6 / slow | 2039 | 60.381 | 7.0268 | 39.681 | 13.5 | 7.2 | 10 | 57.4059 | 47.8705 | 49.9592 | TRUE | FALSE | 1.0359e-15 | 1.4541 | 2.5176 | 0.27337 | 15.8345 | 0.24544 | 65.4298
Test: Proposed / central / ext5 / coal6 / slow | 2040 | 63.1129 | 7.7317 | 40.0129 | 15 | 8.1 | 12 | 52.3639 | 55.3051 | 50.717 | TRUE | FALSE | 8.6561e-16 | 1.2484 | 2.6533 | 0.04725 | 17.0843 | 0.27006 | 70.0216
Test: Proposed / central / ext5 / coal6 / slow | 2041 | 65.5926 | 6.4628 | 40.0926 | 16.5 | 9 | 12 | 46.9555 | 55.5329 | 51.3045 | TRUE | FALSE | 9.0958e-16 | 0.97211 | 2.7654 | 0.09 | 17.9843 | 0.22574 | 67.9016
Test: Proposed / central / ext5 / coal6 / slow | 2042 | 68.3764 | 5.7165 | 40.4764 | 18 | 9.9 | 12 | 40.0856 | 55.3645 | 51.7916 | TRUE | FALSE | 8.0096e-16 | 0.55112 | 2.8395 | 0 | 17.9843 | 0.19967 | 64.7927
Test: Proposed / central / ext5 / coal6 / slow | 2043 | 70.7132 | 3.9915 | 40.4132 | 19.5 | 10.8 | 12 | 34.7477 | 54.6722 | 51.9435 | TRUE | FALSE | 7.2419e-16 | 0.36867 | 2.8635 | 0.10687 | 17.9843 | 0.13942 | 61.889
Test: Proposed / central / ext5 / coal6 / slow | 2044 | 73.6399 | 3.45 | 40.9399 | 21 | 11.7 | 12 | 32.8213 | 53.8715 | 52.7375 | TRUE | FALSE | 9.0124e-16 | 0.12952 | 2.9142 | 0 | 17.9843 | 0.12051 | 60.4457
Test: Proposed / central / ext5 / coal6 / slow | 2045 | 75.9544 | 1.6275 | 40.8544 | 22.5 | 12.6 | 12 | 68.7957 | 0.0083632 | 53.1988 | TRUE | FALSE | 2.4738e-15 | 0.086835 | 3.1105 | 0 | 17.5568 | 0.056847 | 26.155
Test: Proposed / central / ext5 / coal6 / slow | 2046 | 79.8794 | 1.3125 | 42.3794 | 24 | 13.5 | 12 | 63.2403 | 0 | 54.3795 | TRUE | FALSE | 2.0841e-15 | 1.8254e-14 | 3.1022 | 0 | 16.1543 | 0.045844 | 23.9807
Test: Proposed / central / ext5 / coal6 / slow | 2047 | 81.1194 | 0.7125 | 43.6194 | 24 | 13.5 | 12 | 57.1107 | 0 | 54.9303 | TRUE | TRUE | 1.649e-15 | 1.4161e-14 | 3.0355 | 0 | 12.5543 | 0.024887 | 21.6905
Test: Proposed / central / ext5 / coal6 / slow | 2048 | 82.791 | 0.7125 | 45.291 | 24 | 13.5 | 12 | 50.9266 | 0 | 55.4715 | TRUE | TRUE | 1.4704e-15 | 1.3557e-14 | 3.0102 | 0.10103 | 8.9543 | 0.024887 | 19.3925
Test: Proposed / central / ext5 / coal6 / slow | 2049 | 83.1906 | 0.6735 | 45.6906 | 24 | 13.5 | 12 | 45.513 | 0 | 55.7479 | TRUE | TRUE | 1.2381e-15 | 1.1106e-14 | 2.9967 | 0.40309 | 5.3543 | 0.023525 | 17.3888
Test: Proposed / central / ext5 / coal6 / slow | 2050 | 84.8066 | 3.3607 | 47.3066 | 24 | 13.5 | 12 | 37.9115 | 0 | 56.1762 | TRUE | TRUE | 9.6523e-16 | 9.3863e-15 | 3.0036 | 0 | 1.3157 | 0.11739 | 14.6132
Faster: Proposed / central | 2030 | 34.4879 | 0 | 34.4879 | 0 | 0 | 0 | 83.8047 | 0 | 40.4038 | FALSE | FALSE | 0.026374 | 2.5779 | 1.2636 | 0 | 17.8013 | 0 | 35.007
Faster: Proposed / central | 2031 | 37.1918 | 0 | 33.1918 | 4 | 0 | 0 | 83.3594 | 0 | 41.9541 | FALSE | FALSE | 0.0215 | 1.6089 | 1.3966 | 0.069638 | 15.0377 | 0 | 34.7338
Faster: Proposed / central | 2032 | 41.0191 | 0.46425 | 33.0191 | 8 | 0 | 0 | 81.9081 | 0 | 43.9188 | FALSE | FALSE | 0.010278 | 1.0699 | 1.5853 | 0.080437 | 10.664 | 0.016216 | 34.1125
Faster: Proposed / central | 2033 | 48.0094 | 1.0005 | 36.4094 | 11.6 | 0 | 0 | 85.0786 | 0 | 44.5426 | FALSE | FALSE | 1.5583e-15 | 0.2304 | 1.8689 | 0 | 11.2142 | 0.034947 | 35.1981
Faster: Proposed / central | 2034 | 55.01 | 1.0005 | 39.81 | 15.2 | 0 | 0 | 88.7354 | 0 | 45.3231 | TRUE | FALSE | 2.038e-15 | 0.017707 | 2.0613 | 0.16762 | 11.2142 | 0.034947 | 36.4426
Faster: Proposed / central | 2035 | 61.8009 | 2.118 | 43.0009 | 18.8 | 0 | 2 | 79.4778 | 14.9037 | 46.3359 | TRUE | TRUE | 1.5574e-15 | 7.3115e-15 | 2.1542 | 0.2376 | 10.214 | 0.07398 | 45.1628
Faster: Proposed / central | 2036 | 68.6123 | 3.702 | 46.2123 | 22.4 | 0 | 4 | 78.0054 | 29.8073 | 47.4123 | TRUE | FALSE | 1.9132e-15 | 0.016002 | 2.6794 | 0.20194 | 10.0339 | 0.12931 | 56.9314
Faster: Proposed / central | 2037 | 72.5946 | 4.584 | 48.7946 | 23.8 | 0 | 6 | 72.2673 | 35.2625 | 48.6973 | TRUE | TRUE | 1.2577e-15 | 7.5637e-15 | 2.7542 | 0.25875 | 9.4588 | 0.16011 | 59.763
Faster: Proposed / central | 2038 | 75.1311 | 5.7728 | 51.3311 | 23.8 | 0 | 8 | 67.3555 | 41.7721 | 49.8617 | TRUE | TRUE | 1.6567e-15 | 1.1138e-14 | 2.7839 | 0.1881 | 12.5087 | 0.20164 | 63.6987
Faster: Proposed / central | 2039 | 78.201 | 7.0268 | 54.401 | 23.8 | 0 | 8 | 63.0516 | 42.0988 | 50.9135 | TRUE | TRUE | 1.8573e-15 | 2.0808e-14 | 2.8353 | 0.27337 | 14.1041 | 0.24544 | 62.0618
Faster: Proposed / central | 2040 | 80.4729 | 7.7317 | 56.5729 | 23.9 | 0 | 8 | 64.5115 | 43.18 | 51.4893 | TRUE | TRUE | 1.8245e-15 | 4.2618e-14 | 2.9882 | 0.04725 | 14.9619 | 0.27006 | 63.1758
Faster: Proposed / central | 2041 | 82.3926 | 6.4628 | 58.4926 | 23.9 | 0 | 8 | 59.2766 | 43.3022 | 52.0802 | TRUE | TRUE | 1.846e-15 | 5.9664e-14 | 2.9982 | 0.09 | 15.3748 | 0.22574 | 61.0623
Faster: Proposed / central | 2042 | 81.5364 | 5.7165 | 57.0364 | 24.5 | 0 | 8 | 51.0903 | 43.2608 | 52.2589 | TRUE | TRUE | 1.8402e-15 | 5.2815e-14 | 3.0045 | 0 | 16.8696 | 0.19967 | 57.6326
Faster: Proposed / central | 2043 | 82.5532 | 3.9915 | 56.0532 | 26.5 | 0 | 8 | 45.3032 | 42.9352 | 52.2918 | TRUE | TRUE | 1.7653e-15 | 6.0908e-14 | 2.984 | 0.10687 | 15.9922 | 0.13942 | 54.9038
Faster: Proposed / central | 2044 | 83.2599 | 3.45 | 55.6599 | 27.6 | 0 | 8 | 42.963 | 42.5233 | 52.9164 | TRUE | TRUE | 2.0775e-15 | 6.37e-14 | 2.9553 | 0 | 17.5848 | 0.12051 | 53.6656
Faster: Proposed / central | 2045 | 87.1744 | 1.6275 | 55.5744 | 31.6 | 0 | 8 | 68.8146 | 0 | 53.3369 | TRUE | TRUE | 2.4695e-15 | 3.2401e-14 | 3.1218 | 0 | 14.4 | 0.056847 | 26.0114
Faster: Proposed / central | 2046 | 86.8594 | 1.3125 | 55.2594 | 31.6 | 0 | 8 | 63.2477 | 0 | 54.2222 | TRUE | TRUE | 2.0671e-15 | 2.769e-14 | 3.0767 | 0 | 14.4 | 0.045844 | 23.8866
Faster: Proposed / central | 2047 | 86.2594 | 0.7125 | 54.6594 | 31.6 | 0 | 8 | 57.1167 | 0 | 54.6326 | TRUE | TRUE | 1.6407e-15 | 1.5795e-14 | 3.0295 | 0 | 10.8 | 0.024887 | 21.6302
Faster: Proposed / central | 2048 | 86.091 | 0.7125 | 54.491 | 31.6 | 0 | 8 | 50.9311 | 0 | 55.0322 | TRUE | TRUE | 1.4683e-15 | 1.3614e-14 | 2.9976 | 0.10103 | 7.2 | 0.024887 | 19.357
Faster: Proposed / central | 2049 | 84.6506 | 0.6735 | 53.0506 | 31.6 | 0 | 8 | 45.5162 | 0 | 55.1657 | TRUE | TRUE | 1.2422e-15 | 1.1077e-14 | 2.937 | 0.40309 | 3.6 | 0.023525 | 17.3656
Faster: Proposed / central | 2050 | 84.4266 | 3.3607 | 52.8266 | 31.6 | 0 | 8 | 37.9141 | 0 | 55.4505 | TRUE | TRUE | 9.6724e-16 | 9.3863e-15 | 2.8913 | 0 | 0 | 0.11739 | 14.5987
Test: Proposed / central / ext0 / coal4 / fast | 2030 | 34.4879 | 0 | 34.4879 | 0 | 0 | 0 | 83.8047 | 0 | 40.4038 | FALSE | FALSE | 0.026374 | 2.5779 | 1.2636 | 0 | 17.8013 | 0 | 35.007
Test: Proposed / central / ext0 / coal4 / fast | 2031 | 37.3079 | 0 | 33.3079 | 4 | 0 | 0 | 83.365 | 0 | 41.9702 | FALSE | FALSE | 0.02106 | 1.5628 | 1.401 | 0 | 15.0377 | 0 | 34.7367
Test: Proposed / central / ext0 / coal4 / fast | 2032 | 40.6889 | 0 | 32.6889 | 8 | 0 | 0 | 81.8982 | 0 | 43.9074 | FALSE | FALSE | 0.011004 | 1.1605 | 1.5728 | 0 | 10.664 | 0 | 34.1059
Test: Proposed / central / ext0 / coal4 / fast | 2033 | 47.0089 | 0 | 35.4089 | 11.6 | 0 | 0 | 85.0579 | 0 | 44.4789 | FALSE | FALSE | 0.0014273 | 0.36132 | 1.8358 | 0 | 11.2142 | 0 | 35.1877
Test: Proposed / central / ext0 / coal4 / fast | 2034 | 54.2889 | 0 | 39.0889 | 15.2 | 0 | 0 | 88.7278 | 0 | 45.2975 | TRUE | FALSE | 2.0277e-15 | 0.026092 | 2.0528 | 0 | 11.2142 | 0 | 36.4369
Test: Proposed / central / ext0 / coal4 / fast | 2035 | 60.0789 | 0 | 41.2789 | 18.8 | 0 | 2 | 79.4751 | 14.9037 | 46.255 | TRUE | TRUE | 1.5476e-15 | 7.2333e-15 | 2.1438 | 0 | 10.214 | 0 | 45.1583
Test: Proposed / central / ext0 / coal4 / fast | 2036 | 65.2469 | 0 | 42.8469 | 22.4 | 0 | 4 | 78.0036 | 29.8073 | 47.2218 | TRUE | FALSE | 1.9194e-15 | 0.15314 | 2.6292 | 0 | 11.4639 | 0 | 56.9252
Test: Proposed / central / ext0 / coal4 / fast | 2037 | 70.6419 | 0 | 44.6419 | 26 | 0 | 6 | 72.2664 | 35.2625 | 48.5911 | TRUE | FALSE | 1.2475e-15 | 0.011386 | 2.7936 | 0 | 10.8238 | 0 | 59.7558
Test: Proposed / central / ext0 / coal4 / fast | 2038 | 73.9719 | 0 | 45.8719 | 28.1 | 0 | 8 | 67.3546 | 41.7721 | 49.7855 | TRUE | TRUE | 1.6636e-15 | 1.1145e-14 | 2.8291 | 0 | 12.7037 | 0 | 63.6905
Test: Proposed / central / ext0 / coal4 / fast | 2039 | 76.2299 | 0 | 47.8299 | 28.4 | 0 | 8 | 63.0508 | 42.0988 | 50.7942 | TRUE | TRUE | 1.8573e-15 | 1.2744e-14 | 2.8895 | 0 | 15.7941 | 0 | 62.0512
Test: Proposed / central / ext0 / coal4 / fast | 2040 | 80.0199 | 0 | 48.9199 | 31.1 | 0 | 8 | 64.5109 | 43.18 | 51.424 | TRUE | TRUE | 1.8245e-15 | 3.7822e-14 | 3.0484 | 0 | 14.9619 | 0 | 63.1655
Test: Proposed / central / ext0 / coal4 / fast | 2041 | 83.2799 | 0 | 52.1799 | 31.1 | 0 | 8 | 59.2762 | 43.3022 | 52.1061 | TRUE | TRUE | 1.846e-15 | 6.1569e-14 | 3.0352 | 0 | 14.9848 | 0 | 61.054
Test: Proposed / central / ext0 / coal4 / fast | 2042 | 82.4199 | 0 | 51.3199 | 31.1 | 0 | 8 | 51.0896 | 43.2608 | 52.2769 | TRUE | TRUE | 1.8402e-15 | 5.8328e-14 | 3.0394 | 0 | 15.5696 | 0 | 57.625
Test: Proposed / central / ext0 / coal4 / fast | 2043 | 83.3399 | 0 | 52.2399 | 31.1 | 0 | 8 | 45.3027 | 42.9352 | 52.3285 | TRUE | TRUE | 1.7653e-15 | 6.159e-14 | 3.0061 | 0 | 15.2772 | 0 | 54.8987
Test: Proposed / central / ext0 / coal4 / fast | 2044 | 83.3099 | 0 | 52.2099 | 31.1 | 0 | 8 | 42.9625 | 42.5233 | 52.8994 | TRUE | TRUE | 2.0775e-15 | 6.1654e-14 | 2.978 | 0 | 16.3498 | 0 | 53.6616
Test: Proposed / central / ext0 / coal4 / fast | 2045 | 87.1469 | 0 | 53.9469 | 33.2 | 0 | 8 | 68.8143 | 0 | 53.3256 | TRUE | TRUE | 2.4695e-15 | 3.1775e-14 | 3.1345 | 0 | 14.4 | 0 | 26.0092
Test: Proposed / central / ext0 / coal4 / fast | 2046 | 87.1469 | 0 | 53.9469 | 33.2 | 0 | 8 | 63.2474 | 0 | 54.2312 | TRUE | TRUE | 2.0671e-15 | 2.175e-14 | 3.0943 | 0 | 14.4 | 0 | 23.8852
Test: Proposed / central / ext0 / coal4 / fast | 2047 | 87.1469 | 0 | 53.9469 | 33.2 | 0 | 8 | 57.1165 | 0 | 54.68 | TRUE | TRUE | 1.6407e-15 | 1.4246e-14 | 3.0628 | 0 | 10.8 | 0 | 21.6294
Test: Proposed / central / ext0 / coal4 / fast | 2048 | 87.1469 | 0 | 53.9469 | 33.2 | 0 | 8 | 50.931 | 0 | 55.1028 | TRUE | TRUE | 1.4683e-15 | 1.36e-14 | 3.0331 | 0 | 7.2 | 0 | 19.3565
Test: Proposed / central / ext0 / coal4 / fast | 2049 | 86.2489 | 0 | 53.0489 | 33.2 | 0 | 8 | 45.5163 | 0 | 55.3079 | TRUE | TRUE | 1.2422e-15 | 1.1063e-14 | 2.9882 | 0 | 3.6 | 0 | 17.3648
Test: Proposed / central / ext0 / coal4 / fast | 2050 | 82.6659 | 0 | 49.4659 | 33.2 | 0 | 8 | 37.9129 | 0 | 55.3292 | TRUE | TRUE | 9.6321e-16 | 9.4005e-15 | 2.8563 | 0 | 0 | 0 | 14.5959
Planning: Proposed / central | 2030 | 34.4879 | 0 | 34.4879 | 0 | 0 | 0 | 83.8047 | 0 | 40.4038 | FALSE | FALSE | 0.026374 | 2.5779 | 1.2636 | 0 | 15.8728 | 0 | 35.007
Planning: Proposed / central | 2031 | 34.6918 | 0 | 33.1918 | 1.5 | 0 | 0 | 83.2492 | 0 | 41.8078 | FALSE | FALSE | 0.038244 | 2.659 | 1.2843 | 0.069638 | 12.8057 | 0 | 34.6719
Planning: Proposed / central | 2032 | 36.9191 | 0.46425 | 33.0191 | 3 | 0.9 | 0 | 81.7835 | 0 | 43.6968 | FALSE | FALSE | 0.023456 | 2.6497 | 1.4014 | 0.080437 | 7.9611 | 0.016216 | 34.0356
Planning: Proposed / central | 2033 | 39.0294 | 1.0005 | 32.7294 | 4.5 | 1.8 | 0 | 84.8255 | 0 | 43.9875 | FALSE | FALSE | 0.025186 | 2.9222 | 1.5237 | 0 | 8.9499 | 0.034947 | 35.0784
Planning: Proposed / central | 2034 | 42.99 | 1.0005 | 34.29 | 6 | 2.7 | 0 | 88.4763 | 0 | 44.5796 | FALSE | FALSE | 0.019416 | 2.3874 | 1.6972 | 0.16762 | 8.9499 | 0.034947 | 36.3417
Planning: Proposed / central | 2035 | 46.7409 | 2.118 | 35.6409 | 7.5 | 3.6 | 2 | 79.3062 | 14.9037 | 45.4006 | FALSE | FALSE | 0.0088534 | 0.99526 | 1.8589 | 0.2376 | 7.9497 | 0.07398 | 45.1223
Planning: Proposed / central | 2036 | 50.5123 | 3.702 | 37.0123 | 9 | 4.5 | 4 | 77.8626 | 29.8073 | 46.286 | FALSE | FALSE | 0.0073504 | 3.9989 | 2.0661 | 0.20194 | 9.1995 | 0.12931 | 56.9262
Planning: Proposed / central | 2037 | 53.6546 | 4.584 | 37.7546 | 10.5 | 5.4 | 6 | 72.1451 | 35.2625 | 47.5065 | FALSE | FALSE | 0.0026476 | 3.2307 | 2.2089 | 0.25875 | 9.5345 | 0.16011 | 59.7697
Planning: Proposed / central | 2038 | 56.7511 | 5.7728 | 38.4511 | 12 | 6.3 | 8 | 67.2509 | 41.7721 | 48.6884 | FALSE | FALSE | 1.6636e-15 | 2.5239 | 2.3595 | 0.1881 | 12.5843 | 0.20164 | 63.72
Planning: Proposed / central | 2039 | 60.381 | 7.0268 | 39.681 | 13.5 | 7.2 | 8 | 62.979 | 42.0988 | 49.7571 | TRUE | FALSE | 1.9116e-15 | 1.9666 | 2.5253 | 0.27337 | 15.2843 | 0.24544 | 62.1098
Planning: Proposed / central | 2040 | 63.1129 | 7.7317 | 40.0129 | 15 | 8.1 | 8 | 64.4407 | 43.18 | 50.3478 | TRUE | FALSE | 1.8396e-15 | 2.1984 | 2.6649 | 0.04725 | 17.0843 | 0.27006 | 63.261
Planning: Proposed / central | 2041 | 65.5926 | 6.4628 | 40.0926 | 16.5 | 9 | 8 | 59.2229 | 43.3022 | 50.9537 | TRUE | FALSE | 1.8411e-15 | 1.7498 | 2.7857 | 0.09 | 17.9843 | 0.22574 | 61.1527
Planning: Proposed / central | 2042 | 68.3764 | 5.7165 | 40.4764 | 18 | 9.9 | 8 | 51.061 | 43.2608 | 51.3948 | TRUE | FALSE | 1.8697e-15 | 1.1419 | 2.9154 | 0 | 17.9843 | 0.19967 | 57.7202
Planning: Proposed / central | 2043 | 70.7132 | 3.9915 | 40.4132 | 19.5 | 10.8 | 8 | 45.2858 | 42.9352 | 51.5377 | TRUE | FALSE | 1.763e-15 | 0.85795 | 2.9675 | 0.10687 | 17.9843 | 0.13942 | 54.9799
Planning: Proposed / central | 2044 | 73.6399 | 3.45 | 40.9399 | 21 | 11.7 | 8 | 42.9533 | 42.5233 | 52.3257 | TRUE | FALSE | 2.0932e-15 | 0.41596 | 3.0119 | 0 | 17.9843 | 0.12051 | 53.7322
Planning: Proposed / central | 2045 | 75.9544 | 1.6275 | 40.8544 | 22.5 | 12.6 | 8 | 68.7957 | 0.0083632 | 52.6799 | TRUE | FALSE | 2.4738e-15 | 0.32224 | 3.1364 | 0 | 17.5457 | 0.056847 | 26.155
Planning: Proposed / central | 2046 | 79.8794 | 1.3125 | 42.3794 | 24 | 13.5 | 8 | 63.2403 | 0 | 53.8606 | TRUE | FALSE | 2.0841e-15 | 0.029033 | 3.2426 | 0 | 16.4847 | 0.045844 | 23.9807
Planning: Proposed / central | 2047 | 83.2194 | 0.7125 | 43.6194 | 25.2 | 14.4 | 8 | 57.1107 | 0 | 54.5497 | TRUE | TRUE | 1.649e-15 | 1.4161e-14 | 3.1721 | 0 | 11.2386 | 0.024887 | 21.6904
Planning: Proposed / central | 2048 | 84.891 | 0.7125 | 45.291 | 25.2 | 14.4 | 8 | 50.9266 | 0 | 55.0909 | TRUE | TRUE | 1.4704e-15 | 1.3543e-14 | 3.1177 | 0.10103 | 7.2 | 0.024887 | 19.3925
Planning: Proposed / central | 2049 | 83.4506 | 0.6735 | 43.8506 | 25.2 | 14.4 | 8 | 45.5114 | 0 | 55.2241 | TRUE | TRUE | 1.2482e-15 | 1.1006e-14 | 3.0558 | 0.40309 | 3.6 | 0.023525 | 17.3986
Planning: Proposed / central | 2050 | 83.2266 | 3.3607 | 43.6266 | 25.2 | 14.4 | 8 | 37.9092 | 0 | 55.509 | TRUE | TRUE | 9.6321e-16 | 9.3721e-15 | 2.9995 | 0 | 0 | 0.11739 | 14.629
Retention: Proposed / central | 2030 | 34.4879 | 0 | 34.4879 | 0 | 0 | 0 | 83.8047 | 0 | 40.4038 | FALSE | FALSE | 0.026374 | 2.5779 | 1.2636 | 0 | 15.8728 | 0 | 35.007
Retention: Proposed / central | 2031 | 34.6918 | 0 | 33.1918 | 1.5 | 0 | 0 | 83.2492 | 0 | 41.8078 | FALSE | FALSE | 0.038244 | 2.659 | 1.2843 | 0.11606 | 12.8057 | 0 | 34.6719
Retention: Proposed / central | 2032 | 36.9191 | 0.46425 | 33.0191 | 3 | 0.9 | 0 | 81.7826 | 0 | 43.71 | FALSE | FALSE | 0.023585 | 2.6606 | 1.4013 | 0.13406 | 7.9611 | 0.027026 | 34.036
Retention: Proposed / central | 2033 | 39.0294 | 1.0005 | 32.7294 | 4.5 | 1.8 | 0 | 84.823 | 0 | 44.0162 | FALSE | FALSE | 0.025657 | 2.9453 | 1.5234 | 0 | 8.9499 | 0.058244 | 35.0798
Retention: Proposed / central | 2034 | 42.99 | 1.0005 | 34.29 | 6 | 2.7 | 0 | 88.4738 | 0 | 44.6083 | FALSE | FALSE | 0.019598 | 2.4102 | 1.6965 | 0.27937 | 8.9499 | 0.058244 | 36.3436
Retention: Proposed / central | 2035 | 46.7409 | 2.118 | 35.6409 | 7.5 | 3.6 | 2 | 79.3027 | 14.9037 | 45.4613 | FALSE | FALSE | 0.0091955 | 1.0286 | 1.8571 | 0.396 | 7.9497 | 0.1233 | 45.1263
Retention: Proposed / central | 2036 | 50.3962 | 3.5859 | 36.8962 | 9 | 4.5 | 4 | 77.8564 | 29.8073 | 46.3903 | FALSE | FALSE | 0.0078696 | 4.1261 | 2.06 | 0.45262 | 9.1995 | 0.21551 | 56.9344
Retention: Proposed / central | 2037 | 53.9848 | 4.9142 | 38.0848 | 10.5 | 5.4 | 6 | 72.1461 | 35.2625 | 47.6785 | FALSE | FALSE | 0.0025475 | 3.2157 | 2.2171 | 0.56531 | 9.5345 | 0.29388 | 59.7853
Retention: Proposed / central | 2038 | 57.7516 | 6.7732 | 39.4516 | 12 | 6.3 | 8 | 67.2611 | 41.7721 | 48.9465 | TRUE | FALSE | 1.6871e-15 | 2.3369 | 2.3888 | 0.3135 | 12.5843 | 0.39431 | 63.7447
Retention: Proposed / central | 2039 | 61.1021 | 7.7479 | 40.4021 | 13.5 | 7.2 | 8 | 62.9819 | 42.0988 | 50.0462 | TRUE | FALSE | 1.9182e-15 | 1.8902 | 2.5459 | 0.735 | 15.2843 | 0.46731 | 62.1361
Retention: Proposed / central | 2040 | 64.8349 | 9.4537 | 41.7349 | 15 | 8.1 | 8 | 64.4521 | 43.18 | 50.7587 | TRUE | FALSE | 1.8131e-15 | 1.88 | 2.7219 | 0.47475 | 17.0843 | 0.5734 | 63.2996
Retention: Proposed / central | 2041 | 68.9581 | 9.8282 | 43.4581 | 16.5 | 9 | 8 | 59.2451 | 43.3022 | 51.475 | TRUE | FALSE | 1.8423e-15 | 1.1834 | 2.8923 | 0.48656 | 17.9843 | 0.59174 | 61.1919
Retention: Proposed / central | 2042 | 72.5291 | 9.8692 | 44.6291 | 18 | 9.9 | 8 | 51.0775 | 43.2608 | 51.9741 | TRUE | FALSE | 1.8732e-15 | 0.60136 | 2.9987 | 0.43125 | 17.9843 | 0.59965 | 57.7523
Retention: Proposed / central | 2043 | 76.1725 | 9.4507 | 45.8725 | 19.5 | 10.8 | 8 | 45.299 | 42.9352 | 52.1793 | TRUE | FALSE | 1.7653e-15 | 0.29692 | 3.1018 | 0.49162 | 17.9843 | 0.56843 | 55.0036
Retention: Proposed / central | 2044 | 80.211 | 10.0211 | 47.511 | 21 | 11.7 | 8 | 42.9603 | 42.5233 | 53.0648 | TRUE | FALSE | 2.0775e-15 | 0.047771 | 3.1617 | 0.45563 | 17.9843 | 0.60991 | 53.7513
Retention: Proposed / central | 2045 | 83.6074 | 9.2805 | 48.5074 | 22.5 | 12.6 | 8 | 68.8117 | 0 | 53.4387 | TRUE | FALSE | 2.5042e-15 | 0.0082263 | 3.2735 | 0.07875 | 16.7282 | 0.54485 | 26.153
Retention: Proposed / central | 2046 | 85.5921 | 7.6252 | 48.6921 | 23.4 | 13.5 | 8 | 63.2453 | 0 | 54.4566 | TRUE | TRUE | 2.0565e-15 | 1.8268e-14 | 3.226 | 0.15 | 15.2772 | 0.45264 | 23.985
Retention: Proposed / central | 2047 | 86.2359 | 6.429 | 49.3359 | 23.4 | 13.5 | 8 | 57.1148 | 0 | 54.9241 | TRUE | TRUE | 1.6469e-15 | 1.4317e-14 | 3.156 | 0 | 11.2386 | 0.37427 | 21.6952
Retention: Proposed / central | 2048 | 86.0044 | 4.5259 | 49.1044 | 23.4 | 13.5 | 8 | 50.929 | 0 | 55.3028 | TRUE | TRUE | 1.4642e-15 | 1.3586e-14 | 3.1141 | 0.3465 | 7.2 | 0.27384 | 19.397
Retention: Proposed / central | 2049 | 84.2006 | 4.1235 | 47.3006 | 23.4 | 13.5 | 8 | 45.5137 | 0 | 55.3883 | TRUE | TRUE | 1.2381e-15 | 1.1035e-14 | 3.0445 | 0.67181 | 3.6 | 0.24005 | 17.4026
Retention: Proposed / central | 2050 | 82.1541 | 4.9882 | 45.2541 | 23.4 | 13.5 | 8 | 37.9102 | 0 | 55.5819 | TRUE | TRUE | 9.6321e-16 | 9.3578e-15 | 2.948 | 0 | 0 | 0.29039 | 14.6373
Test: Proposed / central / ext5 / coal4 / slow50 | 2030 | 34.4879 | 0 | 34.4879 | 0 | 0 | 0 | 83.8047 | 0 | 40.4038 | FALSE | FALSE | 0.026374 | 2.5779 | 1.2636 | 0 | 15.8728 | 0 | 35.007
Test: Proposed / central / ext5 / coal4 / slow50 | 2031 | 34.6918 | 0 | 33.1918 | 1.5 | 0 | 0 | 83.2492 | 0 | 41.8078 | FALSE | FALSE | 0.038244 | 2.659 | 1.2843 | 0.069638 | 12.8057 | 0 | 34.6719
Test: Proposed / central / ext5 / coal4 / slow50 | 2032 | 36.9191 | 0.46425 | 33.0191 | 3 | 0.9 | 0 | 81.7835 | 0 | 43.6968 | FALSE | FALSE | 0.023456 | 2.6497 | 1.4014 | 0.080437 | 7.9611 | 0.016216 | 34.0356
Test: Proposed / central / ext5 / coal4 / slow50 | 2033 | 39.0294 | 1.0005 | 32.7294 | 4.5 | 1.8 | 0 | 84.8255 | 0 | 43.9875 | FALSE | FALSE | 0.025186 | 2.9222 | 1.5237 | 0 | 8.9499 | 0.034947 | 35.0784
Test: Proposed / central / ext5 / coal4 / slow50 | 2034 | 42.99 | 1.0005 | 34.29 | 6 | 2.7 | 0 | 88.4763 | 0 | 44.5796 | FALSE | FALSE | 0.019416 | 2.3874 | 1.6972 | 0.16762 | 8.9499 | 0.034947 | 36.3417
Test: Proposed / central / ext5 / coal4 / slow50 | 2035 | 46.7409 | 2.118 | 35.6409 | 7.5 | 3.6 | 2 | 79.3062 | 14.9037 | 45.4006 | FALSE | FALSE | 0.0088534 | 0.99526 | 1.8589 | 0.2376 | 7.9497 | 0.07398 | 45.1223
Test: Proposed / central / ext5 / coal4 / slow50 | 2036 | 50.5123 | 3.702 | 37.0123 | 9 | 4.5 | 4 | 77.8626 | 29.8073 | 46.286 | FALSE | FALSE | 0.0073504 | 3.9989 | 2.0661 | 0.20194 | 9.1995 | 0.12931 | 56.9262
Test: Proposed / central / ext5 / coal4 / slow50 | 2037 | 53.6546 | 4.584 | 37.7546 | 10.5 | 5.4 | 6 | 72.1451 | 35.2625 | 47.5065 | FALSE | FALSE | 0.0026476 | 3.2307 | 2.2089 | 0.25875 | 9.5345 | 0.16011 | 59.7697
Test: Proposed / central / ext5 / coal4 / slow50 | 2038 | 56.7511 | 5.7728 | 38.4511 | 12 | 6.3 | 8 | 67.2509 | 41.7721 | 48.6884 | FALSE | FALSE | 1.6636e-15 | 2.5239 | 2.3595 | 0.1881 | 12.5843 | 0.20164 | 63.72
Test: Proposed / central / ext5 / coal4 / slow50 | 2039 | 60.381 | 7.0268 | 39.681 | 13.5 | 7.2 | 8 | 62.979 | 42.0988 | 49.7571 | TRUE | FALSE | 1.9116e-15 | 1.9666 | 2.5253 | 0.27337 | 15.2843 | 0.24544 | 62.1098
Test: Proposed / central / ext5 / coal4 / slow50 | 2040 | 63.1129 | 7.7317 | 40.0129 | 15 | 8.1 | 8 | 64.4407 | 43.18 | 50.3478 | TRUE | FALSE | 1.8396e-15 | 2.1984 | 2.6649 | 0.04725 | 16.6457 | 0.27006 | 63.261
Test: Proposed / central / ext5 / coal4 / slow50 | 2041 | 65.5926 | 6.4628 | 40.0926 | 16.5 | 9 | 8 | 59.2229 | 43.3022 | 50.9537 | TRUE | FALSE | 1.8411e-15 | 1.7498 | 2.7857 | 0.09 | 17.1072 | 0.22574 | 61.1527
Test: Proposed / central / ext5 / coal4 / slow50 | 2042 | 68.3764 | 5.7165 | 40.4764 | 18 | 9.9 | 8 | 51.061 | 43.2608 | 51.3948 | TRUE | FALSE | 1.8697e-15 | 1.1419 | 2.9154 | 0 | 16.6686 | 0.19967 | 57.7202
Test: Proposed / central / ext5 / coal4 / slow50 | 2043 | 70.7132 | 3.9915 | 40.4132 | 19.5 | 10.8 | 8 | 45.2858 | 42.9352 | 51.5377 | TRUE | FALSE | 1.763e-15 | 0.85795 | 2.9675 | 0.10687 | 16.23 | 0.13942 | 54.9799
Test: Proposed / central / ext5 / coal4 / slow50 | 2044 | 71.7999 | 3.45 | 39.0999 | 21 | 11.7 | 8 | 42.9474 | 42.5233 | 52.1836 | TRUE | FALSE | 2.0731e-15 | 0.63719 | 2.9987 | 0 | 16.23 | 0.12051 | 53.7489
Test: Proposed / central / ext5 / coal4 / slow50 | 2045 | 72.2744 | 1.6275 | 37.1744 | 22.5 | 12.6 | 8 | 68.7596 | 0.036412 | 52.3993 | TRUE | FALSE | 2.4814e-15 | 0.80516 | 3.0471 | 0 | 16.23 | 0.056847 | 26.2464
Test: Proposed / central / ext5 / coal4 / slow50 | 2046 | 74.3594 | 1.3125 | 36.8594 | 24 | 13.5 | 8 | 63.2222 | 0.0073787 | 53.438 | TRUE | FALSE | 2.0438e-15 | 0.33997 | 3.1228 | 0 | 16.23 | 0.045844 | 24.0747
Test: Proposed / central / ext5 / coal4 / slow50 | 2047 | 76.1594 | 0.7125 | 36.2594 | 25.5 | 14.4 | 8 | 57.0968 | 0 | 54.0013 | TRUE | FALSE | 1.6261e-15 | 0.092772 | 3.1777 | 0 | 12.63 | 0.024887 | 21.7875
Test: Proposed / central / ext5 / coal4 / slow50 | 2048 | 78.391 | 0.7125 | 36.091 | 27 | 15.3 | 8 | 50.911 | 0 | 54.5536 | TRUE | FALSE | 1.495e-15 | 0.0060554 | 3.1885 | 0.10103 | 8.6025 | 0.024887 | 19.4885
Test: Proposed / central / ext5 / coal4 / slow50 | 2049 | 79.3506 | 0.6735 | 34.6506 | 28.5 | 16.2 | 8 | 45.4929 | 0 | 54.8421 | TRUE | FALSE | 1.2422e-15 | 1.0935e-14 | 3.0966 | 0.40309 | 3.6 | 0.023525 | 17.4911
Test: Proposed / central / ext5 / coal4 / slow50 | 2050 | 79.1266 | 3.3607 | 34.4266 | 28.5 | 16.2 | 8 | 37.8912 | 0 | 55.1264 | TRUE | TRUE | 9.5515e-16 | 9.3578e-15 | 3.0234 | 0 | 0 | 0.11739 | 14.7152
Test: Proposed / central / ext5 / coal6 / slow / earlycoal | 2030 | 34.4879 | 0 | 34.4879 | 0 | 0 | 0 | 83.8047 | 0 | 40.4038 | FALSE | FALSE | 0.026374 | 2.5779 | 1.2636 | 0 | 16.423 | 0 | 35.007
Test: Proposed / central / ext5 / coal6 / slow / earlycoal | 2031 | 34.6918 | 0 | 33.1918 | 1.5 | 0 | 0 | 83.2492 | 0 | 41.8078 | FALSE | FALSE | 0.038244 | 2.659 | 1.2843 | 0.069638 | 13.906 | 0 | 34.6719
Test: Proposed / central / ext5 / coal6 / slow / earlycoal | 2032 | 36.9191 | 0.46425 | 33.0191 | 3 | 0.9 | 0 | 81.7835 | 0 | 43.6968 | FALSE | FALSE | 0.023456 | 2.6497 | 1.4014 | 0.080437 | 9.0615 | 0.016216 | 34.0356
Test: Proposed / central / ext5 / coal6 / slow / earlycoal | 2033 | 39.0294 | 1.0005 | 32.7294 | 4.5 | 1.8 | 0 | 84.8255 | 0 | 43.9875 | FALSE | FALSE | 0.025186 | 2.9222 | 1.5237 | 0 | 10.0502 | 0.034947 | 35.0784
Test: Proposed / central / ext5 / coal6 / slow / earlycoal | 2034 | 42.99 | 1.0005 | 34.29 | 6 | 2.7 | 0 | 88.4763 | 0 | 44.5796 | FALSE | FALSE | 0.019416 | 2.3874 | 1.6972 | 0.16762 | 10.0502 | 0.034947 | 36.3417
Test: Proposed / central / ext5 / coal6 / slow / earlycoal | 2035 | 46.7409 | 2.118 | 35.6409 | 7.5 | 3.6 | 4 | 71.635 | 29.8073 | 45.6443 | FALSE | FALSE | 0.0045412 | 0.57795 | 1.843 | 0.2376 | 8.4999 | 0.07398 | 54.7284
Test: Proposed / central / ext5 / coal6 / slow / earlycoal | 2036 | 50.5123 | 3.702 | 37.0123 | 9 | 4.5 | 8 | 74.5335 | 32.9861 | 46.7668 | TRUE | FALSE | 1.6514e-15 | 2.5187 | 2.0509 | 0.20194 | 9.1995 | 0.12931 | 58.843
Test: Proposed / central / ext5 / coal6 / slow / earlycoal | 2037 | 53.6546 | 4.584 | 37.7546 | 10.5 | 5.4 | 10 | 62.4421 | 45.9663 | 47.9676 | TRUE | FALSE | 7.3283e-16 | 1.8748 | 2.1987 | 0.25875 | 9.5345 | 0.16011 | 66.2314
Test: Proposed / central / ext5 / coal6 / slow / earlycoal | 2038 | 56.7511 | 5.7728 | 38.4511 | 12 | 6.3 | 12 | 57.0674 | 52.4988 | 49.1175 | TRUE | FALSE | 8.6708e-16 | 1.3883 | 2.3447 | 0.1881 | 12.5843 | 0.20164 | 70.0206
Test: Proposed / central / ext5 / coal6 / slow / earlycoal | 2039 | 60.381 | 7.0268 | 39.681 | 13.5 | 7.2 | 12 | 52.1748 | 53.1512 | 50.158 | TRUE | FALSE | 9.5911e-16 | 1.0732 | 2.5058 | 0.27337 | 15.2843 | 0.24544 | 68.4474
Test: Proposed / central / ext5 / coal6 / slow / earlycoal | 2040 | 63.1129 | 7.7317 | 40.0129 | 15 | 8.1 | 12 | 52.3639 | 55.3051 | 50.717 | TRUE | FALSE | 8.6561e-16 | 1.2484 | 2.6533 | 0.04725 | 17.0843 | 0.27006 | 70.0216
Test: Proposed / central / ext5 / coal6 / slow / earlycoal | 2041 | 65.5926 | 6.4628 | 40.0926 | 16.5 | 9 | 12 | 46.9555 | 55.5329 | 51.3045 | TRUE | FALSE | 9.0958e-16 | 0.97211 | 2.7654 | 0.09 | 17.9843 | 0.22574 | 67.9016
Test: Proposed / central / ext5 / coal6 / slow / earlycoal | 2042 | 68.3764 | 5.7165 | 40.4764 | 18 | 9.9 | 12 | 40.0856 | 55.3645 | 51.7916 | TRUE | FALSE | 8.0096e-16 | 0.55112 | 2.8395 | 0 | 17.9843 | 0.19967 | 64.7927
Test: Proposed / central / ext5 / coal6 / slow / earlycoal | 2043 | 70.7132 | 3.9915 | 40.4132 | 19.5 | 10.8 | 12 | 34.7477 | 54.6722 | 51.9435 | TRUE | FALSE | 7.2419e-16 | 0.36867 | 2.8635 | 0.10687 | 17.9843 | 0.13942 | 61.889
Test: Proposed / central / ext5 / coal6 / slow / earlycoal | 2044 | 73.6399 | 3.45 | 40.9399 | 21 | 11.7 | 12 | 32.8213 | 53.8715 | 52.7375 | TRUE | FALSE | 9.0124e-16 | 0.12952 | 2.9142 | 0 | 17.9843 | 0.12051 | 60.4457
Test: Proposed / central / ext5 / coal6 / slow / earlycoal | 2045 | 75.9544 | 1.6275 | 40.8544 | 22.5 | 12.6 | 12 | 68.7957 | 0.0083632 | 53.1988 | TRUE | FALSE | 2.4738e-15 | 0.086835 | 3.1105 | 0 | 17.5568 | 0.056847 | 26.155
Test: Proposed / central / ext5 / coal6 / slow / earlycoal | 2046 | 79.8794 | 1.3125 | 42.3794 | 24 | 13.5 | 12 | 63.2403 | 0 | 54.3795 | TRUE | FALSE | 2.0841e-15 | 1.8254e-14 | 3.1022 | 0 | 16.1543 | 0.045844 | 23.9807
Test: Proposed / central / ext5 / coal6 / slow / earlycoal | 2047 | 81.1194 | 0.7125 | 43.6194 | 24 | 13.5 | 12 | 57.1107 | 0 | 54.9303 | TRUE | TRUE | 1.649e-15 | 1.4161e-14 | 3.0355 | 0 | 12.5543 | 0.024887 | 21.6905
Test: Proposed / central / ext5 / coal6 / slow / earlycoal | 2048 | 82.791 | 0.7125 | 45.291 | 24 | 13.5 | 12 | 50.9266 | 0 | 55.4715 | TRUE | TRUE | 1.4704e-15 | 1.3557e-14 | 3.0102 | 0.10103 | 8.9543 | 0.024887 | 19.3925
Test: Proposed / central / ext5 / coal6 / slow / earlycoal | 2049 | 83.1906 | 0.6735 | 45.6906 | 24 | 13.5 | 12 | 45.513 | 0 | 55.7479 | TRUE | TRUE | 1.2381e-15 | 1.1106e-14 | 2.9967 | 0.40309 | 5.3543 | 0.023525 | 17.3888
Test: Proposed / central / ext5 / coal6 / slow / earlycoal | 2050 | 84.8066 | 3.3607 | 47.3066 | 24 | 13.5 | 12 | 37.9115 | 0 | 56.1762 | TRUE | TRUE | 9.6523e-16 | 9.3863e-15 | 3.0036 | 0 | 1.3157 | 0.11739 | 14.6132

## Reliability standard
Reliability-standard proxy (3 h LOLE) and gas-mix screening — v2.3.1. Values computed by the model; see methods M54–M58.
setting | programme | demand | ccgt_units_planning | ccgt_units_sized | engine_sites_planning | engine_sites_sized | ocgt_units_planning | ocgt_units_sized | new_gas_gw_2050_planning | new_gas_gw_2050_sized | planning_max_lole_h | sized_max_lole_h | sized_years_above_3h | planning_cost_2030_50_bn | sized_cost_2030_50_bn | cost_difference_bn | gas_fuel_twh_2030_50_planning | gas_fuel_twh_2030_50_sized | emissions_mt_2030_50_planning | emissions_mt_2030_50_sized | planning_stress_pass_years | sized_stress_pass_years | peaker_only_v2_3_cost_bn
official | Nuclear buildout | low | 33 | 0 | 172 | 157 | 34 | 21 | 57.8 | 22 | 1.82 | 2.96 | none | 971.8 | 940.1 | 31.7 | 1913 | 1901 | 665.6 | 667.6 | 12 | 0 | 952
official | Nuclear buildout | central | 30 | 1 | 252 | 225 | 48 | 42 | 67.2 | 36 | 2.64 | 2.6 | none | 1035.6 | 1015 | 20.6 | 2706 | 2749 | 876.9 | 881 | 4 | 0 | 1018.3
official | Nuclear buildout | high | 44 | 23 | 300 | 228 | 57 | 41 | 78.4 | 56.3 | 8.34 | 7.88 | 2031, 2032, 2033, 2034, 2035, 2036, 2040, 2041 | 1079.3 | 1074.2 | 5.1 | 3715 | 3707 | 1077.2 | 1082.4 | 0 | 0 | 1076.3
official | Nuclear buildout | programme | 44 | 2 | 300 | 155 | 57 | 18 | 78.4 | 22.7 |  | 6.55 | 2031, 2032, 2033, 2034 |  | 981.6 |  |  | 2304 |  | 780.4 |  | 0
official | Renewables + gas | low | 43 | 0 | 190 | 270 | 38 | 43 | 61.7 | 39.9 | 1.75 | 2.83 | none | 1068.2 | 1046.6 | 21.6 | 3280 | 3289 | 662.5 | 664.4 | 13 | 0 | 1049.4
official | Renewables + gas | central | 44 | 10 | 285 | 296 | 55 | 52 | 76.3 | 54.4 | 2.27 | 2.95 | none | 1220.2 | 1204.7 | 15.5 | 3536 | 3557 | 714.2 | 718.5 | 1 | 0 | 1205
official | Renewables + gas | high | 44 | 23 | 300 | 297 | 57 | 52 | 78.4 | 66.5 | 5.11 | 5.11 | 2031, 2032, 2033 | 1292.9 | 1290 | 2.9 | 3757 | 3761 | 758.8 | 759.7 | 0 | 0 | 1290.1
official | Renewables + gas | programme | 44 | 5 | 300 | 267 | 57 | 33 | 78.4 | 41.2 |  | 4.68 | 2031, 2032 |  | 1146.5 |  |  | 3485 |  | 704 |  | 0
tight | Nuclear buildout | low | 33 | 1 | 172 | 118 | 34 | 31 | 57.8 | 22 | 1.82 | 3.74 | 2031 | 971.8 | 942.8 | 29 | 1913 | 1903 | 665.6 | 669.1 | 12 | 0
tight | Nuclear buildout | central | 30 | 30 | 252 | 113 | 48 | 24 | 67.2 | 46.1 | 2.64 | 8.87 | 2031, 2032, 2033, 2034, 2035, 2036 | 1035.6 | 1026.3 | 9.2 | 2706 | 2730 | 876.9 | 867 | 4 | 0
tight | Nuclear buildout | high | 44 | 34 | 300 | 160 | 57 | 48 | 78.4 | 58 | 8.34 | 30.64 | 2031, 2032, 2033, 2034, 2035, 2036, 2037, 2038, 2039, 2040, 2041, 2042, 2043, 2044, 2045, 2046, 2047 | 1079.3 | 1075.1 | 4.2 | 3715 | 3670 | 1077.2 | 1088 | 0 | 0
tight | Nuclear buildout | programme | 44 | 34 | 300 | 50 | 57 | 15 | 78.4 | 37.1 |  | 18.18 | 2031, 2032, 2033, 2034, 2035, 2036 |  | 998.3 |  |  | 2293 |  | 779.9 |  | 0
tight | Renewables + gas | low | 43 | 21 | 190 | 158 | 38 | 45 | 61.7 | 44.9 | 1.75 | 3.5 | 2031 | 1068.2 | 1052.8 | 15.4 | 3280 | 3282 | 662.5 | 663 | 13 | 0
tight | Renewables + gas | central | 44 | 34 | 285 | 144 | 55 | 36 | 76.3 | 52.8 | 2.27 | 5.15 | 2031, 2034, 2035, 2037 | 1220.2 | 1214 | 6.2 | 3536 | 3531 | 714.2 | 713.3 | 1 | 0
tight | Renewables + gas | high | 44 | 34 | 300 | 190 | 57 | 57 | 78.4 | 63.7 | 5.11 | 23.35 | 2031, 2032, 2033, 2034, 2035, 2036, 2037, 2038, 2039, 2040, 2041, 2042, 2043, 2044, 2045, 2046, 2047, 2048, 2049, 2050 | 1292.9 | 1289.5 | 3.4 | 3757 | 3747 | 758.8 | 756.9 | 0 | 0
tight | Renewables + gas | programme | 44 | 34 | 300 | 88 | 57 | 21 | 78.4 | 42.7 |  | 8.46 | 2031, 2032, 2033, 2034, 2035 |  | 1158 |  |  | 3461 |  | 699.1 |  | 0
Year-by-year LOLE (hours/year)
setting | programme | demand | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
planning | Nuclear buildout | low | 1.339 | 1.821 | 1 | 0.875 | 0.589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018 | 0 | 0
planning | Nuclear buildout | central | 1.411 | 2.643 | 1.661 | 2.464 | 1.607 | 0.357 | 0.446 | 0 | 0 | 0 | 0 | 0 | 0.018 | 0.018 | 0 | 0.071 | 0.125 | 0.054 | 0.018 | 0.036 | 0.036
planning | Nuclear buildout | high | 3.089 | 6.768 | 5.107 | 8.339 | 7.679 | 3.107 | 3.161 | 2.625 | 2.5 | 2.446 | 3.696 | 3.804 | 2.125 | 2.554 | 1.464 | 1.929 | 0.375 | 0.232 | 0.232 | 0.143 | 0.089
planning | Renewables + gas | low | 1.339 | 1.75 | 0.946 | 0.911 | 0.429 | 0 | 0.018 | 0.018 | 0 | 0 | 0 | 0.018 | 0.036 | 0 | 0.054 | 0.018 | 0.054 | 0.018 | 0.054 | 0.054 | 0.036
planning | Renewables + gas | central | 1.411 | 2.268 | 1.304 | 0.964 | 0.75 | 0.179 | 0.304 | 0.196 | 0.161 | 0.036 | 0.054 | 0.196 | 0.089 | 0.161 | 0.161 | 0.179 | 0.125 | 0.089 | 0.214 | 0.143 | 0.161
planning | Renewables + gas | high | 3.089 | 5.107 | 3.25 | 3.732 | 2.554 | 1.268 | 1.482 | 2.018 | 1.911 | 1.625 | 2.089 | 2.732 | 2.482 | 2.5 | 2.554 | 2.125 | 1.286 | 1.161 | 0.839 | 0.786 | 0.661
official | Nuclear buildout | low | 1.298 | 2.964 | 1.69 | 2.095 | 2.619 | 2.071 | 2.286 | 1.893 | 1.631 | 1.393 | 1.869 | 2.083 | 1.464 | 1.929 | 0.964 | 2.786 | 1.56 | 1.036 | 1.262 | 2.679 | 2.619
official | Nuclear buildout | central | 1.381 | 2.595 | 1.75 | 2.238 | 2.071 | 0.964 | 1.631 | 1.369 | 1.345 | 1.476 | 2.357 | 2.524 | 1.857 | 2.357 | 1.405 | 2.452 | 1.56 | 0.893 | 0.417 | 0.333 | 0.274
official | Nuclear buildout | high | 2.905 | 6.702 | 5.036 | 7.881 | 7.417 | 3.024 | 3.143 | 2.798 | 2.56 | 2.381 | 3.726 | 3.893 | 2.786 | 2.595 | 1.798 | 2.429 | 1.774 | 1.595 | 1.155 | 1.095 | 0.452
official | Nuclear buildout | programme | 2.25 | 5.833 | 4.702 | 6.548 | 4.048 | 2.19 | 2.583 | 2.429 | 2.464 | 2.19 | 2.762 | 2.345 | 1.964 | 2.94 | 1.357 | 2.155 | 0.786 | 0.524 | 0.095 | 0.071 | 0.083
official | Renewables + gas | low | 1.298 | 2.833 | 1.964 | 1.893 | 2.655 | 1.452 | 1.262 | 1.179 | 0.75 | 0.44 | 0.524 | 1.214 | 1.488 | 1.619 | 2.238 | 2.381 | 2.81 | 2.702 | 2.702 | 2.821 | 2.548
official | Renewables + gas | central | 1.381 | 2.155 | 1.274 | 0.952 | 1.202 | 0.821 | 1.167 | 2.381 | 2.774 | 2.381 | 2.952 | 2.631 | 2.94 | 2.774 | 2.726 | 2.393 | 2.548 | 2.214 | 1.786 | 2.369 | 1.821
official | Renewables + gas | high | 2.905 | 5.107 | 3.262 | 3.405 | 2.381 | 1.226 | 1.417 | 1.988 | 1.976 | 1.512 | 2.179 | 2.75 | 2.345 | 2.821 | 2.667 | 2.524 | 2.619 | 2.798 | 2.726 | 2.476 | 3
official | Renewables + gas | programme | 2.25 | 4.679 | 3.071 | 2.488 | 2.833 | 2.024 | 2.345 | 2.524 | 2.774 | 2.262 | 2.988 | 2.917 | 2.667 | 2.833 | 2.952 | 2.44 | 2.881 | 2.512 | 2.893 | 2.798 | 2.702
tight | Nuclear buildout | low | 1.298 | 3.738 | 1.714 | 2.024 | 2.31 | 1.679 | 1.726 | 1.393 | 0.905 | 0.607 | 0.857 | 1.202 | 0.845 | 1.393 | 0.726 | 2.917 | 1.679 | 0.881 | 0.905 | 2.595 | 2.762
tight | Nuclear buildout | central | 1.381 | 5.726 | 3.774 | 5.857 | 8.869 | 5.536 | 4.202 | 2.417 | 2.286 | 2.5 | 2.786 | 2.821 | 2.476 | 2.679 | 1.512 | 2.179 | 0.393 | 0.131 | 0.048 | 0.048 | 0.048
tight | Nuclear buildout | high | 2.905 | 11.107 | 10.024 | 17.75 | 25.036 | 22.417 | 24.571 | 24.964 | 22.619 | 20.393 | 28.988 | 30.643 | 24.012 | 24.405 | 15.429 | 22.512 | 9.095 | 4.357 | 2.226 | 1.012 | 0.393
tight | Nuclear buildout | programme | 2.25 | 10.31 | 10.262 | 15.905 | 18.179 | 10.298 | 4.167 | 2.274 | 0.964 | 0.786 | 1.143 | 0.774 | 0.429 | 0.274 | 0.119 | 0.44 | 0.024 | 0.012 | 0.036 | 0.024 | 0.024
tight | Renewables + gas | low | 1.298 | 3.5 | 1.595 | 1.881 | 1.595 | 1.25 | 1.048 | 1.405 | 1.095 | 0.81 | 1.274 | 2.06 | 2.583 | 2.095 | 1.952 | 1.5 | 1.083 | 1.06 | 0.893 | 1 | 1.036
tight | Renewables + gas | central | 1.381 | 5.155 | 2.714 | 2.583 | 3.369 | 3.107 | 2.81 | 3.333 | 2.429 | 1.798 | 2.321 | 2.5 | 2.81 | 2.405 | 2.44 | 2.595 | 2.667 | 2.952 | 2.881 | 2.774 | 2.286
tight | Renewables + gas | high | 2.905 | 9.119 | 7.25 | 8.452 | 10.524 | 9.857 | 11.845 | 17.643 | 15.821 | 11.762 | 17.369 | 21.619 | 22.833 | 23.31 | 23.345 | 20.69 | 16.071 | 12.643 | 8.56 | 6.833 | 4.952
tight | Renewables + gas | programme | 2.25 | 8.464 | 7.274 | 6.833 | 6.774 | 4.321 | 2.964 | 2.381 | 1.893 | 1.286 | 2.726 | 2.738 | 1.988 | 2.298 | 1.81 | 2.238 | 2.036 | 1.976 | 1.893 | 2.012 | 1.976
current policy | Current policy | low | 1.298 | 3.5 | 3.512 | 9.083 | 12.238 | 16.44 | 27.25 | 32.155 | 32.845 | 30.976 | 43.893 | 52.583 | 62.726 | 67.024 | 80.274 | 86.31 | 98.774 | 110.762 | 122.143 | 130.25 | 139.893
current policy | Current policy | central | 1.381 | 4.976 | 6.607 | 12.595 | 19.155 | 19.429 | 33.714 | 47.655 | 50.202 | 48.702 | 72.19 | 66.06 | 80.964 | 90.964 | 109.238 | 127.881 | 148.131 | 159.107 | 172.548 | 181.798 | 185.262
current policy | Current policy | high | 2.905 | 8.976 | 14.476 | 14.655 | 24.69 | 26.571 | 43.048 | 59.929 | 60.202 | 67.238 | 97.536 | 105.821 | 129.833 | 146.524 | 163.988 | 148.988 | 170.321 | 184.583 | 203.512 | 212.167 | 225.202
Firm-capacity gap under current policy (GW; M58)
demand | measure | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
low | gap_gw | 0 | 0.28 | 1.53 | 4.6 | 5.22 | 8.62 | 11.75 | 13.09 | 14.96 | 16.63 | 18.27 | 18.41 | 19.3 | 19.79 | 20.91 | 21.49 | 22.57 | 24.37 | 25.2 | 26.14 | 27.62
low | gap_is_lower_bound | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
central | gap_gw | 0 | 1.38 | 4.23 | 6.38 | 8.5 | 10.06 | 12.27 | 13.61 | 14.56 | 15.31 | 18.79 | 18.93 | 20.74 | 22.15 | 25.11 | 26.61 | 28.69 | 31.41 | 32.34 | 33.28 | 34.76
central | gap_is_lower_bound | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
high | gap_gw | 0 | 1.38 | 4.23 | 4.54 | 8.5 | 11.9 | 15.95 | 18.21 | 20.08 | 23.59 | 27.07 | 28.13 | 30.86 | 32.59 | 34.63 | 34.29 | 36.37 | 38.17 | 40.4 | 41.34 | 42.22
high | gap_is_lower_bound | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE